## SEPT 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26770 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15480824 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49738480 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11206521 |  | mg /l |  | Automatic - i2O | AI | ANDRO MIRAFLOR
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 106 | 15485552 | 4728 | 113.472 | 4.728 | 4.5 | 4.5 | 3B | 0 | 0 | 1065 | 1185 | 1065 | N/A | N/A | N/A | N/A | 49739369 | 889 | 188.0288 | 0% | 0% | 100% | 100% | 100% | 65% | 11206927 | 406 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 108 | 15489331 | 3779 | 90.696 | 3.779 | 5.8 | 5.8 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49740118 | 749 | 198.2006 | 0% | 0% | 100% | 100% | 100% | 65% | 11207716 | 789 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 | 105 | 15493008 | 3677 | 88.248 | 3.677 | 7.1 | 7.1 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49741103 | 985 | 267.8814 | 0% | 0% | 100% | 100% | 100% | 65% | 11208618 | 902 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 131 | 120 | 15497785 | 4777 | 114.648 | 4.777 | 8.7 | 8.7 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 49742102 | 999 | 209.1271 | 0% | 0% | 100% | 100% | 100% | 65% | 11209340 | 722 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 123 | 15502651 | 4866 | 116.784 | 4.866 | 9.5 | 9.5 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 49743102 | 1000 | 205.5076 | 0% | 0% | 100% | 100% | 100% | 65% | 11209940 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 133 | 15507754 | 5103 | 122.472 | 5.103 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49744110 | 1008 | 197.5309 | 0% | 0% | 100% | 100% | 100% | 0% | 11209940 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 140 | 15513706 | 5952 | 142.848 | 5.952 | 9.1 | 9.1 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49745289 | 1179 | 198.0847 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 141 | 15519782 | 6076 | 145.824 | 6.076 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49746486 | 1197 | 197.0046 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 139 | 15525976 | 6194 | 148.656 | 6.194 | 7.8 | 7.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49747693 | 1207 | 194.866 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 141 | 15532099 | 6123 | 146.952 | 6.123 | 7.2 | 7.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49748893 | 1200 | 195.9824 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 | 1.18
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 148 | 15538122 | 6023 | 144.552 | 6.023 | 6.6 | 6.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49750089 | 1196 | 198.5721 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 138 | 15543919 | 5797 | 139.128 | 5.797 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49751276 | 1187 | 204.7611 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 139 | 15549727 | 5808 | 139.392 | 5.808 | 5.6 | 5.6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49752456 | 1180 | 203.168 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 15555791 | 6064 | 145.536 | 6.064 | 5.3 | 5.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49753727 | 1271 | 209.5976 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 137 | 15561570 | 5779 | 138.696 | 5.779 | 5 | 5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49754876 | 1149 | 198.8233 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 147 | 15567490 | 5920 | 142.08 | 5.92 | 4.8 | 4.8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49756057 | 1181 | 199.4932 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 15573328 | 5838 | 140.112 | 5.838 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49757214 | 1157 | 198.1843 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 140 | 15579193 | 5865 | 140.76 | 5.865 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49758389 | 1175 | 200.341 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 137 | 15585070 | 5877 | 141.048 | 5.877 | 4.1 | 4.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49759566 | 1177 | 200.2722 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 139 | 15590776 | 5706 | 136.944 | 5.706 | 3.8 | 3.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49760733 | 1167 | 204.5216 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 137 | 15596617 | 5841 | 140.184 | 5.841 | 3.5 | 3.5 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49761905 | 1172 | 200.6506 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 128 | 15602732 | 6115 | 146.76 | 6.115 | 3.2 | 3.2 | 3B+1S | 0 | 1024 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49763122 | 1217 | 199.0188 | 0% | 100% | 100% | 100% | 100% | 0% | 11209940 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 126 | 15608054 | 5322 | 127.728 | 5.322 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49764216 | 1094 | 205.5618 | 0% | 0% | 100% | 100% | 100% | 30% | 11209967 | 27 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 128 | 120 | 15613096 | 5042 | 121.008 | 5.042 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49765250 | 1034 | 205.0774 | 0% | 0% | 100% | 100% | 100% | 30% | 11210128 | 161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132272 | 132.272 | 132.272 | [12 empty] | 26770 | 26770 | 202.386 | [6 empty] | 3607 | 3607 | 1.1333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV1- INCREASE OPENING @ 12:01 AM (65%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26858 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15613096 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49765250 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11210128 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 | 107 | 15617996 | 4900 | 117.6 | 4.9 | 4.2 | 4.2 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49766228 | 978 | 199.5918 | 0% | 0% | 100% | 100% | 100% | 60% | 11210829 | 701 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 104 | 15622374 | 4378 | 105.072 | 4.378 | 5.3 | 5.3 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49767094 | 866 | 197.8072 | 0% | 0% | 100% | 100% | 100% | 60% | 11211718 | 889 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 104 | 15626820 | 4446 | 106.704 | 4.446 | 6.4 | 6.4 | 3B | 0 | 0 | 1065 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49767968 | 874 | 196.5812 | 0% | 0% | 100% | 100% | 100% | 60% | 11212566 | 848 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 147 | 103 | 15631052 | 4232 | 101.568 | 4.232 | 7.9 | 7.9 | 3B | 0 | 0 | 1066 | 1185 | 1117 | N/A | N/A | N/A | N/A | 49768864 | 896 | 211.7202 | 0% | 0% | 100% | 100% | 100% | 60% | 11212893 | 327 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 123 | 15635144 | 4092 | 98.208 | 4.092 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49769812 | 948 | 231.6716 | 0% | 0% | 100% | 100% | 100% | 60% | 11212993 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 134 | 15640632 | 5488 | 131.712 | 5.488 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49770994 | 1182 | 215.379 | 0% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 15646892 | 6260 | 150.24 | 6.26 | 9.4 | 9.4 | 3B+1S | 996 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49772222 | 1228 | 196.1661 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 15652929 | 6037 | 144.888 | 6.037 | 8.8 | 8.8 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49773414 | 1192 | 197.4491 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 140 | 15658964 | 6035 | 144.84 | 6.035 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49774600 | 1186 | 196.5203 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 15665120 | 6156 | 147.744 | 6.156 | 7.4 | 7.4 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49775806 | 1206 | 195.9064 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 | 1.09
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 15671481 | 6361 | 152.664 | 6.361 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49777025 | 1219 | 191.6365 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 15677234 | 5753 | 138.072 | 5.753 | 6.3 | 6.3 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49778194 | 1169 | 203.1983 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 138 | 15683149 | 5915 | 141.96 | 5.915 | 5.7 | 5.7 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49779394 | 1200 | 202.874 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 143 | 15688770 | 5621 | 134.904 | 5.621 | 5.3 | 5.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49780552 | 1158 | 206.0132 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 15694461 | 5691 | 136.584 | 5.691 | 5 | 5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49781720 | 1168 | 205.2363 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 141 | 15700340 | 5879 | 141.096 | 5.879 | 4.7 | 4.7 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49782892 | 1172 | 199.3536 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 142 | 15706195 | 5855 | 140.52 | 5.855 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49784066 | 1174 | 200.5124 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 139 | 15712105 | 5910 | 141.84 | 5.91 | 4.1 | 4.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49785239 | 1173 | 198.4772 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 135 | 15717939 | 5834 | 140.016 | 5.834 | 3.8 | 3.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49786410 | 1171 | 200.7199 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 140 | 15723712 | 5773 | 138.552 | 5.773 | 3.5 | 3.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49787582 | 1172 | 203.014 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 137 | 140 | 15729547 | 5835 | 140.04 | 5.835 | 3.2 | 3.2 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49788768 | 1186 | 203.2562 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 135 | 137 | 15735412 | 5865 | 140.76 | 5.865 | 3 | 3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49789922 | 1154 | 196.7604 | 100% | 0% | 100% | 100% | 100% | 0% | 11212993 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 125 | 15741470 | 6058 | 145.392 | 6.058 | 3 | 3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49791140 | 1218 | 201.0565 | 0% | 0% | 100% | 100% | 100% | 30% | 11213031 | 38 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 129 | 15745998 | 4528 | 108.672 | 4.528 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49792108 | 968 | 213.7809 | 0% | 0% | 100% | 100% | 100% | 30% | 11213226 | 195 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132902 | 132.902 | 132.902 | [12 empty] | 26858 | 26858 | 202.0888 | [6 empty] | 3098 | 3098 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 6:01 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27186 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15745998 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49792108 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11213226 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 128 | 110 | 15750788 | 4790 | 114.96 | 4.79 | 3.8 | 3.8 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49793076 | 968 | 202.0877 | 0% | 0% | 100% | 100% | 100% | 60% | 11213685 | 459 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 138 | 109 | 15755852 | 5064 | 121.536 | 5.064 | 4.4 | 4.4 | 3B | 0 | 0 | 1076 | 1185 | 1107 | N/A | N/A | N/A | N/A | 49794160 | 1084 | 214.06 | 0% | 0% | 100% | 100% | 100% | 60% | 11214321 | 636 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 107 | 15760482 | 4630 | 111.12 | 4.63 | 5.6 | 5.6 | 3B | 0 | 0 | 1076 | 1185 | 1065 | N/A | N/A | N/A | N/A | 49795062 | 902 | 194.8164 | 0% | 0% | 100% | 100% | 100% | 60% | 11215148 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 146 | 102 | 15764752 | 4270 | 102.48 | 4.27 | 7 | 7 | 3B | 0 | 0 | 1116 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49796048 | 986 | 230.9133 | 0% | 0% | 100% | 100% | 100% | 60% | 11215481 | 333 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 149 | 105 | 15769900 | 5148 | 123.552 | 5.148 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49797080 | 1032 | 200.4662 | 0% | 0% | 100% | 100% | 100% | 60% | 11215581 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 136 | 15774144 | 4244 | 101.856 | 4.244 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49798132 | 1052 | 247.8794 | 0% | 0% | 100% | 100% | 100% | 0% | 11215581 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 140 | 15780004 | 5860 | 140.64 | 5.86 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49799250 | 1118 | 190.785 | 0% | 0% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 146 | 15786356 | 6352 | 152.448 | 6.352 | 9.1 | 9.1 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49800484 | 1234 | 194.2695 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 138 | 15792552 | 6196 | 148.704 | 6.196 | 8.5 | 8.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49801650 | 1166 | 188.1859 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 145 | 15799076 | 6524 | 156.576 | 6.524 | 7.9 | 7.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49802906 | 1256 | 192.5199 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 | 1.09
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 157 | 15804776 | 5700 | 136.8 | 5.7 | 7.3 | 7.3 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49804036 | 1130 | 198.2456 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 15810786 | 6010 | 144.24 | 6.01 | 6.6 | 6.6 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49805264 | 1228 | 204.3261 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 137 | 15817000 | 6214 | 149.136 | 6.214 | 6 | 6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49806518 | 1254 | 201.8024 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 138 | 15822642 | 5642 | 135.408 | 5.642 | 5.5 | 5.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49807611 | 1093 | 193.7256 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 138 | 15828474 | 5832 | 139.968 | 5.832 | 5 | 5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49808803 | 1192 | 204.3896 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 139 | 15834360 | 5886 | 141.264 | 5.886 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49809981 | 1178 | 200.1359 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 15840352 | 5992 | 143.808 | 5.992 | 4.3 | 4.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49811166 | 1185 | 197.7637 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 135 | 15846211 | 5859 | 140.616 | 5.859 | 4 | 4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49812339 | 1173 | 200.2048 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 133 | 15852006 | 5795 | 139.08 | 5.795 | 3.6 | 3.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49813506 | 1167 | 201.3805 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 136 | 15857841 | 5835 | 140.04 | 5.835 | 3.4 | 3.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49814673 | 1167 | 200 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 140 | 15863713 | 5872 | 140.928 | 5.872 | 3 | 3 | 3B+1S | 0 | 1065 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49815880 | 1207 | 205.5518 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 130 | 15869734 | 6021 | 144.504 | 6.021 | 2.6 | 2.6 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49817092 | 1212 | 201.2955 | 0% | 100% | 100% | 100% | 100% | 0% | 11215581 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 131 | 15875856 | 6122 | 146.928 | 6.122 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49818346 | 1254 | 204.835 | 0% | 0% | 100% | 100% | 100% | 30% | 11215655 | 74 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 122 | 15880682 | 4826 | 115.824 | 4.826 | 2.8 | 2.8 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49819294 | 948 | 196.436 | 0% | 0% | 100% | 100% | 100% | 30% | 11215822 | 167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134684 | 134.684 | 134.684 | [12 empty] | 27186 | 27186 | 201.8503 | [6 empty] | 2596 | 2596 | 1.155 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 5:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26846 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 15880682 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49819294 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11215822 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 139 | 120 | 15885422 | 4740 | 113.76 | 4.74 | 3.8 | 3.8 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49820268 | 974 | 205.4852 | 0% | 0% | 100% | 100% | 100% | 60% | 11216284 | 462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 140 | 116 | 15889974 | 4552 | 109.248 | 4.552 | 4.9 | 4.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49821226 | 958 | 210.4569 | 0% | 0% | 100% | 100% | 100% | 60% | 11217084 | 800 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 100 | 15894296 | 4322 | 103.728 | 4.322 | 5.6 | 5.6 | 3B | 0 | 0 | 1055 | 1185 | 1056 | N/A | N/A | N/A | N/A | 49822044 | 818 | 189.2642 | 0% | 0% | 100% | 100% | 100% | 60% | 11217863 | 779 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 148 | 105 | 15898642 | 4346 | 104.304 | 4.346 | 7.9 | 7.9 | 3B | 0 | 0 | 1117 | 1185 | 1116 | N/A | N/A | N/A | N/A | 49822976 | 932 | 214.4501 | 0% | 0% | 100% | 100% | 100% | 60% | 11218391 | 528 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 140 | 106 | 15901656 | 3014 | 72.336 | 3.014 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 49823932 | 956 | 317.1865 | 0% | 0% | 100% | 100% | 100% | 60% | 11218591 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 130 | 15907250 | 5594 | 134.256 | 5.594 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 49825012 | 1080 | 193.064 | 0% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 | 1.07 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 136 | 15912974 | 5724 | 137.376 | 5.724 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49826070 | 1058 | 184.8358 | 0% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 147 | 15918980 | 6006 | 144.144 | 6.006 | 9.3 | 9.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49827260 | 1190 | 198.1352 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 15925033 | 6053 | 145.272 | 6.053 | 8.8 | 8.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49828472 | 1212 | 200.2313 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 15931192 | 6159 | 147.816 | 6.159 | 8.2 | 8.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49829670 | 1198 | 194.5121 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 141 | 15937362 | 6170 | 148.08 | 6.17 | 7.6 | 7.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49830879 | 1209 | 195.9481 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 15943357 | 5995 | 143.88 | 5.995 | 7.1 | 7.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49832027 | 1148 | 191.4929 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 141 | 15949307 | 5950 | 142.8 | 5.95 | 6.6 | 6.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49833262 | 1235 | 207.563 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 132 | 15955606 | 6299 | 151.176 | 6.299 | 6.1 | 6.1 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49834534 | 1272 | 201.9368 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 143 | 15961542 | 5936 | 142.464 | 5.936 | 5.7 | 5.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49835722 | 1188 | 200.1348 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 144 | 15967504 | 5962 | 143.088 | 5.962 | 5.3 | 5.3 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49836926 | 1204 | 201.9457 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 15973206 | 5702 | 136.848 | 5.702 | 4.9 | 4.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49838056 | 1130 | 198.1761 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 15979168 | 5962 | 143.088 | 5.962 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49839244 | 1188 | 199.262 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 | 1.49 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 15985242 | 6074 | 145.776 | 6.074 | 4.2 | 4.2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49840458 | 1214 | 199.8683 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 135 | 15990922 | 5680 | 136.32 | 5.68 | 3.9 | 3.9 | 3B+1S | 995 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49841616 | 1158 | 203.8732 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 136 | 136 | 15997024 | 6102 | 146.448 | 6.102 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49842840 | 1224 | 200.59 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 132 | 16002394 | 5370 | 128.88 | 5.37 | 3.6 | 3.6 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49843968 | 1128 | 210.0559 | 100% | 0% | 100% | 100% | 100% | 0% | 11218591 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 120 | 16007422 | 5028 | 120.672 | 5.028 | 3.7 | 3.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49845006 | 1038 | 206.4439 | 0% | 0% | 100% | 100% | 100% | 30% | 11218698 | 107 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 127 | 118 | 16013042 | 5620 | 134.88 | 5.62 | 4.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49846140 | 1134 | 201.7794 | 0% | 0% | 100% | 100% | 100% | 30% | 11219055 | 357 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132360 | 132.36 | 132.36 | [12 empty] | 26846 | 26846 | 202.8256 | [6 empty] | 3233 | 3233 | 1.22 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 4, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26481 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16013042 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49846140 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11219055 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 | 103 | 16017244 | 4202 | 100.848 | 4.202 | 4.8 | 4.8 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 49847008 | 868 | 206.5683 | 0% | 0% | 100% | 100% | 100% | 60% | 11219716 | 661 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 127 | 104 | 16021584 | 4340 | 104.16 | 4.34 | 5.8 | 5.8 | 3B | 0 | 0 | 1056 | 1185 | 1057 | N/A | N/A | N/A | N/A | 49847872 | 864 | 199.0783 | 0% | 0% | 100% | 100% | 100% | 60% | 11220471 | 755 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 | 103 | 16025982 | 4398 | 105.552 | 4.398 | 6.7 | 6.7 | 3B | 0 | 0 | 1056 | 1185 | 1057 | N/A | N/A | N/A | N/A | 49848746 | 874 | 198.7267 | 0% | 0% | 100% | 100% | 100% | 60% | 11221172 | 701 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 143 | 103 | 16029989 | 4007 | 96.168 | 4.007 | 8.1 | 8.1 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 49849686 | 940 | 234.5895 | 0% | 0% | 100% | 100% | 100% | 60% | 11221449 | 277 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 124 | 16034160 | 4171 | 100.104 | 4.171 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 49850658 | 972 | 233.0376 | 0% | 0% | 100% | 100% | 100% | 60% | 11221549 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 139 | 16039989 | 5829 | 139.896 | 5.829 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49851782 | 1124 | 192.829 | 0% | 0% | 100% | 100% | 100% | 0% | 11221549 | 0 | 1.31 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 137 | 16046119 | 6130 | 147.12 | 6.13 | 9.5 | 9.5 | 3B+1S | 0 | 996 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49852966 | 1184 | 193.1485 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 141 | 16052159 | 6040 | 144.96 | 6.04 | 9.4 | 9.4 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49854142 | 1176 | 194.702 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 140 | 16058210 | 6051 | 145.224 | 6.051 | 8.9 | 8.9 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49855346 | 1204 | 198.9754 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 16064376 | 6166 | 147.984 | 6.166 | 8.5 | 8.5 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49856526 | 1180 | 191.372 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 | 1.14
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 142 | 16070530 | 6154 | 147.696 | 6.154 | 8 | 8 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49857683 | 1157 | 188.0078 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 135 | 16076702 | 6172 | 148.128 | 6.172 | 7.6 | 7.6 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49858874 | 1191 | 192.9682 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 138 | 138 | 16082545 | 5843 | 140.232 | 5.843 | 7.2 | 7.2 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49860043 | 1169 | 200.0685 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 132 | 16087599 | 5054 | 121.296 | 5.054 | 6.9 | 6.9 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49861098 | 1055 | 208.7455 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 138 | 16093244 | 5645 | 135.48 | 5.645 | 6.6 | 6.6 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49862211 | 1113 | 197.1656 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 16099181 | 5937 | 142.488 | 5.937 | 6.3 | 6.3 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49863384 | 1173 | 197.5745 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 16105022 | 5841 | 140.184 | 5.841 | 6 | 6 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49864558 | 1174 | 200.993 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 134 | 16110859 | 5837 | 140.088 | 5.837 | 5.7 | 5.7 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49865731 | 1173 | 200.9594 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 16117005 | 6146 | 147.504 | 6.146 | 5.3 | 5.3 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49866910 | 1179 | 191.8321 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 138 | 16122866 | 5861 | 140.664 | 5.861 | 5 | 5 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49868089 | 1179 | 201.1602 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 138 | 16128743 | 5877 | 141.048 | 5.877 | 4.3 | 4.3 | 3B+1S | 0 | 1057 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49869288 | 1199 | 204.0157 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 134 | 16134606 | 5863 | 140.712 | 5.863 | 3.9 | 3.9 | 3B+1S | 0 | 1057 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49870481 | 1193 | 203.4794 | 0% | 100% | 100% | 100% | 100% | 0% | 11221549 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 128 | 16140013 | 5407 | 129.768 | 5.407 | 3.7 | 3.7 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49871574 | 1093 | 202.1454 | 0% | 0% | 100% | 100% | 100% | 30% | 11221572 | 23 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 120 | 16145237 | 5224 | 125.376 | 5.224 | 4 | 4 | 3B | 0 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49872621 | 1047 | 200.4211 | 0% | 0% | 100% | 100% | 100% | 30% | 11221820 | 248 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132195 | 132.195 | 132.195 | [12 empty] | 26481 | 26481 | 200.3177 | [6 empty] | 2765 | 2765 | 1.2 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV1- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27059 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16145237 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49872621 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11221820 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 138 | 105 | 16149501 | 4264 | 102.336 | 4.264 | 5.4 | 5.4 | 3B | 0 | 0 | 1077 | 1185 | 1077 | N/A | N/A | N/A | N/A | 49873491 | 870 | 204.0338 | 0% | 0% | 100% | 100% | 100% | 70% | 11222405 | 585 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 139 | 110 | 16153721 | 4220 | 101.28 | 4.22 | 7.3 | 7.3 | 3B | 0 | 0 | 1077 | 1185 | 1077 | N/A | N/A | N/A | N/A | 49874377 | 886 | 209.9526 | 0% | 0% | 100% | 100% | 100% | 70% | 11223005 | 600 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 131 | 103 | 16158081 | 4360 | 104.64 | 4.36 | 8.1 | 8.1 | 3B | 0 | 0 | 1077 | 1185 | 1077 | N/A | N/A | N/A | N/A | 49875291 | 914 | 209.633 | 0% | 0% | 100% | 100% | 100% | 70% | 11223601 | 596 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 129 | 112 | 16162701 | 4620 | 110.88 | 4.62 | 9.3 | 9.3 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49876295 | 1004 | 217.316 | 0% | 0% | 100% | 100% | 100% | 70% | 11224206 | 605 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P.LABIAN/A.MIRAFLOR
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 117 | 16167308 | 4607 | 110.568 | 4.607 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49877310 | 1015 | 220.3169 | 0% | 0% | 100% | 100% | 100% | 70% | 11224261 | 55 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 132 | 16172876 | 5568 | 133.632 | 5.568 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49878368 | 1058 | 190.0144 | 0% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 | 1.11 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 149 | 16179574 | 6698 | 160.752 | 6.698 | 9.1 | 9.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49879734 | 1366 | 203.9415 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 16186136 | 6562 | 157.488 | 6.562 | 8.5 | 8.5 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49880974 | 1240 | 188.9668 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 141 | 16192439 | 6303 | 151.272 | 6.303 | 7.8 | 7.8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49882146 | 1172 | 185.9432 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 148 | 16198759 | 6320 | 151.68 | 6.32 | 7.2 | 7.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49883394 | 1248 | 197.4684 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 | 1.06
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 16204919 | 6160 | 147.84 | 6.16 | 6.6 | 6.6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49884597 | 1203 | 195.2922 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 140 | 16210999 | 6080 | 145.92 | 6.08 | 6.1 | 6.1 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49885779 | 1182 | 194.4079 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 135 | 141 | 16216870 | 5871 | 140.904 | 5.871 | 5.6 | 5.6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49886947 | 1168 | 198.944 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 138 | 16222532 | 5662 | 135.888 | 5.662 | 5.1 | 5.1 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49888078 | 1131 | 199.7527 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 16228758 | 6226 | 149.424 | 6.226 | 4.7 | 4.7 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49889284 | 1206 | 193.7038 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 139 | 16234648 | 5890 | 141.36 | 5.89 | 4.3 | 4.3 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49890458 | 1174 | 199.3209 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 16240708 | 6060 | 145.44 | 6.06 | 3.9 | 3.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49891660 | 1202 | 198.3498 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 134 | 16246614 | 5906 | 141.744 | 5.906 | 3.4 | 3.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49892822 | 1162 | 196.7491 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 135 | 16252572 | 5958 | 142.992 | 5.958 | 3.1 | 3.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49894034 | 1212 | 203.424 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 130 | 16258327 | 5755 | 138.12 | 5.755 | 2.9 | 2.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49895196 | 1162 | 201.9114 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 108 | 16263912 | 5585 | 134.04 | 5.585 | 2.7 | 2.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49896334 | 1138 | 203.7601 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 140 | 133 | 16269522 | 5610 | 134.64 | 5.61 | 2.5 | 2.5 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49897470 | 1136 | 202.4955 | 100% | 0% | 100% | 100% | 100% | 0% | 11224261 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 135 | 126 | 16275052 | 5530 | 132.72 | 5.53 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49898598 | 1128 | 203.9783 | 0% | 0% | 100% | 100% | 100% | 30% | 11224404 | 143 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 133 | 16280348 | 5296 | 127.104 | 5.296 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49899680 | 1082 | 204.3051 | 0% | 0% | 100% | 100% | 100% | 30% | 11224729 | 325 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135111 | 135.111 | 135.111 | [12 empty] | 27059 | 27059 | 200.2724 | [6 empty] | 2909 | 2909 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27528 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16280348 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49899680 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11224729 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 146 | 120 | 16285932 | 5584 | 134.016 | 5.584 | 3.8 | 3.8 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49900730 | 1050 | 188.0372 | 0% | 0% | 100% | 100% | 100% | 60% | 11225563 | 834 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 | 114 | 16290640 | 4708 | 112.992 | 4.708 | 4.7 | 4.7 | 3B | 0 | 0 | 1148 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49901778 | 1048 | 222.5998 | 0% | 0% | 100% | 100% | 100% | 60% | 11226215 | 652 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 132 | 108 | 16295341 | 4701 | 112.824 | 4.701 | 5.4 | 5.4 | 3B | 0 | 0 | 1148 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49902838 | 1060 | 225.4839 | 0% | 0% | 100% | 100% | 100% | 60% | 11226456 | 241 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 106 | 16299341 | 4000 | 96 | 4 | 7.8 | 7.8 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49903848 | 1010 | 252.5 | 0% | 0% | 100% | 100% | 100% | 60% | 11226656 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 121 | 16303374 | 4033 | 96.792 | 4.033 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 49904892 | 1044 | 258.8644 | 0% | 0% | 100% | 100% | 100% | 60% | 11226982 | 326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 146 | 141 | 16309044 | 5670 | 136.08 | 5.67 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49905994 | 1102 | 194.3563 | 0% | 0% | 100% | 100% | 100% | 0% | 11226982 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 150 | 16315480 | 6436 | 154.464 | 6.436 | 9.3 | 9.3 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49907267 | 1273 | 197.7937 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 152 | 16321859 | 6379 | 153.096 | 6.379 | 8.6 | 8.6 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49908507 | 1240 | 194.3878 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 16327815 | 5956 | 142.944 | 5.956 | 8 | 8 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49909680 | 1173 | 196.9443 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 16333588 | 5773 | 138.552 | 5.773 | 7.4 | 7.4 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49910814 | 1134 | 196.4317 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 | 1.16
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 16340195 | 6607 | 158.568 | 6.607 | 6.9 | 6.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49912109 | 1295 | 196.0042 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 16346269 | 6074 | 145.776 | 6.074 | 6.3 | 6.3 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49913315 | 1206 | 198.5512 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 16352174 | 5905 | 141.72 | 5.905 | 5.9 | 5.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49914490 | 1175 | 198.9839 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 16357824 | 5650 | 135.6 | 5.65 | 5.3 | 5.3 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49915614 | 1124 | 198.9381 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 144 | 16363708 | 5884 | 141.216 | 5.884 | 4.9 | 4.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49916792 | 1178 | 200.2039 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 16369604 | 5896 | 141.504 | 5.896 | 4.6 | 4.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49917960 | 1168 | 198.1004 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 16375468 | 5864 | 140.736 | 5.864 | 4.1 | 4.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49919148 | 1188 | 202.5921 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 140 | 16380926 | 5458 | 130.992 | 5.458 | 3.7 | 3.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49920266 | 1118 | 204.8369 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 16387196 | 6270 | 150.48 | 6.27 | 3.4 | 3.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49921520 | 1254 | 200 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 135 | 16393442 | 6246 | 149.904 | 6.246 | 3 | 3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49922756 | 1236 | 197.8866 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 134 | 16398644 | 5202 | 124.848 | 5.202 | 2.7 | 2.7 | 3B+1S | 0 | 1024 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49923858 | 1102 | 211.8416 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 133 | 16404242 | 5598 | 134.352 | 5.598 | 2.5 | 2.5 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49925010 | 1152 | 205.7878 | 0% | 100% | 100% | 100% | 100% | 0% | 11226982 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 126 | 16409910 | 5668 | 136.032 | 5.668 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49926154 | 1144 | 201.8349 | 0% | 0% | 100% | 100% | 100% | 30% | 11227157 | 175 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 121 | 16415012 | 5102 | 122.448 | 5.102 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49927208 | 1054 | 206.5857 | 0% | 0% | 100% | 100% | 100% | 30% | 11227568 | 411 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134664 | 134.664 | 134.664 | [12 empty] | 27528 | 27528 | 204.4199 | [6 empty] | 2839 | 2839 | 1.1667 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
AS PER (SPM) ALVIN CRUZ EFFECTIVE @ 1:00AM AUGUST 16,2016 FROM 1AM NORMALY MEET THE TARGET DISCHARGE PRESSURE @ VILLAMOR PS 75 PSI DUE TO NORMAL SUCTION PRESSURE (BACK TO NORMAL OPERATION)
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27120 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16415012 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49927208 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11227568 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 112 | 16419928 | 4916 | 117.984 | 4.916 | 3.8 | 3.8 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49928234 | 1026 | 208.7063 | 0% | 0% | 100% | 100% | 100% | 60% | 11228313 | 745 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 111 | 16424994 | 5066 | 121.584 | 5.066 | 4.9 | 4.9 | 3B | 0 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 49929252 | 1018 | 200.9475 | 0% | 0% | 100% | 100% | 100% | 60% | 11229195 | 882 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 113 | 16429666 | 4672 | 112.128 | 4.672 | 5.8 | 5.8 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49930252 | 1000 | 214.0411 | 0% | 0% | 100% | 100% | 100% | 60% | 11230019 | 824 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 112 | 16433842 | 4176 | 100.224 | 4.176 | 7.7 | 7.7 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49931292 | 1040 | 249.0421 | 0% | 0% | 100% | 100% | 100% | 60% | 11230119 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 124 | 16437862 | 4020 | 96.48 | 4.02 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49932344 | 1052 | 261.6915 | 0% | 0% | 100% | 100% | 100% | 60% | 11230140 | 21 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 131 | 16442693 | 4831 | 115.944 | 4.831 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49933355 | 1011 | 209.2734 | 0% | 0% | 100% | 100% | 100% | 0% | 112 | -11230028 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 141 | 16448568 | 5875 | 141 | 5.875 | 9.3 | 9.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49934492 | 1137 | 193.5319 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 11230028 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 16454591 | 6023 | 144.552 | 6.023 | 8.8 | 8.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49935697 | 1205 | 200.0664 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 139 | 16460524 | 5933 | 142.392 | 5.933 | 8.2 | 8.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49936881 | 1184 | 199.5618 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 141 | 16466592 | 6068 | 145.632 | 6.068 | 7.6 | 7.6 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49938084 | 1203 | 198.2531 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 | 1.2
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 138 | 16472653 | 6061 | 145.464 | 6.061 | 7.1 | 7.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49939282 | 1198 | 197.6572 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 141 | 16478857 | 6204 | 148.896 | 6.204 | 6.5 | 6.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49940475 | 1193 | 192.2953 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 135 | 16484781 | 5924 | 142.176 | 5.924 | 6.1 | 6.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49941648 | 1173 | 198.0081 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 16490685 | 5904 | 141.696 | 5.904 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49942820 | 1172 | 198.5095 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 137 | 16496613 | 5928 | 142.272 | 5.928 | 5.6 | 5.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49943989 | 1169 | 197.1997 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 16502370 | 5757 | 138.168 | 5.757 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49945147 | 1158 | 201.1464 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 16508166 | 5796 | 139.104 | 5.796 | 5 | 5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49946312 | 1165 | 201.0007 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 136 | 16513866 | 5700 | 136.8 | 5.7 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49947479 | 1167 | 204.7368 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 137 | 16519616 | 5750 | 138 | 5.75 | 4.5 | 4.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49948644 | 1165 | 202.6087 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 138 | 16525338 | 5722 | 137.328 | 5.722 | 4.3 | 4.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49949817 | 1173 | 204.9983 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 137 | 16531221 | 5883 | 141.192 | 5.883 | 3.7 | 3.7 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49951006 | 1189 | 202.1078 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 132 | 16536906 | 5685 | 136.44 | 5.685 | 3.4 | 3.4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49952175 | 1169 | 205.6288 | 100% | 0% | 100% | 100% | 100% | 0% | 11230140 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 121 | 16542010 | 5104 | 122.496 | 5.104 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49953180 | 1005 | 196.9044 | 0% | 0% | 100% | 100% | 100% | 20% | 11230180 | 40 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 126 | 120 | 16547263 | 5253 | 126.072 | 5.253 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49954328 | 1148 | 218.5418 | 0% | 0% | 100% | 100% | 100% | 20% | 11230248 | 68 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132251 | 132.251 | 132.251 | [12 empty] | 27120 | 27120 | 205.0646 | [6 empty] | 2680 | 2680 | 1.2 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## SEPT 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27258 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16547263 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49954328 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11230248 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 119 | 16551765 | 4502 | 108.048 | 4.502 | 5.2 | 5.2 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49955268 | 940 | 208.7961 | 0% | 0% | 100% | 100% | 100% | 75% | 11230865 | 617 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 110 | 16556225 | 4460 | 107.04 | 4.46 | 6.8 | 6.8 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 49956250 | 982 | 220.1794 | 0% | 0% | 100% | 100% | 100% | 75% | 11231465 | 600 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 113 | 16560893 | 4668 | 112.032 | 4.668 | 7.7 | 7.7 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 49957347 | 1097 | 235.0043 | 0% | 0% | 100% | 100% | 100% | 75% | 11232055 | 590 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 121 | 116 | 16565483 | 4590 | 110.16 | 4.59 | 8.9 | 8.9 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49958353 | 1006 | 219.1721 | 0% | 0% | 100% | 100% | 100% | 75% | 11232675 | 620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 115 | 16570227 | 4744 | 113.856 | 4.744 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 49959399 | 1046 | 220.489 | 0% | 0% | 100% | 100% | 100% | 75% | 11232816 | 141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 136 | 16575539 | 5312 | 127.488 | 5.312 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49960395 | 996 | 187.5 | 0% | 0% | 100% | 100% | 100% | 0% | 11232816 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 16582388 | 6849 | 164.376 | 6.849 | 9.2 | 9.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49961744 | 1349 | 196.9631 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 16588910 | 6522 | 156.528 | 6.522 | 8.7 | 8.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49963009 | 1265 | 193.9589 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 145 | 16594970 | 6060 | 145.44 | 6.06 | 8.1 | 8.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49964190 | 1181 | 194.8845 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 139 | 145 | 16601375 | 6405 | 153.72 | 6.405 | 7.6 | 7.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49965397 | 1207 | 188.4465 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 | 1.12
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 140 | 146 | 16607419 | 6044 | 145.056 | 6.044 | 7.2 | 7.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49966564 | 1167 | 193.0841 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 16613508 | 6089 | 146.136 | 6.089 | 6.8 | 6.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49967759 | 1195 | 196.2555 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 135 | 16619632 | 6124 | 146.976 | 6.124 | 6.4 | 6.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 49968959 | 1200 | 195.9504 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 137 | 16624966 | 5334 | 128.016 | 5.334 | 5.9 | 5.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49970012 | 1053 | 197.4128 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 139 | 16631012 | 6046 | 145.104 | 6.046 | 5.6 | 5.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49971180 | 1168 | 193.1856 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 16637080 | 6068 | 145.632 | 6.068 | 5.3 | 5.3 | 3B+1S | 0 | 1014 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49972396 | 1216 | 200.3955 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 16642618 | 5538 | 132.912 | 5.538 | 4.9 | 4.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49973524 | 1128 | 203.6836 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 141 | 16648552 | 5934 | 142.416 | 5.934 | 4.7 | 4.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49974718 | 1194 | 201.2133 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 136 | 16654446 | 5894 | 141.456 | 5.894 | 4.4 | 4.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49975856 | 1138 | 193.0777 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 134 | 16660322 | 5876 | 141.024 | 5.876 | 4 | 4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49977010 | 1154 | 196.3921 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 131 | 16666264 | 5942 | 142.608 | 5.942 | 3.8 | 3.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49978218 | 1208 | 203.2986 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 132 | 16671992 | 5728 | 137.472 | 5.728 | 3.7 | 3.7 | 3B+1S | 0 | 1003 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49979376 | 1158 | 202.1648 | 0% | 100% | 100% | 100% | 100% | 0% | 11232816 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 133 | 16677762 | 5770 | 138.48 | 5.77 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49980466 | 1090 | 188.9081 | 0% | 0% | 100% | 100% | 100% | 30% | 11232916 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 125 | 130 | 16683432 | 5670 | 136.08 | 5.67 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 49981586 | 1120 | 197.5309 | 0% | 0% | 100% | 100% | 100% | 30% | 11233046 | 130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136169 | 136.169 | 136.169 | [12 empty] | 27258 | 27258 | 200.1777 | [6 empty] | 2798 | 2798 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27078 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16683432 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 49981586 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11233046 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 116 | 16687626 | 4194 | 100.656 | 4.194 | 4.6 | 4.6 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 49982606 | 1020 | 243.2046 | 0% | 0% | 100% | 100% | 100% | 60% | 11233640 | 594 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 114 | 16692498 | 4872 | 116.928 | 4.872 | 5.3 | 5.3 | 3B | 0 | 0 | 1148 | 1185 | 1148 | N/A | N/A | N/A | N/A | 49983618 | 1012 | 207.7176 | 0% | 0% | 100% | 100% | 100% | 60% | 11234380 | 740 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 116 | 16697176 | 4678 | 112.272 | 4.678 | 6.2 | 6.2 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 49984588 | 970 | 207.3536 | 0% | 0% | 100% | 100% | 100% | 60% | 11235084 | 704 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 110 | 16701426 | 4250 | 102 | 4.25 | 8.1 | 8.1 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 49985594 | 1006 | 236.7059 | 0% | 0% | 100% | 100% | 100% | 60% | 11235184 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 114 | 16705692 | 4266 | 102.384 | 4.266 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 49986662 | 1068 | 250.3516 | 0% | 0% | 100% | 100% | 100% | 60% | 11235205 | 21 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 123 | 134 | 16710989 | 5297 | 127.128 | 5.297 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49987762 | 1100 | 207.6647 | 0% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 | 1.18 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 150 | 16716745 | 5756 | 138.144 | 5.756 | 9.4 | 9.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49988881 | 1119 | 194.4058 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 152 | 16722900 | 6155 | 147.72 | 6.155 | 9.1 | 9.1 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49990019 | 1138 | 184.8903 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 152 | 16729178 | 6278 | 150.672 | 6.278 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49991179 | 1160 | 184.7722 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 145 | 16735421 | 6243 | 149.832 | 6.243 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49992395 | 1216 | 194.7782 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 | 1.07
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 16741812 | 6391 | 153.384 | 6.391 | 7.4 | 7.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49993610 | 1215 | 190.1111 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 16747879 | 6067 | 145.608 | 6.067 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49994820 | 1210 | 199.4396 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 135 | 16753773 | 5894 | 141.456 | 5.894 | 6.1 | 6.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49995993 | 1173 | 199.0159 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 139 | 16759138 | 5365 | 128.76 | 5.365 | 5.6 | 5.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49997044 | 1051 | 195.8993 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 137 | 16764974 | 5836 | 140.064 | 5.836 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49998236 | 1192 | 204.2495 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 16771114 | 6140 | 147.36 | 6.14 | 4.7 | 4.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49999411 | 1175 | 191.3681 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 16777231 | 6117 | 146.808 | 6.117 | 4.2 | 4.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50000589 | 1178 | 192.5781 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 125 | 16782970 | 5739 | 137.736 | 5.739 | 3.8 | 3.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50001759 | 1170 | 203.8683 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 136 | 16788762 | 5792 | 139.008 | 5.792 | 3.6 | 3.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50002918 | 1159 | 200.1036 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 139 | 16794667 | 5905 | 141.72 | 5.905 | 3.3 | 3.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50004084 | 1166 | 197.4598 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 134 | 16800419 | 5752 | 138.048 | 5.752 | 2.9 | 2.9 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50005266 | 1182 | 205.4937 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 133 | 16806418 | 5999 | 143.976 | 5.999 | 2.6 | 2.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50006504 | 1238 | 206.3677 | 100% | 0% | 100% | 100% | 100% | 0% | 11235205 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 126 | 125 | 16811768 | 5350 | 128.4 | 5.35 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50007606 | 1102 | 205.9813 | 0% | 0% | 100% | 100% | 100% | 30% | 11235407 | 202 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 123 | 16816462 | 4694 | 112.656 | 4.694 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50008664 | 1058 | 225.3941 | 0% | 0% | 100% | 100% | 100% | 30% | 11235911 | 504 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133030 | 133.03 | 133.03 | [12 empty] | 27078 | 27078 | 203.5481 | [6 empty] | 2865 | 2865 | 1.1233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27218 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16816462 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50008664 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11235911 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 115 | 16822110 | 5648 | 135.552 | 5.648 | 4 | 4 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50009750 | 1086 | 192.2805 | 0% | 0% | 100% | 100% | 100% | 60% | 11236557 | 646 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 116 | 16826942 | 4832 | 115.968 | 4.832 | 5.3 | 5.3 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50010748 | 998 | 206.5397 | 0% | 0% | 100% | 100% | 100% | 60% | 11237388 | 831 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 111 | 16831762 | 4820 | 115.68 | 4.82 | 5.8 | 5.8 | 3B | 0 | 0 | 1126 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50011742 | 994 | 206.2241 | 0% | 0% | 100% | 100% | 100% | 60% | 11238109 | 721 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 134 | 110 | 16836022 | 4260 | 102.24 | 4.26 | 7.8 | 7.8 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50012618 | 876 | 205.6338 | 0% | 0% | 100% | 100% | 100% | 60% | 11238200 | 91 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 119 | 16840120 | 4098 | 98.352 | 4.098 | 9.5 | 9.5 | 3B | 0 | 0 | 1086 | 1185 | 1087 | N/A | N/A | N/A | N/A | 50013468 | 850 | 207.4183 | 0% | 0% | 100% | 100% | 100% | 60% | 11238209 | 9 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 133 | 133 | 16844862 | 4742 | 113.808 | 4.742 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50014869 | 1401 | 295.445 | 0% | 0% | 100% | 100% | 100% | 0% | 11238209 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 140 | 16850747 | 5885 | 141.24 | 5.885 | 9.5 | 9.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50016061 | 1192 | 202.5489 | 0% | 0% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 16856792 | 6045 | 145.08 | 6.045 | 9.4 | 9.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50017189 | 1128 | 186.6005 | 0% | 0% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 144 | 16863034 | 6242 | 149.808 | 6.242 | 9.3 | 9.3 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50018385 | 1196 | 191.6053 | 0% | 0% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 123 | 144 | 16869038 | 6004 | 144.096 | 6.004 | 8.7 | 8.7 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50019593 | 1208 | 201.1992 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 | 1.18
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 123 | 143 | 16875399 | 6361 | 152.664 | 6.361 | 8 | 8 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50020808 | 1215 | 191.0077 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 125 | 145 | 16881482 | 6083 | 145.992 | 6.083 | 7.3 | 7.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50021954 | 1146 | 188.3939 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 135 | 16887605 | 6123 | 146.952 | 6.123 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50023209 | 1255 | 204.9649 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 132 | 16893230 | 5625 | 135 | 5.625 | 6.3 | 6.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50024336 | 1127 | 200.3556 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 16898980 | 5750 | 138 | 5.75 | 5.8 | 5.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50025488 | 1152 | 200.3478 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 16904805 | 5825 | 139.8 | 5.825 | 5.4 | 5.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50026669 | 1181 | 202.7468 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 16910657 | 5852 | 140.448 | 5.852 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50027850 | 1181 | 201.8113 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 144 | 16916722 | 6065 | 145.56 | 6.065 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50029036 | 1186 | 195.5482 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 140 | 16922611 | 5889 | 141.336 | 5.889 | 4.2 | 4.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50030217 | 1181 | 200.5434 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 137 | 16928402 | 5791 | 138.984 | 5.791 | 3.8 | 3.8 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50031388 | 1171 | 202.2103 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 134 | 16934077 | 5675 | 136.2 | 5.675 | 3.5 | 3.5 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50032537 | 1149 | 202.467 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 131 | 16939806 | 5729 | 137.496 | 5.729 | 3.2 | 3.2 | 3B+1S | 0 | 1044 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50033698 | 1161 | 202.6532 | 0% | 100% | 100% | 100% | 100% | 0% | 11238209 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 123 | 16945112 | 5306 | 127.344 | 5.306 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50034798 | 1100 | 207.3125 | 0% | 0% | 100% | 100% | 100% | 30% | 11238363 | 154 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 120 | 16950338 | 5226 | 125.424 | 5.226 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50035882 | 1084 | 207.4244 | 0% | 0% | 100% | 100% | 100% | 30% | 11238859 | 496 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133876 | 133.876 | 133.876 | [12 empty] | 27218 | 27218 | 203.3075 | [6 empty] | 2948 | 2948 | 1.1283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26748 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 16950338 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50035882 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11238859 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 134 | 113 | 16955304 | 4966 | 119.184 | 4.966 | 4.4 | 4.4 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 50036934 | 1052 | 211.8405 | 0% | 0% | 100% | 100% | 100% | 60% | 11239350 | 491 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 136 | 116 | 16959822 | 4518 | 108.432 | 4.518 | 5.6 | 5.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50037872 | 938 | 207.614 | 0% | 0% | 100% | 100% | 100% | 60% | 11239988 | 638 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 113 | 16964356 | 4534 | 108.816 | 4.534 | 6.3 | 6.3 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50038808 | 936 | 206.4402 | 0% | 0% | 100% | 100% | 100% | 60% | 11240698 | 710 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 115 | 16967624 | 3268 | 78.432 | 3.268 | 8 | 8 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50039786 | 978 | 299.2656 | 0% | 0% | 100% | 100% | 100% | 60% | 11240918 | 220 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 114 | 111 | 16970750 | 3126 | 75.024 | 3.126 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50040740 | 954 | 305.1823 | 0% | 0% | 100% | 100% | 100% | 60% | 11241020 | 102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 129 | 124 | 16976993 | 6243 | 149.832 | 6.243 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50041724 | 984 | 157.6165 | 0% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 135 | 16983032 | 6039 | 144.936 | 6.039 | 9.5 | 9.5 | 3B | 0 | 0 | 1168 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50042706 | 982 | 162.6097 | 0% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 138 | 16989370 | 6338 | 152.112 | 6.338 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50043877 | 1171 | 184.7586 | 0% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 16995748 | 6378 | 153.072 | 6.378 | 9 | 9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50045058 | 1181 | 185.1678 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 17002060 | 6312 | 151.488 | 6.312 | 8.4 | 8.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50046283 | 1225 | 194.0748 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 | 1.09
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 17008120 | 6060 | 145.44 | 6.06 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50047482 | 1199 | 197.8548 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 145 | 17014172 | 6052 | 145.248 | 6.052 | 7.1 | 7.1 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50048674 | 1192 | 196.9597 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 147 | 17020309 | 6137 | 147.288 | 6.137 | 6.3 | 6.3 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50049923 | 1249 | 203.5196 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 141 | 17026139 | 5830 | 139.92 | 5.83 | 5.5 | 5.5 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50051079 | 1156 | 198.2847 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 141 | 17032171 | 6032 | 144.768 | 6.032 | 4.9 | 4.9 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50052284 | 1205 | 199.7679 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 17038205 | 6034 | 144.816 | 6.034 | 4.3 | 4.3 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50053486 | 1202 | 199.2045 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 17044107 | 5902 | 141.648 | 5.902 | 3.7 | 3.7 | 3B+1S | 1066 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50054685 | 1199 | 203.1515 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 140 | 17050027 | 5920 | 142.08 | 5.92 | 3.2 | 3.2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50055880 | 1195 | 201.8581 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 138 | 17055840 | 5813 | 139.512 | 5.813 | 2.9 | 2.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50057057 | 1177 | 202.4772 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 141 | 17061630 | 5790 | 138.96 | 5.79 | 2.7 | 2.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50058228 | 1171 | 202.2453 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 138 | 17067359 | 5729 | 137.496 | 5.729 | 2.4 | 2.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50059402 | 1174 | 204.9223 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 136 | 130 | 17072667 | 5308 | 127.392 | 5.308 | 2.4 | 2.4 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50060469 | 1067 | 201.0173 | 100% | 0% | 100% | 100% | 100% | 0% | 11241020 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 126 | 17078122 | 5455 | 130.92 | 5.455 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50061537 | 1068 | 195.7837 | 0% | 0% | 100% | 100% | 100% | 20% | 11241162 | 142 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 121 | 17083242 | 5120 | 122.88 | 5.12 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50062630 | 1093 | 213.4766 | 0% | 0% | 100% | 100% | 100% | 20% | 11241624 | 462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132904 | 132.904 | 132.904 | [12 empty] | 26748 | 26748 | 201.2581 | [6 empty] | 2765 | 2765 | 1.1717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## SEPT 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27328 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17083242 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50062630 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11241624 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 109 | 17087686 | 4444 | 106.656 | 4.444 | 4.1 | 4.1 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50063577 | 947 | 213.0963 | 0% | 0% | 100% | 100% | 100% | 75% | 11242267 | 643 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 103 | 17092166 | 4480 | 107.52 | 4.48 | 6.3 | 6.3 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50064497 | 920 | 205.3571 | 0% | 0% | 100% | 100% | 100% | 75% | 11242877 | 610 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 107 | 17096716 | 4550 | 109.2 | 4.55 | 7.5 | 7.5 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50065593 | 1096 | 240.8791 | 0% | 0% | 100% | 100% | 100% | 75% | 11243537 | 660 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 129 | 118 | 17101269 | 4553 | 109.272 | 4.553 | 8.9 | 8.9 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 50066612 | 1019 | 223.8085 | 0% | 0% | 100% | 100% | 100% | 75% | 11244217 | 680 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 124 | 17105966 | 4697 | 112.728 | 4.697 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 50067671 | 1059 | 225.4631 | 0% | 0% | 100% | 100% | 100% | 75% | 11244397 | 180 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 139 | 17112209 | 6243 | 149.832 | 6.243 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50068933 | 1262 | 202.1464 | 0% | 0% | 100% | 100% | 100% | 0% | 11244397 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 140 | 17118466 | 6257 | 150.168 | 6.257 | 8.9 | 8.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50070146 | 1213 | 193.8629 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 17124556 | 6090 | 146.16 | 6.09 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50071336 | 1190 | 195.4023 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 143 | 17130772 | 6216 | 149.184 | 6.216 | 7.8 | 7.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50072543 | 1207 | 194.1763 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 145 | 17136872 | 6100 | 146.4 | 6.1 | 7.2 | 7.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50073663 | 1120 | 183.6066 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 | 1.09
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 17143023 | 6151 | 147.624 | 6.151 | 6.7 | 6.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50074941 | 1278 | 207.7711 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 17149292 | 6269 | 150.456 | 6.269 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50076198 | 1257 | 200.5104 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 139 | 17154857 | 5565 | 133.56 | 5.565 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50077259 | 1061 | 190.6559 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 132 | 17160551 | 5694 | 136.656 | 5.694 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50078424 | 1165 | 204.6013 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 131 | 17166345 | 5794 | 139.056 | 5.794 | 5.1 | 5.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50079584 | 1160 | 200.2071 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 132 | 17172161 | 5816 | 139.584 | 5.816 | 4.9 | 4.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50080750 | 1166 | 200.4814 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 17177993 | 5832 | 139.968 | 5.832 | 4.8 | 4.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50081921 | 1171 | 200.7888 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 136 | 17183785 | 5792 | 139.008 | 5.792 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50083081 | 1160 | 200.2762 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 135 | 137 | 17189644 | 5859 | 140.616 | 5.859 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50084258 | 1177 | 200.8875 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 136 | 17195544 | 5900 | 141.6 | 5.9 | 3.9 | 3.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50085434 | 1176 | 199.322 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 139 | 17201387 | 5843 | 140.232 | 5.843 | 3.6 | 3.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50086615 | 1181 | 202.1222 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 149 | 137 | 17207404 | 6017 | 144.408 | 6.017 | 3.3 | 3.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50087826 | 1211 | 201.2631 | 0% | 100% | 100% | 100% | 100% | 0% | 11244397 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 128 | 17212718 | 5314 | 127.536 | 5.314 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50088906 | 1080 | 203.2367 | 0% | 0% | 100% | 100% | 100% | 30% | 11244585 | 188 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 141 | 124 | 17217884 | 5166 | 123.984 | 5.166 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50089958 | 1052 | 203.6392 | 0% | 0% | 100% | 100% | 100% | 30% | 11245008 | 423 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134642 | 134.642 | 134.642 | [12 empty] | 27328 | 27328 | 202.9679 | [6 empty] | 3384 | 3384 | 1.1433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27102 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17217884 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50089958 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11245008 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 120 | 17223078 | 5194 | 124.656 | 5.194 | 4.5 | 4.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50091018 | 1060 | 204.0816 | 0% | 0% | 100% | 100% | 100% | 60% | 11245458 | 450 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 111 | 17228048 | 4970 | 119.28 | 4.97 | 5.4 | 5.4 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50092028 | 1010 | 203.2193 | 0% | 0% | 100% | 100% | 100% | 60% | 11246106 | 648 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 107 | 17232702 | 4654 | 111.696 | 4.654 | 6.3 | 6.3 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50092972 | 944 | 202.8363 | 0% | 0% | 100% | 100% | 100% | 60% | 11246804 | 698 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 | 110 | 17236862 | 4160 | 99.84 | 4.16 | 8.3 | 8.3 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50093942 | 970 | 233.1731 | 0% | 0% | 100% | 100% | 100% | 60% | 11247104 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 112 | 17240986 | 4124 | 98.976 | 4.124 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1107 | N/A | N/A | N/A | N/A | 50094908 | 966 | 234.2386 | 0% | 0% | 100% | 100% | 100% | 60% | 11247231 | 127 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 133 | 17247066 | 6080 | 145.92 | 6.08 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50096097 | 1189 | 195.5592 | 0% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 | 1.11 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 144 | 17253121 | 6055 | 145.32 | 6.055 | 9.1 | 9.1 | 3B + 1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50097302 | 1205 | 199.0091 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 17259204 | 6083 | 145.992 | 6.083 | 8.5 | 8.5 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50098451 | 1149 | 188.8871 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 145 | 17265305 | 6101 | 146.424 | 6.101 | 7.8 | 7.8 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50099669 | 1218 | 199.6394 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 17271459 | 6154 | 147.696 | 6.154 | 7.3 | 7.3 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50100882 | 1213 | 197.1076 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 | 1.06
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 17277694 | 6235 | 149.64 | 6.235 | 6.9 | 6.9 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50102145 | 1263 | 202.5662 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 17283835 | 6141 | 147.384 | 6.141 | 6.1 | 6.1 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50103284 | 1139 | 185.4747 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 146 | 17290029 | 6194 | 148.656 | 6.194 | 5.5 | 5.5 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50104514 | 1230 | 198.5793 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 17295585 | 5556 | 133.344 | 5.556 | 5.2 | 5.2 | 3B + 1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50105646 | 1132 | 203.7437 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 17301103 | 5518 | 132.432 | 5.518 | 5 | 5 | 3B + 1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50106769 | 1123 | 203.5158 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 140 | 17306976 | 5873 | 140.952 | 5.873 | 4.8 | 4.8 | 3B + 1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50107940 | 1171 | 199.387 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 17313012 | 6036 | 144.864 | 6.036 | 4.5 | 4.5 | 3B + 1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50109116 | 1176 | 194.831 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 | 138 | 17318799 | 5787 | 138.888 | 5.787 | 4.2 | 4.2 | 3B + 1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50110285 | 1169 | 202.0045 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 17324530 | 5731 | 137.544 | 5.731 | 3.9 | 3.9 | 3B + 1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50111458 | 1173 | 204.6763 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 138 | 17330300 | 5770 | 138.48 | 5.77 | 3.6 | 3.6 | 3B + 1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50112625 | 1167 | 202.253 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 133 | 17336202 | 5902 | 141.648 | 5.902 | 3.3 | 3.3 | 3B + 1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50113808 | 1183 | 200.4405 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 129 | 17341988 | 5786 | 138.864 | 5.786 | 3.2 | 3.2 | 3B + 1S | 1024 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50115004 | 1196 | 206.7058 | 100% | 0% | 100% | 100% | 100% | 0% | 11247231 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 124 | 17347012 | 5024 | 120.576 | 5.024 | 3.3 | 3.3 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50116032 | 1028 | 204.6178 | 0% | 0% | 100% | 100% | 100% | 30% | 11247358 | 127 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 115 | 17352016 | 5004 | 120.096 | 5.004 | 4.2 | 4.2 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50117060 | 1028 | 205.4357 | 0% | 0% | 100% | 100% | 100% | 30% | 11248166 | 808 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134132 | 134.132 | 134.132 | [12 empty] | 27102 | 27102 | 202.0547 | [6 empty] | 3158 | 3158 | 1.0967 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27148 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17352016 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50117060 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11248166 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 112 | 17357016 | 5000 | 120 | 5 | 4.7 | 4.7 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50118074 | 1014 | 202.8 | 0% | 0% | 100% | 100% | 100% | 60% | 11248666 | 500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 109 | 17361664 | 4648 | 111.552 | 4.648 | 5.6 | 5.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50119034 | 960 | 206.5404 | 0% | 0% | 100% | 100% | 100% | 60% | 11249349 | 683 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 106 | 17366296 | 4632 | 111.168 | 4.632 | 6.4 | 6.4 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50119986 | 952 | 205.5268 | 0% | 0% | 100% | 100% | 100% | 60% | 11250032 | 683 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 105 | 17370476 | 4180 | 100.32 | 4.18 | 8 | 8 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50120946 | 960 | 229.6651 | 0% | 0% | 100% | 100% | 100% | 60% | 11250232 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 115 | 17374676 | 4200 | 100.8 | 4.2 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50121924 | 978 | 232.8571 | 0% | 0% | 100% | 100% | 100% | 60% | 11250356 | 124 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 134 | 17379731 | 5055 | 121.32 | 5.055 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50122887 | 963 | 190.5045 | 0% | 0% | 100% | 100% | 100% | 0% | 11250356 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 147 | 17385897 | 6166 | 147.984 | 6.166 | 9 | 9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50124084 | 1197 | 194.1291 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 17391984 | 6087 | 146.088 | 6.087 | 8.4 | 8.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50125279 | 1195 | 196.32 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 141 | 17397970 | 5986 | 143.664 | 5.986 | 7.9 | 7.9 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50126464 | 1185 | 197.9619 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 147 | 17404385 | 6415 | 153.96 | 6.415 | 7.1 | 7.1 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50127687 | 1223 | 190.6469 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 | 0.99
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 150 | 17410630 | 6245 | 149.88 | 6.245 | 6.4 | 6.4 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50128917 | 1230 | 196.9576 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 143 | 17416808 | 6178 | 148.272 | 6.178 | 5.6 | 5.6 | 3B+1S | 0 | 1128 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50130156 | 1239 | 200.5503 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 137 | 17422849 | 6041 | 144.984 | 6.041 | 4.9 | 4.9 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50131369 | 1213 | 200.7946 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 17429025 | 6176 | 148.224 | 6.176 | 4.3 | 4.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50132663 | 1294 | 209.5207 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 139 | 147 | 17435074 | 6049 | 145.176 | 6.049 | 4 | 4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50133837 | 1174 | 194.0817 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 136 | 17440933 | 5859 | 140.616 | 5.859 | 3.8 | 3.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50134996 | 1159 | 197.8153 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 138 | 17446706 | 5773 | 138.552 | 5.773 | 3.6 | 3.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50136163 | 1167 | 202.1479 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 137 | 134 | 17452527 | 5821 | 139.704 | 5.821 | 3.4 | 3.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50137330 | 1167 | 200.481 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 138 | 17458366 | 5839 | 140.136 | 5.839 | 3.3 | 3.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50138494 | 1164 | 199.3492 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 134 | 17464212 | 5846 | 140.304 | 5.846 | 3.1 | 3.1 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50139659 | 1165 | 199.2816 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 140 | 17470184 | 5972 | 143.328 | 5.972 | 2.9 | 2.9 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50140835 | 1176 | 196.919 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 134 | 17476202 | 6018 | 144.432 | 6.018 | 2.5 | 2.5 | 3B+1S | 0 | 1044 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50142030 | 1195 | 198.571 | 0% | 100% | 100% | 100% | 100% | 0% | 11250356 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 122 | 17481466 | 5264 | 126.336 | 5.264 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50143098 | 1068 | 202.8875 | 0% | 0% | 100% | 100% | 100% | 30% | 11250438 | 82 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 128 | 17486926 | 5460 | 131.04 | 5.46 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50144208 | 1110 | 203.2967 | 0% | 0% | 100% | 100% | 100% | 30% | 11250712 | 274 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134910 | 134.91 | 134.91 | [12 empty] | 27148 | 27148 | 201.2304 | [6 empty] | 2546 | 2546 | 1.0867 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27358 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17486926 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50144208 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11250712 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 148 | 117 | 17492028 | 5102 | 122.448 | 5.102 | 3.5 | 3.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50145256 | 1048 | 205.4096 | 0% | 0% | 100% | 100% | 100% | 60% | 11251475 | 763 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 114 | 17497028 | 5000 | 120 | 5 | 4.7 | 4.7 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50146286 | 1030 | 206 | 0% | 0% | 100% | 100% | 100% | 60% | 11252375 | 900 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 112 | 17502048 | 5020 | 120.48 | 5.02 | 5.6 | 5.6 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50147318 | 1032 | 205.5777 | 0% | 0% | 100% | 100% | 100% | 60% | 11253116 | 741 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 132 | 110 | 17506348 | 4300 | 103.2 | 4.3 | 7.4 | 7.4 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50148318 | 1000 | 232.5581 | 0% | 0% | 100% | 100% | 100% | 60% | 11253316 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 134 | 125 | 17510758 | 4410 | 105.84 | 4.41 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50149380 | 1062 | 240.8163 | 0% | 0% | 100% | 100% | 100% | 60% | 11253343 | 27 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 145 | 145 | 17516872 | 6114 | 146.736 | 6.114 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50150557 | 1177 | 192.509 | 0% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 | 1.04 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 149 | 17523092 | 6220 | 149.28 | 6.22 | 9.2 | 9.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50151780 | 1223 | 196.6238 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 144 | 17529246 | 6154 | 147.696 | 6.154 | 8.6 | 8.6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50152954 | 1174 | 190.7702 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 144 | 17535458 | 6212 | 149.088 | 6.212 | 8 | 8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50154177 | 1223 | 196.877 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 14 | 17541642 | 6184 | 148.416 | 6.184 | 7.6 | 7.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50155454 | 1277 | 206.5006 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 | 1.12
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 142 | 17547857 | 6215 | 149.16 | 6.215 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50156683 | 1229 | 197.7474 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 137 | 17553980 | 6123 | 146.952 | 6.123 | 6.3 | 6.3 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50157806 | 1123 | 183.4068 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 137 | 17560020 | 6040 | 144.96 | 6.04 | 5.9 | 5.9 | 3B+1S | 1038 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50158914 | 1108 | 183.4437 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 17565467 | 5447 | 130.728 | 5.447 | 5.6 | 5.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50160045 | 1131 | 207.6372 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 135 | 17570923 | 5456 | 130.944 | 5.456 | 5.3 | 5.3 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50161206 | 1161 | 212.7933 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 144 | 17576853 | 5930 | 142.32 | 5.93 | 5 | 5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50162373 | 1167 | 196.796 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 17582796 | 5943 | 142.632 | 5.943 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50163560 | 1187 | 199.7308 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 140 | 17588545 | 5749 | 137.976 | 5.749 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50164722 | 1162 | 202.1221 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 139 | 17594352 | 5807 | 139.368 | 5.807 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50165896 | 1174 | 202.1698 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 137 | 17600043 | 5691 | 136.584 | 5.691 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50167064 | 1168 | 205.2363 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 135 | 17605784 | 5741 | 137.784 | 5.741 | 3.4 | 3.4 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50168235 | 1171 | 203.9714 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 132 | 17611572 | 5788 | 138.912 | 5.788 | 3.2 | 3.2 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50169404 | 1169 | 201.9696 | 100% | 0% | 100% | 100% | 100% | 0% | 11253343 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 123 | 17616844 | 5272 | 126.528 | 5.272 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50170498 | 1094 | 207.5114 | 0% | 0% | 100% | 100% | 100% | 30% | 11253453 | 110 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 122 | 17621966 | 5122 | 122.928 | 5.122 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50171566 | 1068 | 208.5123 | 0% | 0% | 100% | 100% | 100% | 30% | 11253694 | 241 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135040 | 135.04 | 135.04 | [12 empty] | 27358 | 27358 | 202.5918 | [6 empty] | 2982 | 2982 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:36 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27208 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17621966 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50171566 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11253694 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 116 | 17627018 | 5052 | 121.248 | 5.052 | 4.3 | 4.3 | 3B | 0 | 0 | 1167 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50172572 | 1006 | 199.1291 | 0% | 0% | 100% | 100% | 100% | 60% | 11254236 | 542 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 115 | 17631454 | 4436 | 106.464 | 4.436 | 4.9 | 4.9 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50173524 | 952 | 214.6078 | 0% | 0% | 100% | 100% | 100% | 60% | 11254778 | 542 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 108 | 17636266 | 4812 | 115.488 | 4.812 | 5.5 | 5.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50174538 | 1014 | 210.7232 | 0% | 0% | 100% | 100% | 100% | 60% | 11255277 | 499 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 112 | 17640284 | 4018 | 96.432 | 4.018 | 6.9 | 6.9 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50175576 | 1038 | 258.3375 | 0% | 0% | 100% | 100% | 100% | 60% | 11255377 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 119 | 117 | 17644308 | 4024 | 96.576 | 4.024 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1855 | 1126 | N/A | N/A | N/A | N/A | 50176608 | 1032 | 256.4612 | 0% | 0% | 100% | 100% | 100% | 60% | 11255392 | 15 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 | 143 | 17650276 | 5968 | 143.232 | 5.968 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1156 | N/A | N/A | N/A | N/A | 50177698 | 1090 | 182.6408 | 0% | 0% | 100% | 100% | 100% | 0% | 11255392 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 146 | 140 | 17656338 | 6062 | 145.488 | 6.062 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50178808 | 1110 | 183.1079 | 0% | 0% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 142 | 17662454 | 6116 | 146.784 | 6.116 | 9.1 | 9.1 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50179975 | 1167 | 190.811 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 144 | 17668653 | 6199 | 148.776 | 6.199 | 8.6 | 8.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50181228 | 1253 | 202.1294 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 17674810 | 6157 | 147.768 | 6.157 | 7.9 | 7.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50182346 | 1118 | 181.5819 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 | 1.01
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 142 | 17681055 | 6245 | 149.88 | 6.245 | 7.2 | 7.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50183631 | 1285 | 205.7646 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 17687326 | 6271 | 150.504 | 6.271 | 6.6 | 6.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50184846 | 1215 | 193.749 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 137 | 17693179 | 5853 | 140.472 | 5.853 | 5.9 | 5.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50186051 | 1205 | 205.8773 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 17698388 | 5209 | 125.016 | 5.209 | 5.4 | 5.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50187097 | 1046 | 200.8063 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 140 | 17704230 | 5842 | 140.208 | 5.842 | 4.9 | 4.9 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50188278 | 1181 | 202.1568 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 137 | 17710167 | 5937 | 142.488 | 5.937 | 4.6 | 4.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50189459 | 1181 | 198.922 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 141 | 17716103 | 5936 | 142.464 | 5.936 | 4.4 | 4.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50190635 | 1176 | 198.1132 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 133 | 17721913 | 5810 | 139.44 | 5.81 | 4 | 4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50191807 | 1172 | 201.7212 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 137 | 17727679 | 5766 | 138.384 | 5.766 | 3.7 | 3.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50192978 | 1171 | 203.0871 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 139 | 17733588 | 5909 | 141.816 | 5.909 | 3.5 | 3.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50194151 | 1173 | 198.5107 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 138 | 17739490 | 5902 | 141.648 | 5.902 | 3 | 3 | 3B+1S | 0 | 1075 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50195348 | 1197 | 202.8126 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 134 | 17745642 | 6152 | 147.648 | 6.152 | 2.6 | 2.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50196598 | 1250 | 203.186 | 0% | 100% | 100% | 100% | 100% | 0% | 11255392 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 138 | 126 | 17750992 | 5350 | 128.4 | 5.35 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50197696 | 1098 | 205.2336 | 0% | 0% | 100% | 100% | 100% | 30% | 11255542 | 150 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 129 | 17756268 | 5276 | 126.624 | 5.276 | 3.1 | 3.1 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50198774 | 1078 | 204.3215 | 0% | 0% | 100% | 100% | 100% | 30% | 11255858 | 316 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134302 | 134.302 | 134.302 | [12 empty] | 27208 | 27208 | 202.5882 | [6 empty] | 2164 | 2164 | 1.13 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
BP1 STOPPED @ 12:01AM DUE TO EXPERIMENT TO THE SCHEDULED FOR ANNUAL PREVENTED MAINTENANCE
BP1- STARTED @ 12:15 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27010 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17756268 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50198774 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11255858 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 140 | 116 | 17761346 | 5078 | 121.872 | 5.078 | 3.7 | 3.7 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50199792 | 1018 | 200.4726 | 0% | 0% | 100% | 100% | 100% | 60% | 11256522 | 664 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 115 | 17766156 | 4810 | 115.44 | 4.81 | 4.8 | 4.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50200806 | 1014 | 210.8108 | 0% | 0% | 100% | 100% | 100% | 60% | 11257432 | 910 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 118 | 17771006 | 4850 | 116.4 | 4.85 | 5.8 | 5.8 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50201804 | 998 | 205.7732 | 0% | 0% | 100% | 100% | 100% | 60% | 11258150 | 718 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 114 | 17775286 | 4280 | 102.72 | 4.28 | 7.8 | 7.8 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50202872 | 1068 | 249.5327 | 0% | 0% | 100% | 100% | 100% | 60% | 11258340 | 190 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 144 | 17779562 | 4276 | 102.624 | 4.276 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1855 | 1147 | N/A | N/A | N/A | N/A | 50203916 | 1044 | 244.1534 | 0% | 0% | 100% | 100% | 100% | 60% | 11258376 | 36 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 145 | 17785437 | 5875 | 141 | 5.875 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 50205070 | 1154 | 196.4255 | 0% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 144 | 17791213 | 5776 | 138.624 | 5.776 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50206099 | 1029 | 178.151 | 0% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 142 | 17796942 | 5729 | 137.496 | 5.729 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50207099 | 1000 | 174.5505 | 0% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 145 | 17802937 | 5995 | 143.88 | 5.995 | 9 | 9 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50208294 | 1195 | 199.3328 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 147 | 17809161 | 6224 | 149.376 | 6.224 | 8.4 | 8.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50209438 | 1144 | 183.8046 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 | 1.03
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 17815435 | 6274 | 150.576 | 6.274 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50210718 | 1280 | 204.0166 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 142 | 17821701 | 6266 | 150.384 | 6.266 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50211973 | 1255 | 200.2873 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 141 | 17827783 | 6082 | 145.968 | 6.082 | 6.5 | 6.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50213157 | 1184 | 194.6728 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 138 | 17833942 | 6159 | 147.816 | 6.159 | 6 | 6 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50214362 | 1205 | 195.6486 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 137 | 17839502 | 5560 | 133.44 | 5.56 | 5.6 | 5.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50215486 | 1124 | 202.1583 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 143 | 17845544 | 6042 | 145.008 | 6.042 | 5.2 | 5.2 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50216654 | 1168 | 193.3135 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 17851314 | 5770 | 138.48 | 5.77 | 4.8 | 4.8 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50217808 | 1154 | 200 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 138 | 17857296 | 5982 | 143.568 | 5.982 | 4.4 | 4.4 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50219028 | 1220 | 203.9452 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 140 | 17862992 | 5696 | 136.704 | 5.696 | 4 | 4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50220200 | 1172 | 205.7584 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 136 | 128 | 17868624 | 5632 | 135.168 | 5.632 | 3.9 | 3.9 | 3B+1S | 974 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50221350 | 1150 | 204.1903 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 134 | 17874192 | 5568 | 133.632 | 5.568 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50222506 | 1156 | 207.6149 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 164 | 17879848 | 5656 | 135.744 | 5.656 | 3.6 | 3.6 | 3B+1S | 1024 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50223668 | 1162 | 205.4455 | 100% | 0% | 100% | 100% | 100% | 0% | 11258376 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 128 | 117 | 17885394 | 5546 | 133.104 | 5.546 | 3.7 | 3.7 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 50224816 | 1148 | 206.996 | 0% | 0% | 100% | 100% | 100% | 30% | 11258700 | 324 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 120 | 17890242 | 4848 | 116.352 | 4.848 | 4.1 | 4.1 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 50225784 | 968 | 199.67 | 0% | 0% | 100% | 100% | 100% | 30% | 11259008 | 308 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133974 | 133.974 | 133.974 | [12 empty] | 27010 | 27010 | 201.6063 | [6 empty] | 3150 | 3150 | 1.1367 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:36 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27034 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 17890242 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50225784 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11259008 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 112 | 17895316 | 5074 | 121.776 | 5.074 | 4.8 | 4.8 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 50226832 | 1048 | 206.5432 | 0% | 0% | 100% | 100% | 100% | 60% | 11259618 | 610 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 122 | 110 | 17900186 | 4870 | 116.88 | 4.87 | 5.6 | 5.6 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50227865 | 1033 | 212.115 | 0% | 0% | 100% | 100% | 100% | 60% | 11260614 | 996 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 125 | 113 | 17905052 | 4866 | 116.784 | 4.866 | 7 | 7 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 50228910 | 1045 | 214.7554 | 0% | 0% | 100% | 100% | 100% | 60% | 11261543 | 929 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 116 | 17909282 | 4230 | 101.52 | 4.23 | 8 | 8 | 3B | 0 | 0 | 1117 | 1185 | 1116 | N/A | N/A | N/A | N/A | 50229852 | 942 | 222.695 | 0% | 0% | 100% | 100% | 100% | 60% | 11261743 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 127 | 17913522 | 4240 | 101.76 | 4.24 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1855 | 1117 | N/A | N/A | N/A | N/A | 50230800 | 948 | 223.5849 | 0% | 0% | 100% | 100% | 100% | 60% | 11261760 | 17 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 141 | 132 | 17919505 | 5983 | 143.592 | 5.983 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50231969 | 1169 | 195.3869 | 0% | 0% | 100% | 100% | 100% | 0% | 11261760 | 0 | 1.143 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 17925761 | 6256 | 150.144 | 6.256 | 9 | 9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50233175 | 1206 | 192.7749 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 140 | 17931863 | 6102 | 146.448 | 6.102 | 8.5 | 8.5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50234357 | 1182 | 193.707 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 17938023 | 6160 | 147.84 | 6.16 | 7.9 | 7.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50235552 | 1195 | 193.9935 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 142 | 17944309 | 6286 | 150.864 | 6.286 | 7.2 | 7.2 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50236773 | 1221 | 194.2412 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 | 1.08
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 140 | 17950575 | 6266 | 150.384 | 6.266 | 6.7 | 7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50237985 | 1212 | 193.4248 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 17956672 | 6097 | 146.328 | 6.097 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50239167 | 1182 | 193.8658 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 134 | 139 | 17962351 | 5679 | 136.296 | 5.679 | 5.6 | 5.6 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50240327 | 1160 | 204.2613 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 17967944 | 5593 | 134.232 | 5.593 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50241438 | 1111 | 198.6412 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 137 | 139 | 17973743 | 5799 | 139.176 | 5.799 | 5 | 5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50242606 | 1168 | 201.414 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 140 | 17979603 | 5860 | 140.64 | 5.86 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50243776 | 1170 | 199.6587 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 137 | 17985373 | 5770 | 138.48 | 5.77 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50244937 | 1161 | 201.2132 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 142 | 17991085 | 5712 | 137.088 | 5.712 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50246103 | 1166 | 204.1317 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 130 | 17996790 | 5705 | 136.92 | 5.705 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50247265 | 1162 | 203.681 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 133 | 18002498 | 5708 | 136.992 | 5.708 | 3.9 | 3.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50248434 | 1169 | 204.8003 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 132 | 18008184 | 5686 | 136.464 | 5.686 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50249606 | 1172 | 206.1203 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 136 | 18013484 | 5300 | 127.2 | 5.3 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50250665 | 1059 | 199.8113 | 0% | 100% | 100% | 100% | 100% | 0% | 11261760 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 125 | 18018711 | 5227 | 125.448 | 5.227 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50251748 | 1083 | 207.1934 | 0% | 0% | 100% | 100% | 100% | 23% | 11261851 | 91 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 126 | 18023815 | 5104 | 122.496 | 5.104 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50252818 | 1070 | 209.6395 | 0% | 0% | 100% | 100% | 100% | 23% | 11262077 | 226 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133573 | 133.573 | 133.573 | [12 empty] | 27034 | 27034 | 202.3912 | [6 empty] | 3069 | 3069 | 1.1405 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (23%)

## SEPT 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26896 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18023815 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50252818 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11262077 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 113 | 18028159 | 4344 | 104.256 | 4.344 | 4.7 | 4.7 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50253737 | 919 | 211.5562 | 0% | 0% | 100% | 100% | 100% | 75% | 11262658 | 581 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 110 | 18032470 | 4311 | 103.464 | 4.311 | 6.2 | 6.2 | 3B | 0 | 0 | 1118 | 1185 | 1105 | N/A | N/A | N/A | N/A | 50254681 | 944 | 218.9747 | 0% | 0% | 100% | 100% | 100% | 75% | 11263358 | 700 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 131 | 108 | 18036930 | 4460 | 107.04 | 4.46 | 7.4 | 7.4 | 3B | 0 | 0 | 1118 | 1185 | 1105 | N/A | N/A | N/A | N/A | 50255665 | 984 | 220.6278 | 0% | 0% | 100% | 100% | 100% | 75% | 11263998 | 640 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 118 | 18041490 | 4560 | 109.44 | 4.56 | 8.9 | 8.9 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50256641 | 976 | 214.0351 | 0% | 0% | 100% | 100% | 100% | 75% | 11264708 | 710 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 124 | 18046135 | 4645 | 111.48 | 4.645 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50257640 | 999 | 215.07 | 0% | 0% | 100% | 100% | 100% | 75% | 11265109 | 401 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 139 | 18052349 | 6214 | 149.136 | 6.214 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50258882 | 1242 | 199.8713 | 0% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 | 1.17 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 141 | 18058537 | 6188 | 148.512 | 6.188 | 9.2 | 9.2 | 3B+1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50260106 | 1224 | 197.8022 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 140 | 18064694 | 6157 | 147.768 | 6.157 | 8.6 | 8.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50261315 | 1209 | 196.3619 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 18070842 | 6148 | 147.552 | 6.148 | 8 | 8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50262465 | 1150 | 187.0527 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 18077047 | 6205 | 148.92 | 6.205 | 7.6 | 7.6 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50263660 | 1195 | 192.5866 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 | 1.07
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 141 | 18083211 | 6164 | 147.936 | 6.164 | 7.1 | 7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50264852 | 1192 | 193.3809 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 144 | 18089317 | 6106 | 146.544 | 6.106 | 6.6 | 6.6 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50266056 | 1204 | 197.1831 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 139 | 18095037 | 5720 | 137.28 | 5.72 | 6.3 | 6.3 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50267188 | 1132 | 197.9021 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 135 | 18100492 | 5455 | 130.92 | 5.455 | 6 | 6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50268274 | 1086 | 199.0834 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 18106013 | 5521 | 132.504 | 5.521 | 5.7 | 5.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50269433 | 1159 | 209.9257 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 18111784 | 5771 | 138.504 | 5.771 | 5.5 | 5.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50270594 | 1161 | 201.1783 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 129 | 18117579 | 5795 | 139.08 | 5.795 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50271765 | 1171 | 202.0708 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 134 | 18123262 | 5683 | 136.392 | 5.683 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50272924 | 1159 | 203.9416 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 134 | 18129157 | 5895 | 141.48 | 5.895 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50274103 | 1179 | 200 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 131 | 18135030 | 5873 | 140.952 | 5.873 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50275253 | 1150 | 195.8113 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 126 | 132 | 18140738 | 5708 | 136.992 | 5.708 | 4 | 4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50276418 | 1165 | 204.0995 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 126 | 18146606 | 5868 | 140.832 | 5.868 | 3.6 | 3.6 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50277596 | 1178 | 200.7498 | 100% | 0% | 100% | 100% | 100% | 0% | 11265109 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting |  | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 123 | 18151622 | 5016 | 120.384 | 5.016 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50278640 | 1044 | 208.134 | 0% | 0% | 100% | 100% | 100% | 30% | 11265266 | 157 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 115 | 18156884 | 5262 | 126.288 | 5.262 | 4.2 | 4.2 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50279714 | 1074 | 204.1049 | 0% | 0% | 100% | 100% | 100% | 30% | 11265604 | 338 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133069 | 133.069 | 133.069 | [12 empty] | 26896 | 26896 | 202.1207 | [6 empty] | 3527 | 3527 | 1.1317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
AS. PER ENGR ERNESTO PASCUA DRYRUN TEST FOR 15 MINUTES
BP2 - STOPPED @ 12:01 AM DUE TO DRYRUN FOR 15 MINUTES AS PER ENGR ERNESTO PASCUA
BP2 - STARTED @ 12:15 AM
BP1 - STOPPED @ 1:30 AM DUE TO DRYRUN FOR 15 MINUTES @ VILLAMOR P.S AS PER ENGR ERNESTO PASCUA
SP2 - STARTED @ 1:30 AM DUE TO DRYRUN FOR 15 MINUTES @ VILLAMOR P.S AS PER ENGR ERNESTO PASCUA
SP2 - STOPPED @ 1:45 AM
BP1 - STARTED @ 1: 45 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS♥
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27100 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18156884 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50279714 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11265604 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 134 | 117 | 18161822 | 4938 | 118.512 | 4.938 | 4.8 | 4.8 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 50280736 | 1022 | 206.9664 | 0% | 0% | 100% | 100% | 100% | 60% | 11266089 | 485 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 125 | 112 | 18166844 | 5022 | 120.528 | 5.022 | 5.5 | 5.5 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 50281782 | 1046 | 208.2836 | 0% | 0% | 100% | 100% | 100% | 60% | 11266798 | 709 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS♥
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 104 | 18171852 | 5008 | 120.192 | 5.008 | 6.4 | 6.4 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 50282808 | 1026 | 204.8722 | 0% | 0% | 100% | 100% | 100% | 60% | 11267576 | 778 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 114 | 18175752 | 3900 | 93.6 | 3.9 | 8.1 | 8.1 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 50283738 | 930 | 238.4615 | 0% | 0% | 100% | 100% | 100% | 60% | 11267680 | 104 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 117 | 18179336 | 3584 | 86.016 | 3.584 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50284656 | 918 | 256.1384 | 0% | 0% | 100% | 100% | 100% | 60% | 11267697 | 17 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 143 | 18185524 | 6188 | 148.512 | 6.188 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50285911 | 1255 | 202.8119 | 0% | 0% | 100% | 100% | 100% | 0% | 11267697 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 18191754 | 6230 | 149.52 | 6.23 | 9 | 9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50287120 | 1209 | 194.061 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 18197978 | 6224 | 149.376 | 6.224 | 8.5 | 8.5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50288302 | 1182 | 189.91 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 18204136 | 6158 | 147.792 | 6.158 | 7.9 | 7.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50289494 | 1192 | 193.5693 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 144 | 18210161 | 6025 | 144.6 | 6.025 | 7.2 | 7.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50290652 | 1158 | 192.1992 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 | 1.14
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 18216252 | 6091 | 146.184 | 6.091 | 6.6 | 6.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50291910 | 1258 | 206.5342 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 18222264 | 6012 | 144.288 | 6.012 | 6.1 | 6.1 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50293093 | 1183 | 196.7731 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 137 | 18228113 | 5849 | 140.376 | 5.849 | 5.4 | 5.4 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50294269 | 1176 | 201.06 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 18233745 | 5632 | 135.168 | 5.632 | 5.1 | 5.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50295410 | 1141 | 202.5923 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 18239358 | 5613 | 134.712 | 5.613 | 4.9 | 4.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50296547 | 1137 | 202.5655 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 136 | 18245155 | 5797 | 139.128 | 5.797 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50297715 | 1168 | 201.4835 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 18250973 | 5818 | 139.632 | 5.818 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50298884 | 1169 | 200.9282 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 137 | 18256716 | 5743 | 137.832 | 5.743 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50300054 | 1170 | 203.7263 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 18262507 | 5791 | 138.984 | 5.791 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50301221 | 1167 | 201.5196 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 138 | 18268411 | 5904 | 141.696 | 5.904 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50302389 | 1168 | 197.832 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 130 | 18274172 | 5761 | 138.264 | 5.761 | 3.1 | 3.1 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50303549 | 1160 | 201.3539 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 126 | 18279772 | 5600 | 134.4 | 5.6 | 3 | 3 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50304674 | 1125 | 200.8929 | 0% | 100% | 100% | 100% | 100% | 0% | 11267697 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 119 | 18285092 | 5320 | 127.68 | 5.32 | 3.1 | 3.1 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50305766 | 1092 | 205.2632 | 0% | 0% | 100% | 100% | 100% | 30% | 11267868 | 171 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 120 | 18290408 | 5316 | 127.584 | 5.316 | 3.5 | 3.5 | 3B | 0 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 50306814 | 1048 | 197.1407 | 0% | 0% | 100% | 100% | 100% | 30% | 11268254 | 386 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133524 | 133.524 | 133.524 | [12 empty] | 27100 | 27100 | 202.9598 | [6 empty] | 2650 | 2650 | 1.1133 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS♥
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27010 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18290408 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50306814 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11268254 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 114 | 18295256 | 4848 | 116.352 | 4.848 | 4.1 | 4.1 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 50307808 | 994 | 205.033 | 0% | 0% | 100% | 100% | 100% | 70% | 11268866 | 612 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 122 | 111 | 18299998 | 4742 | 113.808 | 4.742 | 4.9 | 4.9 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 50308788 | 980 | 206.6639 | 0% | 0% | 100% | 100% | 100% | 70% | 11269554 | 688 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS♥
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 125 | 106 | 18304868 | 4870 | 116.88 | 4.87 | 5.7 | 5.7 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50309786 | 998 | 204.9281 | 0% | 0% | 100% | 100% | 100% | 70% | 11270087 | 533 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 108 | 18308868 | 4000 | 96 | 4 | 7.5 | 7.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50310784 | 998 | 249.5 | 0% | 0% | 100% | 100% | 100% | 70% | 11270187 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 121 | 18312876 | 4008 | 96.192 | 4.008 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50311782 | 998 | 249.002 | 0% | 0% | 100% | 100% | 100% | 70% | 11270209 | 22 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 135 | 18318321 | 5445 | 130.68 | 5.445 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50312824 | 1042 | 191.3682 | 0% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 142 | 18324540 | 6219 | 149.256 | 6.219 | 9.1 | 9.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50314007 | 1183 | 190.2235 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 18330540 | 6000 | 144 | 6 | 8.7 | 8.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50315187 | 1180 | 196.6667 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 141 | 18336833 | 6293 | 151.032 | 6.293 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50316381 | 1194 | 189.7346 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 148 | 18343159 | 6326 | 151.824 | 6.326 | 7.7 | 7.7 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50317612 | 1231 | 194.5937 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 | 1.25
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 146 | 18349046 | 5887 | 141.288 | 5.887 | 7.2 | 7.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50318762 | 1150 | 195.3457 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 144 | 18355224 | 6178 | 148.272 | 6.178 | 6.6 | 6.6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50319972 | 1210 | 195.8563 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 149 | 18361197 | 5973 | 143.352 | 5.973 | 6.2 | 6.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50321145 | 1173 | 196.3837 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 134 | 18367359 | 6162 | 147.888 | 6.162 | 5.8 | 5.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50322403 | 1258 | 204.1545 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 18373327 | 5968 | 143.232 | 5.968 | 5.5 | 5.5 | 3B+1S | 1004 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50323599 | 1196 | 200.4021 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 130 | 18379141 | 5814 | 139.536 | 5.814 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50324772 | 1173 | 201.7544 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 18384987 | 5846 | 140.304 | 5.846 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 50325923 | 1151 | 196.8868 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 133 | 18390957 | 5970 | 143.28 | 5.97 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50327078 | 1155 | 193.4673 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 18396662 | 5705 | 136.92 | 5.705 | 4.6 | 4.6 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50328236 | 1158 | 202.9798 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 133 | 18402420 | 5758 | 138.192 | 5.758 | 4.3 | 4.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50329402 | 1166 | 202.5009 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 137 | 18408291 | 5871 | 140.904 | 5.871 | 3.8 | 3.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50330577 | 1175 | 200.1363 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 127 | 18413828 | 5537 | 132.888 | 5.537 | 3.5 | 3.5 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50331690 | 1113 | 201.0114 | 100% | 0% | 100% | 100% | 100% | 0% | 11270209 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 120 | 18419340 | 5512 | 132.288 | 5.512 | 3.6 | 3.6 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50332816 | 1126 | 204.2816 | 0% | 0% | 100% | 100% | 100% | 30% | 11270308 | 99 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 129 | 116 | 18424322 | 4982 | 119.568 | 4.982 | 3.9 | 3.9 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50333824 | 1008 | 202.3284 | 0% | 0% | 100% | 100% | 100% | 30% | 11270624 | 316 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133914 | 133.914 | 133.914 | [12 empty] | 27010 | 27010 | 201.6966 | [6 empty] | 2370 | 2370 | 1.1683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/ JEFFREY LAMAYO
[13 empty] | 10pm - 6am | FIDEL RAMOS♥
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26892 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18424322 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50333824 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11270624 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 107 | 18429402 | 5080 | 121.92 | 5.08 | 4.7 | 4.7 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50334874 | 1050 | 206.6929 | 0% | 0% | 100% | 100% | 100% | 60% | 11271342 | 718 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 104 | 18434176 | 4774 | 114.576 | 4.774 | 5.7 | 5.7 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50335858 | 984 | 206.1165 | 0% | 0% | 100% | 100% | 100% | 60% | 11272196 | 854 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS♥
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 127 | 105 | 18438762 | 4586 | 110.064 | 4.586 | 6.8 | 6.8 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50336788 | 930 | 202.7911 | 0% | 0% | 100% | 100% | 100% | 60% | 11273056 | 860 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 110 | 18442962 | 4200 | 100.8 | 4.2 | 8.8 | 8.8 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50337742 | 954 | 227.1429 | 0% | 0% | 100% | 100% | 100% | 60% | 11273386 | 330 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 116 | 18447202 | 4240 | 101.76 | 4.24 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50338696 | 954 | 225 | 0% | 0% | 100% | 100% | 100% | 60% | 11273409 | 23 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 144 | 136 | 18453254 | 6052 | 145.248 | 6.052 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50339869 | 1173 | 193.8202 | 0% | 0% | 100% | 100% | 100% | 0% | 11273409 | 0 | 1.08 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 145 | 18459376 | 6122 | 146.928 | 6.122 | 9.3 | 9.3 | 3B + 1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50341132 | 1263 | 206.3051 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 140 | 18465481 | 6105 | 146.52 | 6.105 | 8.7 | 8.7 | 3B + 1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50342271 | 1139 | 186.5684 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 145 | 18471640 | 6159 | 147.816 | 6.159 | 8.3 | 8.3 | 3B + 1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50343419 | 1148 | 186.3939 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 140 | 18477813 | 6173 | 148.152 | 6.173 | 7.9 | 7.9 | 3B + 1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50344622 | 1203 | 194.8809 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 | 1.18
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 137 | 18483829 | 6016 | 144.384 | 6.016 | 7.5 | 7.5 | 3B + 1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50345784 | 1162 | 193.1516 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 139 | 18490035 | 6206 | 148.944 | 6.206 | 6.9 | 6.9 | 3B + 1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50346977 | 1193 | 192.2333 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 137 | 18496070 | 6035 | 144.84 | 6.035 | 6.5 | 6.5 | 3B + 1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50348164 | 1187 | 196.686 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 136 | 18501757 | 5687 | 136.488 | 5.687 | 6.1 | 6.1 | 3B + 1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50349281 | 1117 | 196.4129 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 133 | 18507549 | 5792 | 139.008 | 5.792 | 5.7 | 5.7 | 3B + 1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50350448 | 1167 | 201.4848 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 18513447 | 5898 | 141.552 | 5.898 | 5.4 | 5.4 | 3B + 1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50351615 | 1167 | 197.8637 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 18519175 | 5728 | 137.472 | 5.728 | 5 | 5 | 3B + 1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50352788 | 1173 | 204.7835 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 18525137 | 5962 | 143.088 | 5.962 | 4.8 | 4.8 | 3B + 1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50353967 | 1179 | 197.7524 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 130 | 18530881 | 5744 | 137.856 | 5.744 | 4.6 | 4.6 | 3B + 1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50355124 | 1157 | 201.4276 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 127 | 18536395 | 5514 | 132.336 | 5.514 | 4.4 | 4.4 | 3B + 1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50356266 | 1142 | 207.1092 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 132 | 18542106 | 5711 | 137.064 | 5.711 | 4.2 | 4.2 | 3B + 1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50357442 | 1176 | 205.9184 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 124 | 18547706 | 5600 | 134.4 | 5.6 | 3.9 | 3.9 | 3B + 1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50358608 | 1166 | 208.2143 | 0% | 100% | 100% | 100% | 100% | 0% | 11273409 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 122 | 18552922 | 5216 | 125.184 | 5.216 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1166 | N/A | N/A | N/A | N/A | 50359674 | 1066 | 204.3712 | 0% | 0% | 100% | 100% | 100% | 30% | 11273498 | 89 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 115 | 18558058 | 5136 | 123.264 | 5.136 | 4.4 | 4.4 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50360716 | 1042 | 202.8816 | 0% | 0% | 100% | 100% | 100% | 30% | 11273846 | 348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133736 | 133.736 | 133.736 | [12 empty] | 26892 | 26892 | 201.0827 | [6 empty] | 3222 | 3222 | 1.1617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS♥
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26950 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18558058 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50360716 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11273846 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 125 | 118 | 18562816 | 4758 | 114.192 | 4.758 | 4.8 | 4.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50361704 | 988 | 207.6503 | 0% | 0% | 100% | 100% | 100% | 60% | 11274194 | 348 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 116 | 110 | 18567486 | 4670 | 112.08 | 4.67 | 5.6 | 5.6 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50362698 | 994 | 212.848 | 0% | 0% | 100% | 100% | 100% | 60% | 11274772 | 578 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS♥
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 120 | 106 | 18572038 | 4552 | 109.248 | 4.552 | 6.4 | 6.4 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50363656 | 958 | 210.4569 | 0% | 0% | 100% | 100% | 100% | 60% | 11275346 | 574 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 118 | 112 | 18576036 | 3998 | 95.952 | 3.998 | 8.3 | 8.3 | 3B | 0 | 0 | 1127 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50364654 | 998 | 249.6248 | 0% | 0% | 100% | 100% | 100% | 60% | 11275686 | 340 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 116 | 18580018 | 3982 | 95.568 | 3.982 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 50365654 | 1000 | 251.1301 | 0% | 0% | 100% | 100% | 100% | 60% | 11275781 | 95 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 132 | 18586002 | 5984 | 143.616 | 5.984 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50366820 | 1166 | 194.8529 | 0% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 142 | 18592027 | 6025 | 144.6 | 6.025 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50367931 | 1111 | 184.3983 | 0% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 145 | 18597945 | 5918 | 142.032 | 5.918 | 9.3 | 9.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50369083 | 1152 | 194.6604 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 143 | 18603831 | 5886 | 141.264 | 5.886 | 8.9 | 8.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50370119 | 1036 | 176.0109 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 144 | 18610057 | 6226 | 149.424 | 6.226 | 8.2 | 8.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50371320 | 1201 | 192.9007 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 | 1.15
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 133 | 18616259 | 6202 | 148.848 | 6.202 | 7.6 | 7.5 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50372539 | 1219 | 196.5495 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 274 | 18622497 | 6238 | 149.712 | 6.238 | 6.9 | 6.9 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50373746 | 1207 | 193.4915 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 18628759 | 6262 | 150.288 | 6.262 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50374953 | 1207 | 192.7499 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 145 | 18634685 | 5926 | 142.224 | 5.926 | 5.7 | 5.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50376128 | 1175 | 198.2788 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 141 | 18640360 | 5675 | 136.2 | 5.675 | 5.3 | 5.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50377283 | 1155 | 203.5242 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 18646030 | 5670 | 136.08 | 5.67 | 5 | 5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50378431 | 1148 | 202.4691 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 18651729 | 5699 | 136.776 | 5.699 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50379571 | 1140 | 200.0351 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 18657248 | 5519 | 132.456 | 5.519 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50380689 | 1118 | 202.5729 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 18662885 | 5637 | 135.288 | 5.637 | 4 | 4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50381846 | 1157 | 205.251 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 135 | 18668543 | 5658 | 135.792 | 5.658 | 3.7 | 3.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50383017 | 1171 | 206.9636 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 135 | 18674448 | 5905 | 141.72 | 5.905 | 3.3 | 3.3 | 3B+1S | 1044 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50384235 | 1218 | 206.2659 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 128 | 18680242 | 5794 | 139.056 | 5.794 | 3 | 3 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50385442 | 1207 | 208.319 | 100% | 0% | 100% | 100% | 100% | 0% | 11275781 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 128 | 126 | 18685656 | 5414 | 129.936 | 5.414 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 50386546 | 1104 | 203.9158 | 0% | 0% | 100% | 100% | 100% | 30% | 11275981 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 121 | 18691066 | 5410 | 129.84 | 5.41 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50387666 | 1120 | 207.024 | 0% | 0% | 100% | 100% | 100% | 30% | 11276117 | 136 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133008 | 133.008 | 133.008 | [12 empty] | 26950 | 26950 | 202.6194 | [6 empty] | 2271 | 2271 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:24 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS♥
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS♥
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26758 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18691066 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50387666 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11276117 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 126 | 116 | 18695892 | 4826 | 115.824 | 4.826 | 3.9 | 3.9 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50388644 | 978 | 202.6523 | 0% | 0% | 100% | 100% | 100% | 60% | 11276676 | 559 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 110 | 18700766 | 4874 | 116.976 | 4.874 | 5 | 5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50389626 | 982 | 201.4772 | 0% | 0% | 100% | 100% | 100% | 60% | 11277317 | 641 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS♥
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 127 | 106 | 18705678 | 4912 | 117.888 | 4.912 | 5.8 | 5.8 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50390624 | 998 | 203.1759 | 0% | 0% | 100% | 100% | 100% | 60% | 11278003 | 686 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 104 | 18709608 | 3930 | 94.32 | 3.93 | 8.6 | 8.6 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50391619 | 995 | 253.1807 | 0% | 0% | 100% | 100% | 100% | 60% | 11278522 | 519 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 117 | 18713552 | 3944 | 94.656 | 3.944 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50392616 | 997 | 252.789 | 0% | 0% | 100% | 100% | 100% | 60% | 11278553 | 31 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 128 | 18718764 | 5212 | 125.088 | 5.212 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50393578 | 962 | 184.5741 | 0% | 0% | 100% | 100% | 100% | 0% | 11278553 | 0 | 1.08 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 136 | 18724640 | 5876 | 141.024 | 5.876 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50394656 | 1078 | 183.4581 | 0% | 0% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 140 | 18730596 | 5956 | 142.944 | 5.956 | 9.4 | 9.4 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50395816 | 1160 | 194.7616 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 147 | 18736588 | 5992 | 143.808 | 5.992 | 8.9 | 8.9 | 3B+1S | 0 | 1057 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50396992 | 1176 | 196.2617 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 18742892 | 6304 | 151.296 | 6.304 | 8.2 | 8.2 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50398208 | 1216 | 192.8934 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 | 1.16
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 143 | 18749434 | 6542 | 157.008 | 6.542 | 7.6 | 7.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50399478 | 1270 | 194.1302 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 18755526 | 6092 | 146.208 | 6.092 | 7 | 7 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50400686 | 1208 | 198.2928 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 136 | 18761322 | 5796 | 139.104 | 5.796 | 6.4 | 6.4 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50401858 | 1172 | 202.2084 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 134 | 18766933 | 5611 | 134.664 | 5.611 | 5.9 | 5.9 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50403039 | 1181 | 210.4794 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 135 | 18772590 | 5657 | 135.768 | 5.657 | 5.5 | 5.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50404205 | 1166 | 206.1163 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 18778410 | 5820 | 139.68 | 5.82 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50405377 | 1172 | 201.3746 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 18784134 | 5724 | 137.376 | 5.724 | 4.9 | 4.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50406542 | 1165 | 203.529 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 18790013 | 5879 | 141.096 | 5.879 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50407712 | 1170 | 199.0134 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 133 | 18795795 | 5782 | 138.768 | 5.782 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50408885 | 1173 | 202.871 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 131 | 18801425 | 5630 | 135.12 | 5.63 | 4.1 | 4.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50410044 | 1159 | 205.8615 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 132 | 18807058 | 5633 | 135.192 | 5.633 | 3.8 | 3.8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50411206 | 1162 | 206.2844 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 129 | 18812512 | 5454 | 130.896 | 5.454 | 3.7 | 3.7 | 3B+1S | 0 | 950 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50412340 | 1134 | 207.9208 | 0% | 100% | 100% | 100% | 100% | 0% | 11278553 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 128 | 119 | 18817612 | 5100 | 122.4 | 5.1 | 3.9 | 3.9 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50413376 | 1036 | 203.1373 | 0% | 0% | 100% | 100% | 100% | 30% | 11278753 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 116 | 18822742 | 5130 | 123.12 | 5.13 | 4.4 | 4.4 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 50414424 | 1048 | 204.2885 | 0% | 0% | 100% | 100% | 100% | 30% | 11279119 | 366 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131676 | 131.676 | 131.676 | [12 empty] | 26758 | 26758 | 203.2109 | [6 empty] | 3002 | 3002 | 1.155 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 25, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/ JEFFREY LAMAYO
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26877 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18822742 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50414424 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11279119 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 128 | 110 | 18827554 | 4812 | 115.488 | 4.812 | 4.9 | 4.9 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50415414 | 990 | 205.7357 | 0% | 0% | 100% | 100% | 100% | 60% | 11279593 | 474 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 108 | 18832216 | 4662 | 111.888 | 4.662 | 5.6 | 5.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50416402 | 988 | 211.9262 | 0% | 0% | 100% | 100% | 100% | 60% | 11280126 | 533 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 120 | 106 | 18836882 | 4666 | 111.984 | 4.666 | 6.2 | 6.2 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50417368 | 966 | 207.0296 | 0% | 0% | 100% | 100% | 100% | 60% | 11280719 | 593 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 104 | 18840986 | 4104 | 98.496 | 4.104 | 8.2 | 8.2 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 50418376 | 1008 | 245.614 | 0% | 0% | 100% | 100% | 100% | 60% | 11280919 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 123 | 18845022 | 4036 | 96.864 | 4.036 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 50419380 | 1004 | 248.7611 | 0% | 0% | 100% | 100% | 100% | 60% | 11280934 | 15 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 | 140 | 18850927 | 5905 | 141.72 | 5.905 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50420547 | 1167 | 197.6291 | 0% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 144 | 18857108 | 6181 | 148.344 | 6.181 | 9.3 | 9.3 | 3B+1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50421756 | 1209 | 195.5994 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 145 | 18863240 | 6132 | 147.168 | 6.132 | 8.8 | 8.8 | 3B+1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50422936 | 1180 | 192.4331 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 139 | 142 | 18869414 | 6174 | 148.176 | 6.174 | 8.5 | 8.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50424141 | 1205 | 195.1733 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 141 | 18875699 | 6285 | 150.84 | 6.285 | 8 | 8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50425340 | 1199 | 190.7717 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 | 1.14
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 18881921 | 6222 | 149.328 | 6.222 | 7.6 | 7.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50426522 | 1182 | 189.9711 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 18888016 | 6095 | 146.28 | 6.095 | 7 | 7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50427644 | 1122 | 184.0853 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 18893775 | 5759 | 138.216 | 5.759 | 6.6 | 6.6 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50428837 | 1193 | 207.154 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 131 | 18899194 | 5419 | 130.056 | 5.419 | 6.3 | 6.3 | 3B+1S | 1019 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50429986 | 1149 | 212.0317 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 133 | 18904710 | 5516 | 132.384 | 5.516 | 6 | 6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50431134 | 1148 | 208.1218 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 136 | 18910229 | 5519 | 132.456 | 5.519 | 5.7 | 5.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50432250 | 1116 | 202.2105 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 18915950 | 5721 | 137.304 | 5.721 | 5.4 | 5.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50433421 | 1171 | 204.6845 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 18921868 | 5918 | 142.032 | 5.918 | 5.1 | 5.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50434634 | 1213 | 204.9679 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 139 | 18927470 | 5602 | 134.448 | 5.602 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50435770 | 1136 | 202.7847 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 134 | 18933115 | 5645 | 135.48 | 5.645 | 4.3 | 4.3 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50436928 | 1158 | 205.1373 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 131 | 18938781 | 5666 | 135.984 | 5.666 | 3.9 | 3.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50438107 | 1179 | 208.0833 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 132 | 18944021 | 5240 | 125.76 | 5.24 | 3.5 | 3.5 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50439190 | 1083 | 206.6794 | 100% | 0% | 100% | 100% | 100% | 0% | 11280934 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 128 | 18949337 | 5316 | 127.584 | 5.316 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50440260 | 1070 | 201.2792 | 0% | 0% | 100% | 100% | 100% | 20% | 11280983 | 49 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 116 | 18954280 | 4943 | 118.632 | 4.943 | 4.1 | 4.1 | 3B | 0 | 0 | 1095 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50441301 | 1041 | 210.6008 | 0% | 0% | 100% | 100% | 100% | 20% | 11281503 | 520 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131538 | 131.538 | 131.538 | [12 empty] | 26877 | 26877 | 204.3288 | [6 empty] | 2384 | 2384 | 1.1617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26313 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 18954280 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50441301 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11281503 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 82 | 57.7465 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 11.4 | 127 | 92 | 18958172 | 3892 | 93.408 | 3.892 | 5.5 | 5.5 | 2B | 0 | 0 | 0 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50442059 | 758 | 194.7585 | 0% | 0% | 0% | 100% | 100% | 75% | 11282838 | 1335 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 75 | 52.8169 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 128 | 104 | 18962194 | 4022 | 96.528 | 4.022 | 6.8 | 6.8 | 2B | 0 | 0 | 1187 | 1185 | 0 | N/A | N/A | N/A | N/A | 50442803 | 744 | 184.9826 | 0% | 0% | 100% | 100% | 0% | 75% | 11283993 | 1155 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 115 | 108 | 18966798 | 4604 | 110.496 | 4.604 | 7.7 | 7.7 | 2B+1S | 1076 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 50443676 | 873 | 189.6177 | 100% | 0% | 100% | 0% | 100% | 75% | 11284801 | 808 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 113 | 111 | 18971228 | 4430 | 106.32 | 4.43 | 8.4 | 8.4 | 2B+1S | 1076 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 50444537 | 861 | 194.3567 | 100% | 0% | 100% | 0% | 100% | 75% | 11285190 | 389 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 | 117 | 18975342 | 4114 | 98.736 | 4.114 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50445656 | 1119 | 271.9981 | 0% | 0% | 100% | 100% | 100% | 75% | 11285530 | 340 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 140 | 18981447 | 6105 | 146.52 | 6.105 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50446801 | 1145 | 187.5512 | 0% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 142 | 18987588 | 6141 | 147.384 | 6.141 | 9.1 | 9.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50447976 | 1175 | 191.3369 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 144 | 18993651 | 6063 | 145.512 | 6.063 | 8.5 | 8.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50449253 | 1277 | 210.6218 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 141 | 18999654 | 6003 | 144.072 | 6.003 | 8.1 | 8.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50450475 | 1222 | 203.5649 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 142 | 19005741 | 6087 | 146.088 | 6.087 | 7.6 | 7.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50451754 | 1279 | 210.1199 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 | 1.12
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 142 | 19011645 | 5904 | 141.696 | 5.904 | 7.2 | 7.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50452896 | 1142 | 193.4282 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 19017569 | 5924 | 142.176 | 5.924 | 6.8 | 6.8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50454012 | 1116 | 188.3862 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 139 | 19023425 | 5856 | 140.544 | 5.856 | 6.3 | 6.3 | 3B+1S | 1018 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50455204 | 1192 | 203.5519 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 132 | 19028837 | 5412 | 129.888 | 5.412 | 6.1 | 6.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50456318 | 1114 | 205.8389 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 133 | 19034306 | 5469 | 131.256 | 5.469 | 5.8 | 5.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50457437 | 1119 | 204.6078 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 19039885 | 5579 | 133.896 | 5.579 | 5.6 | 5.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50458578 | 1141 | 204.5169 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 19045699 | 5814 | 139.536 | 5.814 | 5.3 | 5.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50459746 | 1168 | 200.8944 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 136 | 19051400 | 5701 | 136.824 | 5.701 | 5 | 5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50460916 | 1170 | 205.2272 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 132 | 19057080 | 5680 | 136.32 | 5.68 | 4.8 | 4.8 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50462078 | 1162 | 204.5775 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 130 | 19062623 | 5543 | 133.032 | 5.543 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50463241 | 1163 | 209.8142 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 128 | 19068183 | 5560 | 133.44 | 5.56 | 4.3 | 4.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50464398 | 1157 | 208.0935 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 126 | 19073692 | 5509 | 132.216 | 5.509 | 4.1 | 4.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50465538 | 1140 | 206.9341 | 100% | 0% | 100% | 100% | 100% | 0% | 11285530 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 121 | 19078912 | 5220 | 125.28 | 5.22 | 4.5 | 4.5 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 50466606 | 1068 | 204.5977 | 0% | 0% | 100% | 100% | 100% | 30% | 11285886 | 356 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 125 | 110 | 19083859 | 4947 | 118.728 | 4.947 | 5 | 5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50467614 | 1008 | 203.7599 | 0% | 0% | 100% | 100% | 100% | 30% | 11286348 | 462 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129579 | 129.579 | 129.579 | [12 empty] | 26313 | 26313 | 203.0653 | [6 empty] | 4845 | 4845 | 1.125 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:00 AM (75%)
BP1 - STOPPED @ 12:01AM DUE TO ELECTRICAL INSTRUMENTAL TEST AND PREVENTIVE MAINTENANCE
BP1 - STARTED @ 1:30 AM
BP3 - STOPPED @ 1:31AM DUE TO ELECTRICAL INSTRUMENTAL TEST AND PREVENTIVE MAINTENANCE
SP1 - STARTED @ 2:15AM TO MEET THE 83PSI TARGET DISCHARGE PRESSURE
BP3 - STARTED @ 2:49 AM
BP2 - STOPPED @ 2:50AM DUE TO ELECTRICAL INSTRUMENTAL TEST AND PREVENTIVE MAINTENANCE
SP1 - STOPPED @ 4:00 AM
BP2 - STARTED @ 4:01 AM
XCV2- CLOSED @ 4:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
UNABLE TO START SP2 DUE TO ERROR IN COMMUNICATION BETWEEN PLC AND MOTOR
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
ENGR. A. TRINIDAD ARRIVED @ 8:30AM AND CHECK UP THE STORAGE PUMP 2. RESET THE VFD OF SP2. NOW OPERABLE BUT NOT IN OPERATION.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26336 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19083859 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50467614 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11286348 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 122 | 116 | 19088416 | 4557 | 109.368 | 4.557 | 5.8 | 5.8 | 3B | 0 | 0 | 1096 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50468546 | 932 | 204.5205 | 0% | 0% | 100% | 100% | 100% | 60% | 11286842 | 494 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 119 | 110 | 19092948 | 4532 | 108.768 | 4.532 | 6.8 | 6.8 | 3B | 0 | 0 | 1095 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50469474 | 928 | 204.7661 | 0% | 0% | 100% | 100% | 100% | 60% | 11287564 | 722 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 115 | 106 | 19097472 | 4524 | 108.576 | 4.524 | 7.5 | 7.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50470400 | 926 | 204.6861 | 0% | 0% | 100% | 100% | 100% | 60% | 11288458 | 894 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 115 | 107 | 19101512 | 4040 | 96.96 | 4.04 | 7.9 | 7.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50471226 | 826 | 204.4554 | 0% | 0% | 100% | 100% | 100% | 60% | 11289018 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 125 | 19105888 | 4376 | 105.024 | 4.376 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50472214 | 988 | 225.777 | 0% | 0% | 100% | 100% | 100% | 60% | 11289118 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 141 | 19111587 | 5699 | 136.776 | 5.699 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50473266 | 1052 | 184.5938 | 0% | 0% | 100% | 100% | 100% | 0% | 11289118 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 143 | 19117323 | 5736 | 137.664 | 5.736 | 9.4 | 9.4 | 3B+1S | 0 | 976 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50474292 | 1026 | 178.8703 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 19123067 | 5744 | 137.856 | 5.744 | 8.9 | 8.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50475531 | 1239 | 215.7033 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 144 | 19128924 | 5857 | 140.568 | 5.857 | 8.4 | 8.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50476786 | 1255 | 214.2735 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 141 | 19135001 | 6077 | 145.848 | 6.077 | 8 | 8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50477995 | 1209 | 198.9468 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 | 1.09
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 140 | 19141047 | 6046 | 145.104 | 6.046 | 7.6 | 7.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50479185 | 1190 | 196.8243 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 19147104 | 6057 | 145.368 | 6.057 | 7.2 | 7.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50480369 | 1184 | 195.4763 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 19152893 | 5789 | 138.936 | 5.789 | 6.8 | 6.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50481545 | 1176 | 203.1439 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 131 | 19158454 | 5561 | 133.464 | 5.561 | 6.5 | 6.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50482648 | 1103 | 198.3456 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 134 | 19164088 | 5634 | 135.216 | 5.634 | 6.2 | 6.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50483798 | 1150 | 204.1179 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 19169765 | 5677 | 136.248 | 5.677 | 6 | 6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50484968 | 1170 | 206.0948 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 131 | 19175580 | 5815 | 139.56 | 5.815 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50486130 | 1162 | 199.828 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 132 | 19181252 | 5672 | 136.128 | 5.672 | 5.4 | 5.4 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50487291 | 1161 | 204.6897 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 133 | 19186887 | 5635 | 135.24 | 5.635 | 5.1 | 5.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50488452 | 1161 | 206.0337 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 128 | 19192659 | 5772 | 138.528 | 5.772 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50489612 | 1160 | 200.9702 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 132 | 19198397 | 5738 | 137.712 | 5.738 | 4.6 | 4.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50490762 | 1150 | 200.4183 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 122 | 19204172 | 5775 | 138.6 | 5.775 | 4.5 | 4.5 | 3B+1S | 0 | 994 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50491928 | 1166 | 201.9048 | 0% | 100% | 100% | 100% | 100% | 0% | 11289118 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 126 | 121 | 19209476 | 5304 | 127.296 | 5.304 | 4.7 | 4.7 | 3B | 0 | 0 | 1157 | 1185 | 1156 | N/A | N/A | N/A | N/A | 50492996 | 1068 | 201.3575 | 0% | 0% | 100% | 100% | 100% | 30% | 11289326 | 208 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 154 | 108 | 19214186 | 4710 | 113.04 | 4.71 | 5.5 | 5.5 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 50493950 | 954 | 202.5478 | 0% | 0% | 100% | 100% | 100% | 30% | 11290202 | 876 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130327 | 130.327 | 130.327 | [12 empty] | 26336 | 26336 | 202.0763 | [6 empty] | 3854 | 3854 | 1.1283 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 5:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26428 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19214186 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50493950 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11290202 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 130 | 104 | 19218786 | 4600 | 110.4 | 4.6 | 6.4 | 6.4 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50494888 | 938 | 203.913 | 0% | 0% | 100% | 100% | 100% | 60% | 11291046 | 844 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 102 | 19223388 | 4602 | 110.448 | 4.602 | 7.4 | 7.4 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50495822 | 934 | 202.9552 | 0% | 0% | 100% | 100% | 100% | 60% | 11292046 | 1000 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 127 | 106 | 19227962 | 4574 | 109.776 | 4.574 | 8.5 | 8.5 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 50496736 | 914 | 199.8251 | 0% | 0% | 100% | 100% | 100% | 60% | 11293048 | 1002 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 109 | 19232422 | 4460 | 107.04 | 4.46 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50497646 | 910 | 204.0359 | 0% | 0% | 100% | 100% | 100% | 60% | 11293086 | 38 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 | 122 | 19236746 | 4324 | 103.776 | 4.324 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50498556 | 910 | 210.4533 | 0% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 137 | 19241828 | 5082 | 121.968 | 5.082 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50499536 | 980 | 192.8375 | 0% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 144 | 19247667 | 5839 | 140.136 | 5.839 | 9.2 | 9.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50500723 | 1187 | 203.2882 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 19253583 | 5916 | 141.984 | 5.916 | 8.8 | 8.8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50501899 | 1176 | 198.783 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 139 | 19259531 | 5948 | 142.752 | 5.948 | 8.4 | 8.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50503069 | 1170 | 196.7048 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 141 | 19265480 | 5949 | 142.776 | 5.949 | 8 | 8 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50504248 | 1179 | 198.1846 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 | 1.07
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 139 | 19271544 | 6064 | 145.536 | 6.064 | 7.7 | 7.7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50505430 | 1182 | 194.9208 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 137 | 19277505 | 5961 | 143.064 | 5.961 | 7.4 | 7.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50506600 | 1170 | 196.2758 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 135 | 19283373 | 5868 | 140.832 | 5.868 | 7 | 7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50507771 | 1171 | 199.5569 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 134 | 19289265 | 5892 | 141.408 | 5.892 | 6.7 | 6.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50508968 | 1197 | 203.1568 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 132 | 19295435 | 6170 | 148.08 | 6.17 | 6.4 | 6.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50510181 | 1213 | 196.5964 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 19301403 | 5968 | 143.232 | 5.968 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50511363 | 1182 | 198.0563 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 19307297 | 5894 | 141.456 | 5.894 | 5.9 | 5.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50512523 | 1160 | 196.8103 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 136 | 19313231 | 5934 | 142.416 | 5.934 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50513709 | 1186 | 199.8652 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 129 | 19319080 | 5849 | 140.376 | 5.849 | 5.4 | 5.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50514851 | 1142 | 195.2471 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 135 | 19324638 | 5558 | 133.392 | 5.558 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50516012 | 1161 | 208.8881 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 131 | 19330290 | 5652 | 135.648 | 5.652 | 4.9 | 4.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50517167 | 1155 | 204.3524 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 123 | 127 | 19336002 | 5712 | 137.088 | 5.712 | 4.6 | 4.6 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50518352 | 1185 | 207.458 | 100% | 0% | 100% | 100% | 100% | 0% | 11293086 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 119 | 19340836 | 4834 | 116.016 | 4.834 | 4.6 | 4.6 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 50519338 | 986 | 203.9719 | 0% | 0% | 100% | 100% | 100% | 30% | 11293161 | 75 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 108 | 19345856 | 5020 | 120.48 | 5.02 | 5.4 | 5.4 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 50520378 | 1040 | 207.1713 | 0% | 0% | 100% | 100% | 100% | 30% | 11293988 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131670 | 131.67 | 131.67 | [12 empty] | 26428 | 26428 | 200.7139 | [6 empty] | 3786 | 3786 | 1.1233 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## SEPT 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-09-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26700 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19345856 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50520378 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11293988 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 106 | 19350556 | 4700 | 112.8 | 4.7 | 6.4 | 6.4 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 50521366 | 988 | 210.2128 | 0% | 0% | 100% | 100% | 100% | 60% | 11294298 | 310 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 118 | 105 | 19354992 | 4436 | 106.464 | 4.436 | 7.4 | 7.4 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50522284 | 918 | 206.9432 | 0% | 0% | 100% | 100% | 100% | 60% | 11295398 | 1100 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 122 | 103 | 19359436 | 4444 | 106.656 | 4.444 | 8.2 | 8.2 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50523198 | 914 | 205.6706 | 0% | 0% | 100% | 100% | 100% | 60% | 11296450 | 1052 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 106 | 19363726 | 4290 | 102.96 | 4.29 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50524114 | 916 | 213.5198 | 0% | 0% | 100% | 100% | 100% | 60% | 11296670 | 220 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN/ JEFFREY LAMAYO
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 119 | 117 | 19368016 | 4290 | 102.96 | 4.29 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50525032 | 918 | 213.986 | 0% | 0% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | RANDY REGENCIA
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 132 | 19373636 | 5620 | 134.88 | 5.62 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50526088 | 1056 | 187.9004 | 0% | 0% | 100% | 100% | 100% | 0% | 11296670 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 142 | 19379608 | 5972 | 143.328 | 5.972 | 9.4 | 9.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50527270 | 1182 | 197.9236 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 137 | 19385724 | 6116 | 146.784 | 6.116 | 8.8 | 8.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50528482 | 1212 | 198.1687 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 143 | 19391706 | 5982 | 143.568 | 5.982 | 8.2 | 8.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 50529672 | 1190 | 198.9301 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 19398092 | 6386 | 153.264 | 6.386 | 7.7 | 7.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50530928 | 1256 | 196.6802 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 | 1.2
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 136 | 19404066 | 5974 | 143.376 | 5.974 | 7.2 | 7.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50532050 | 1122 | 187.8139 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 138 | 19410428 | 6362 | 152.688 | 6.362 | 6.7 | 6.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50533274 | 1224 | 192.3923 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 134 | 19416346 | 5918 | 142.032 | 5.918 | 6.3 | 6.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50534462 | 1188 | 200.7435 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 132 | 19422077 | 5731 | 137.544 | 5.731 | 5.9 | 5.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50535625 | 1163 | 202.9314 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 142 | 19427848 | 5771 | 138.504 | 5.771 | 5.6 | 5.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50536797 | 1172 | 203.0844 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 138 | 19433646 | 5798 | 139.152 | 5.798 | 5.3 | 5.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50537973 | 1176 | 202.8286 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 19439409 | 5763 | 138.312 | 5.763 | 5.1 | 5.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50539143 | 1170 | 203.0193 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 139 | 19445207 | 5798 | 139.152 | 5.798 | 4.7 | 4.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50540316 | 1173 | 202.3111 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 130 | 19450855 | 5648 | 135.552 | 5.648 | 4.4 | 4.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50541481 | 1165 | 206.2677 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 140 | 19456491 | 5636 | 135.264 | 5.636 | 4.1 | 4.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50542640 | 1159 | 205.6423 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 125 | 19462008 | 5517 | 132.408 | 5.517 | 3.9 | 3.9 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50543796 | 1156 | 209.5342 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 130 | 19467592 | 5584 | 134.016 | 5.584 | 3.7 | 3.7 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50544958 | 1162 | 208.0946 | 0% | 100% | 100% | 100% | 100% | 0% | 11296670 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 134 | 125 | 19472622 | 5030 | 120.72 | 5.03 | 3.9 | 3.9 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50546004 | 1046 | 207.9523 | 0% | 0% | 100% | 100% | 100% | 30% | 11296868 | 198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 110 | 19477894 | 5272 | 126.528 | 5.272 | 4.8 | 4.8 | 3B | 0 | 0 | 1137 | 1185 | 1137 | N/A | N/A | N/A | N/A | 50547078 | 1074 | 203.7178 | 0% | 0% | 100% | 100% | 100% | 30% | 11297673 | 805 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132038 | 132.038 | 132.038 | [12 empty] | 26700 | 26700 | 202.2145 | [6 empty] | 3685 | 3685 | 1.18 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (SEPT 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PLANT OPERATION SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)