## OCT 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26538 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19477894 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 50547078 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11297673 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 129 | 105 | 19482478 | 4584 | 110.016 | 4.584 | 5.7 | 5.7 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 50548086 | 1008 | 219.8953 | 0% | 0% | 100% | 100% | 100% | 60% | 11298528 | 855 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 116 | 102 | 19486832 | 4354 | 104.496 | 4.354 | 6.7 | 6.7 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 50548986 | 900 | 206.7065 | 0% | 0% | 100% | 100% | 100% | 60% | 11299388 | 860 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 113 | 101 | 19491172 | 4340 | 104.16 | 4.34 | 7.5 | 7.5 | 3B | 0 | 0 | 1107 | 1185 | 1106 | N/A | N/A | N/A | N/A | 50549888 | 902 | 207.8341 | 0% | 0% | 100% | 100% | 100% | 60% | 11300150 | 762 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 112 | 104 | 19495244 | 4072 | 97.728 | 4.072 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 50550822 | 934 | 229.3713 | 0% | 0% | 100% | 100% | 100% | 60% | 11300363 | 213 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 116 | 114 | 19499326 | 4082 | 97.968 | 4.082 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 50551746 | 924 | 226.3596 | 0% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 132 | 19504941 | 5615 | 134.76 | 5.615 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 50552814 | 1068 | 190.2048 | 0% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 | 1.09 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 137 | 19510752 | 5811 | 139.464 | 5.811 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50553906 | 1092 | 187.9195 | 0% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 136 | 19516676 | 5924 | 142.176 | 5.924 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50555028 | 1122 | 189.3991 | 0% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 142 | 19522717 | 6041 | 144.984 | 6.041 | 9.2 | 9.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50556187 | 1159 | 191.8557 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 140 | 19528967 | 6250 | 150 | 6.25 | 8.4 | 8.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50557384 | 1197 | 191.52 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 | 1.1
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 142 | 19535213 | 6246 | 149.904 | 6.246 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50558565 | 1181 | 189.081 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 143 | 19541476 | 6263 | 150.312 | 6.263 | 7.1 | 7.1 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50559862 | 1297 | 207.0893 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 144 | 19547610 | 6134 | 147.216 | 6.134 | 6.4 | 6.4 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50561006 | 1144 | 186.5015 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 137 | 19553337 | 5727 | 137.448 | 5.727 | 5.6 | 5.6 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50562108 | 1102 | 192.4219 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 137 | 19559320 | 5983 | 143.592 | 5.983 | 5.2 | 5.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50563300 | 1192 | 199.2312 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 19565149 | 5829 | 139.896 | 5.829 | 4.7 | 4.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50564476 | 1176 | 201.7499 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 19571296 | 6147 | 147.528 | 6.147 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50565651 | 1175 | 191.1502 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 132 | 19577156 | 5860 | 140.64 | 5.86 | 4 | 4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50566828 | 1177 | 200.8532 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 134 | 133 | 19582881 | 5725 | 137.4 | 5.725 | 3.6 | 3.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50567977 | 1149 | 200.6987 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 141 | 19588715 | 5834 | 140.016 | 5.834 | 3.4 | 3.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50569141 | 1164 | 199.5201 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 134 | 134 | 19594474 | 5759 | 138.216 | 5.759 | 3.1 | 3.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50570321 | 1180 | 204.8967 | 100% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 134 | 121 | 19599959 | 5485 | 131.64 | 5.485 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50571474 | 1153 | 210.2097 | 0% | 0% | 100% | 100% | 100% | 0% | 11300363 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 120 | 19605644 | 5685 | 136.44 | 5.685 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50572569 | 1095 | 192.6121 | 0% | 0% | 100% | 100% | 100% | 30% | 11300460 | 97 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 120 | 19610681 | 5037 | 120.888 | 5.037 | 3.7 | 3.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 50573616 | 1047 | 207.8618 | 0% | 0% | 0% | 0% | 0% | 30% | 11300956 | 496 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132787 | 132.787 | 132.787 | [12 empty] | 26538 | 26538 | 199.8539 | 0% | 0% | 0% | 0% | 0% |  | 3283 | 3283 | 1.144 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 1, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24142 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19610681 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 0 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11300956 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 130 | 121 | 19614864 | 4183 | 100.392 | 4.183 | 4.4 | 4.4 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 75% | 11301520 | 564 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 108 | 19619119 | 4255 | 102.12 | 4.255 | 5.2 | 5.2 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0% | 0% | 100% | 100% | 100% | 75% | 11302030 | 510 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 121 | 105 | 19623329 | 4210 | 101.04 | 4.21 | 6.8 | 6.8 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 304 | 304 | 72.209 | 0% | 0% | 100% | 100% | 100% | 75% | 11302530 | 500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 110 | 19627659 | 4330 | 103.92 | 4.33 | 8.9 | 8.9 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1246 | 942 | 217.552 | 0% | 0% | 100% | 100% | 100% | 75% | 11303073 | 543 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 110 | 101 | 19632188 | 4529 | 108.696 | 4.529 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1087 | N/A | N/A | N/A | N/A | 2218 | 972 | 214.6169 | 0% | 0% | 100% | 100% | 100% | 75% | 11303273 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 128 | 124 | 19637175 | 4987 | 119.688 | 4.987 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1076 | N/A | N/A | N/A | N/A | 3127 | 909 | 182.2739 | 0% | 0% | 100% | 100% | 100% | 0% | 11303273 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 142 | 19643234 | 6059 | 145.416 | 6.059 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 4228 | 1101 | 181.7132 | 0% | 0% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 140 | 19649468 | 6234 | 149.616 | 6.234 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 5392 | 1164 | 186.718 | 0% | 0% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 143 | 19655731 | 6263 | 150.312 | 6.263 | 9.2 | 9.2 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 6564 | 1172 | 187.1308 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 141 | 19661963 | 6232 | 149.568 | 6.232 | 8.7 | 8.7 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 7738 | 1174 | 188.3825 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 | 1.03
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 143 | 19668114 | 6151 | 147.624 | 6.151 | 8.2 | 8.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 8957 | 1219 | 198.1792 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 19674122 | 6008 | 144.192 | 6.008 | 7.5 | 7.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 10143 | 1186 | 197.4035 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 19680319 | 6197 | 148.728 | 6.197 | 6.8 | 6.8 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 11366 | 1223 | 197.3536 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 144 | 19686453 | 6134 | 147.216 | 6.134 | 6.2 | 6.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 12575 | 1209 | 197.0981 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 139 | 19692309 | 5856 | 140.544 | 5.856 | 5.7 | 5.7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 13760 | 1185 | 202.3566 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 140 | 19698337 | 6028 | 144.672 | 6.028 | 5.2 | 5.2 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 14949 | 1189 | 197.2462 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 139 | 19704217 | 5880 | 141.12 | 5.88 | 4.7 | 4.7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 16131 | 1182 | 201.0204 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 138 | 19710018 | 5801 | 139.224 | 5.801 | 4.3 | 4.3 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 17314 | 1183 | 203.9304 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 136 | 19715737 | 5719 | 137.256 | 5.719 | 3.8 | 3.8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 18495 | 1181 | 206.5046 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 131 | 19721422 | 5685 | 136.44 | 5.685 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 19667 | 1172 | 206.1566 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 127 | 19727163 | 5741 | 137.784 | 5.741 | 3.3 | 3.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 20854 | 1187 | 206.7584 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 132 | 19733102 | 5939 | 142.536 | 5.939 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 22032 | 1178 | 198.3499 | 0% | 100% | 100% | 100% | 100% | 0% | 11303273 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 125 | 19738266 | 5164 | 123.936 | 5.164 | 3.1 | 3.1 | 3B | 0 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 23110 | 1078 | 208.7529 | 0% | 100% | 100% | 100% | 100% | 30% | 11303320 | 47 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 121 | 19743324 | 5058 | 121.392 | 5.058 | 3.7 | 3.7 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 24142 | 1032 | 204.0332 | 0% | 0% | 100% | 100% | 100% | 30% | 11303938 | 618 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132643 | 132.643 | 132.643 | [12 empty] | 24142 | 24142 | 182.0073 | 0% | 0% | 0% | 0% | 0% |  | 2982 | 2982 | 1.0833 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
MERALCO POWER STOOPED @ 12:03 AM DUE TO LOAD TEST OF GENSET 1 AND 2
ALL BOOSTER PUMP STOPPED @ 12:03 AM
GENSET 2 POWER STARTED @ 12:04 AM
BP2 - STARTED @ 12:05 AM
BP1 - STARTED @ 12:06 AM
BP3 - STARTED @ 12:07 AM
NORMAL OPERATION
GENSET 2 STOPPED @ 1:04 AM AND SWITCH IT TO GENSET 1 @ 1:04 AM
GENSET 1 STOPPED @ 1:50 AM
BACK TO MERALCO POWER @ 1:51 AM
GENSET 1 AND 2 STARTED WARMUP @ 2:00 AM AND STOPPED @ 2: 21 AM
MR. CONRADO BINONDO OF ELECDES RESET THE MAIN POWER CONSUMPTION KWTHR OF @ GENSET @ 2:45 AM
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26870 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19743324 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 24142 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11303938 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 120 | 112 | 19748444 | 5120 | 122.88 | 5.12 | 4.6 | 4.6 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 25218 | 1076 | 210.1562 | 0% | 0% | 100% | 100% | 100% | 60% | 11304734 | 796 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 114 | 106 | 19753568 | 5124 | 122.976 | 5.124 | 5.7 | 5.7 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 26300 | 1082 | 211.1632 | 0% | 0% | 100% | 100% | 100% | 60% | 11305632 | 898 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 118 | 104 | 19758688 | 5120 | 122.88 | 5.12 | 7 | 7 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 27374 | 1074 | 209.7656 | 0% | 0% | 100% | 100% | 100% | 60% | 11306502 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 108 | 19762088 | 3400 | 81.6 | 3.4 | 8.5 | 8.5 | 3B | 0 | 0 | 1156 | 1185 | 1156 | N/A | N/A | N/A | N/A | 28194 | 820 | 241.1765 | 0% | 0% | 100% | 100% | 100% | 60% | 11306802 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 117 | 19765432 | 3344 | 80.256 | 3.344 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 29020 | 826 | 247.0096 | 0% | 0% | 100% | 100% | 100% | 60% | 11306909 | 107 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 | 135 | 19770874 | 5442 | 130.608 | 5.442 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 30123 | 1103 | 202.6828 | 0% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 138 | 19776801 | 5927 | 142.248 | 5.927 | 9.2 | 9.2 | 3B + 1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 31285 | 1162 | 196.052 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 140 | 19782725 | 5924 | 142.176 | 5.924 | 8.8 | 8.8 | 3B + 1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 32450 | 1165 | 196.6577 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 142 | 19788666 | 5941 | 142.584 | 5.941 | 8.4 | 8.4 | 3B + 1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 33635 | 1185 | 199.4614 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 144 | 19794740 | 6074 | 145.776 | 6.074 | 8 | 8 | 3B + 1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 34811 | 1176 | 193.6121 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 | 1.03
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 19800671 | 5931 | 142.344 | 5.931 | 7.6 | 7.6 | 3B + 1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 36014 | 1203 | 202.8326 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 141 | 19806555 | 5884 | 141.216 | 5.884 | 6.9 | 6.9 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 37183 | 1169 | 198.6744 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 141 | 19812583 | 6028 | 144.672 | 6.028 | 6.3 | 6.3 | 3B + 1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 38413 | 1230 | 204.0478 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 135 | 19818437 | 5854 | 140.496 | 5.854 | 5.8 | 5.8 | 3B + 1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 39583 | 1170 | 199.8633 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 131 | 19824187 | 5750 | 138 | 5.75 | 5.6 | 5.6 | 3B + 1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 40727 | 1144 | 198.9565 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 19829884 | 5697 | 136.728 | 5.697 | 5.3 | 5.3 | 3B + 1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 41892 | 1165 | 204.4936 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 19835590 | 5706 | 136.944 | 5.706 | 5.1 | 5.1 | 3B + 1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 43056 | 1164 | 203.9958 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 133 | 19841266 | 5676 | 136.224 | 5.676 | 4.9 | 4.9 | 3B + 1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 44225 | 1169 | 205.9549 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 19847022 | 5756 | 138.144 | 5.756 | 4.6 | 4.6 | 3B + 1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 45387 | 1162 | 201.8763 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 132 | 19852752 | 5730 | 137.52 | 5.73 | 4.4 | 4.4 | 3B + 1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 46544 | 1157 | 201.9197 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 129 | 19858317 | 5565 | 133.56 | 5.565 | 4.1 | 4.1 | 3B + 1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 47704 | 1160 | 208.4456 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 128 | 19863853 | 5536 | 132.864 | 5.536 | 3.8 | 3.8 | 3B + 1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 48859 | 1155 | 208.6344 | 100% | 0% | 100% | 100% | 100% | 0% | 11306909 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 122 | 19869043 | 5190 | 124.56 | 5.19 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 49943 | 1084 | 208.8632 | 0% | 0% | 100% | 100% | 100% | 35% | 11307050 | 141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 119 | 19874130 | 5087 | 122.088 | 5.087 | 4.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 51012 | 1069 | 210.1435 | 0% | 0% | 100% | 100% | 100% | 35% | 11307325 | 275 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130806 | 130.806 | 130.806 | [12 empty] | 26870 | 26870 | 205.4187 | 0% | 0% | 0% | 0% | 0% |  | 3387 | 3387 | 1.0983 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 3, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26868 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 19874130 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 51012 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11307325 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 131 | 116 | 19879075 | 4945 | 118.68 | 4.945 | 4.9 | 4.9 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 52050 | 1038 | 209.909 | 0% | 0% | 100% | 100% | 100% | 60% | 11307846 | 521 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 109 | 19883891 | 4816 | 115.584 | 4.816 | 5.8 | 5.8 | 3B | 0 | 0 | 1145 | 1185 | 1147 | N/A | N/A | N/A | N/A | 53041 | 991 | 205.7724 | 0% | 0% | 100% | 100% | 100% | 60% | 11308403 | 557 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 120 | 107 | 19888490 | 4599 | 110.376 | 4.599 | 6.9 | 6.9 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 53999 | 958 | 208.3062 | 0% | 0% | 100% | 100% | 100% | 60% | 11308912 | 509 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 108 | 19892596 | 4106 | 98.544 | 4.106 | 8.8 | 8.8 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 54982 | 983 | 239.4057 | 0% | 0% | 100% | 100% | 100% | 60% | 11309426 | 514 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 122 | 19896777 | 4181 | 100.344 | 4.181 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 55981 | 999 | 238.9381 | 0% | 0% | 100% | 100% | 100% | 60% | 11309486 | 60 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 129 | 19902325 | 5548 | 133.152 | 5.548 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 57091 | 1110 | 200.0721 | 0% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 140 | 19908321 | 5996 | 143.904 | 5.996 | 9.5 | 9.5 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 58214 | 1123 | 187.2915 | 0% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 140 | 19914289 | 5968 | 143.232 | 5.968 | 9.1 | 9.1 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 59404 | 1190 | 199.3968 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 142 | 19920284 | 5995 | 143.88 | 5.995 | 8.6 | 8.6 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 60548 | 1144 | 190.8257 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 140 | 19926274 | 5990 | 143.76 | 5.99 | 8.1 | 8.1 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 61781 | 1233 | 205.8431 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 | 1.05
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 141 | 19932082 | 5808 | 139.392 | 5.808 | 7.73 | 7.73 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 62994 | 1213 | 208.8499 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 19937882 | 5800 | 139.2 | 5.8 | 7.6 | 7.6 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 64106 | 1112 | 191.7241 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 140 | 19943373 | 5491 | 131.784 | 5.491 | 6.7 | 6.7 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 65225 | 1119 | 203.788 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 132 | 19949259 | 5886 | 141.264 | 5.886 | 6.4 | 6.4 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 66451 | 1226 | 208.2909 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 19955077 | 5818 | 139.632 | 5.818 | 6.2 | 6.2 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 67646 | 1195 | 205.397 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 19960660 | 5583 | 133.992 | 5.583 | 6 | 6 | 3B + 1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 68802 | 1156 | 207.0571 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 19966393 | 5733 | 137.592 | 5.733 | 5.8 | 5.8 | 3B + 1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 69964 | 1162 | 202.6862 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 132 | 19972158 | 5765 | 138.36 | 5.765 | 5.5 | 5.5 | 3B + 1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 71129 | 1165 | 202.0815 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 19977878 | 5720 | 137.28 | 5.72 | 5.2 | 5.2 | 3B + 1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 72302 | 1173 | 205.0699 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 135 | 136 | 19983639 | 5761 | 138.264 | 5.761 | 5 | 5 | 3B + 1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 73464 | 1162 | 201.7011 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 133 | 135 | 19989350 | 5711 | 137.064 | 5.711 | 4.7 | 4.7 | 3B + 1S | 1025 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 74634 | 1170 | 204.8678 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 129 | 19995282 | 5932 | 142.368 | 5.932 | 4.5 | 4.5 | 3B + 1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 75832 | 1198 | 201.9555 | 100% | 0% | 100% | 100% | 100% | 0% | 11309486 | 0 | 0.74 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 124 | 20000332 | 5050 | 121.2 | 5.05 | 4.6 | 4.6 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 76866 | 1034 | 204.7525 | 0% | 0% | 100% | 100% | 100% | 30% | 11309648 | 162 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 146 | 113 | 20005316 | 4984 | 119.616 | 4.984 | 5.5 | 5.5 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 77880 | 1014 | 203.451 | 0% | 0% | 100% | 100% | 100% | 30% | 11310556 | 908 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131186 | 131.186 | 131.186 | [12 empty] | 26868 | 26868 | 204.8084 | [6 empty] | 3231 | 3231 | 1.0683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 2, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/JEFFREY LAMAYO
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26462 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20005316 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 77880 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11310556 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 134 | 108 | 20010078 | 4762 | 114.288 | 4.762 | 6.4 | 6.4 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 78834 | 954 | 200.336 | 0% | 0% | 100% | 100% | 100% | 60% | 11311210 | 654 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 120 | 110 | 20014598 | 4520 | 108.48 | 4.52 | 7.2 | 7.2 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 79750 | 916 | 202.6549 | 0% | 0% | 100% | 100% | 100% | 60% | 11311820 | 610 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 123 | 106 | 20019118 | 4520 | 108.48 | 4.52 | 7.6 | 7.6 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 80664 | 914 | 202.2124 | 0% | 0% | 100% | 100% | 100% | 60% | 11312420 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 106 | 111 | 20023642 | 4524 | 108.576 | 4.524 | 8.2 | 8.2 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 81586 | 922 | 203.8019 | 0% | 0% | 100% | 100% | 100% | 60% | 11313042 | 622 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 124 | 20027906 | 4264 | 102.336 | 4.264 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 82526 | 940 | 220.4503 | 0% | 0% | 100% | 100% | 100% | 60% | 11313142 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 126 | 132 | 20032984 | 5078 | 121.872 | 5.078 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 83544 | 1018 | 200.4726 | 0% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 | 1.07 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 142 | 20038987 | 6003 | 144.072 | 6.003 | 9.3 | 9.3 | 3B + 1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 84721 | 1177 | 196.0686 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 20044992 | 6005 | 144.12 | 6.005 | 8.8 | 8.8 | 3B + 1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 85906 | 1185 | 197.3356 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 142 | 20051015 | 6023 | 144.552 | 6.023 | 8.3 | 8.3 | 3B + 1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 87107 | 1201 | 199.4023 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 20057130 | 6115 | 146.76 | 6.115 | 7.8 | 7.8 | 3B + 1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 88289 | 1182 | 193.2952 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 | 1.01
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 141 | 20063164 | 6034 | 144.816 | 6.034 | 7.4 | 7.4 | 3B + 1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 89483 | 1194 | 197.8787 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 20069151 | 5987 | 143.688 | 5.987 | 6.8 | 6.8 | 3B + 1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 90686 | 1203 | 200.9354 | 0% | 100% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 142 | 20075160 | 6009 | 144.216 | 6.009 | 6.3 | 6.3 | 3B + 1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 91876 | 1190 | 198.0363 | 0% | 100% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 136 | 20081557 | 6397 | 153.528 | 6.397 | 6 | 6 | 3B + 1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 93158 | 1282 | 200.4064 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 20087017 | 5460 | 131.04 | 5.46 | 5.9 | 5.9 | 3B + 1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 94271 | 1113 | 203.8462 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 132 | 20092848 | 5831 | 139.944 | 5.831 | 5.8 | 5.8 | 3B + 1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 95427 | 1156 | 198.2507 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 20098479 | 5631 | 135.144 | 5.631 | 5.5 | 5.5 | 3B + 1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 96589 | 1162 | 206.3577 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 130 | 20104259 | 5780 | 138.72 | 5.78 | 5.3 | 5.3 | 3B + 1S | 1006 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 97734 | 1145 | 198.0969 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 127 | 20109807 | 5548 | 133.152 | 5.548 | 5 | 5 | 3B + 1S | 1005 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 98860 | 1126 | 202.956 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 133 | 20115488 | 5681 | 136.344 | 5.681 | 4.7 | 4.7 | 3B + 1S | 1005 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 99992 | 1132 | 199.2607 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 127 | 20121183 | 5695 | 136.68 | 5.695 | 4.4 | 4.4 | 3B + 1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 101133 | 1141 | 200.3512 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 129 | 20126412 | 5229 | 125.496 | 5.229 | 4.2 | 4.2 | 3B + 1S | 955 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 102220 | 1087 | 207.8791 | 100% | 0% | 100% | 100% | 100% | 0% | 11313142 | 0 | 0.76 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 128 | 120 | 20132006 | 5594 | 134.256 | 5.594 | 4.4 | 4.4 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 103370 | 1150 | 205.5774 | 0% | 0% | 100% | 100% | 100% | 30% | 11313322 | 180 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 112 | 20136682 | 4676 | 112.224 | 4.676 | 5.2 | 5.2 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 104342 | 972 | 207.87 | 0% | 0% | 100% | 100% | 100% | 30% | 11314077 | 755 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131366 | 131.366 | 131.366 | [12 empty] | 26462 | 26462 | 201.4372 | [6 empty] | 3521 | 3521 | 1.0183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:44 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 5, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
SP1 SHIFT TO SP2 DUE PREVENTIVE MAINTENANCE @ 11:30AM
SP2 SHIFT TO SP1 DUE PREVENTIVE MAINTENANCE @ 1:30AM
GENSET 1 WARM UP FOR 5MINS DUE PREVENTIVE MAINTENANCE @ 1:O5PM - 1:10PM
GENSET 2 WARM UP FOR 5MINS DUE PREVENTIVE MAINTENANCE @ 1:11PM - 1:16PM
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/JEFFREY LAMAYO
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26600 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20136682 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 104342 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11314077 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 106 | 20141286 | 4604 | 110.496 | 4.604 | 6 | 6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 105300 | 958 | 208.0799 | 0% | 0% | 100% | 100% | 100% | 60% | 11314898 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 131 | 104 | 20145888 | 4602 | 110.448 | 4.602 | 7.1 | 7.1 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 106240 | 940 | 204.259 | 0% | 0% | 100% | 100% | 100% | 60% | 11315816 | 918 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 108 | 20150106 | 4218 | 101.232 | 4.218 | 8.1 | 8.1 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 107100 | 860 | 203.8881 | 0% | 0% | 100% | 100% | 100% | 60% | 11316652 | 836 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 110 | 20154468 | 4362 | 104.688 | 4.362 | 9.5 | 9.5 | 3B | 0 | 0 | 1067 | 1185 | 1067 | N/A | N/A | N/A | N/A | 108040 | 940 | 215.4975 | 0% | 0% | 100% | 100% | 100% | 60% | 11316874 | 222 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 | 111 | 20158846 | 4378 | 105.072 | 4.378 | 9.5 | 9.5 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 108970 | 930 | 212.4258 | 0% | 0% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 134 | 20164246 | 5400 | 129.6 | 5.4 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 110012 | 1042 | 192.963 | 0% | 0% | 100% | 100% | 100% | 0% | 11316874 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 141 | 20170314 | 6068 | 145.632 | 6.068 | 9.2 | 9.2 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 111186 | 1174 | 193.474 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 20176322 | 6008 | 144.192 | 6.008 | 8.7 | 8.7 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 112382 | 1196 | 199.0679 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 139 | 20182612 | 6290 | 150.96 | 6.29 | 8 | 8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 113640 | 1258 | 200 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 140 | 20188822 | 6210 | 149.04 | 6.21 | 7.5 | 7.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 114832 | 1192 | 191.9485 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 | 1.48
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 143 | 20195034 | 6212 | 149.088 | 6.212 | 6.9 | 6.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 116064 | 1232 | 198.3258 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 136 | 20200716 | 5682 | 136.368 | 5.682 | 6.4 | 6.4 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 117202 | 1138 | 200.2816 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 136 | 132 | 20206544 | 5828 | 139.872 | 5.828 | 6 | 6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 118396 | 1194 | 204.873 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 140 | 20212115 | 5571 | 133.704 | 5.571 | 5.7 | 5.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 119557 | 1161 | 208.4006 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 136 | 20217904 | 5789 | 138.936 | 5.789 | 5.4 | 5.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 120727 | 1170 | 202.1074 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 142 | 20223745 | 5841 | 140.184 | 5.841 | 5.1 | 5.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 121910 | 1183 | 202.5338 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 20229537 | 5792 | 139.008 | 5.792 | 4.8 | 4.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 123066 | 1156 | 199.5856 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 131 | 20235163 | 5626 | 135.024 | 5.626 | 4.6 | 4.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 124225 | 1159 | 206.0078 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 126 | 20240737 | 5574 | 133.776 | 5.574 | 4.4 | 4.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 125383 | 1158 | 207.7503 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 130 | 20246129 | 5392 | 129.408 | 5.392 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 126522 | 1139 | 211.2389 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 127 | 20251687 | 5558 | 133.392 | 5.558 | 4 | 4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 127685 | 1163 | 209.2479 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 120 | 20257496 | 5809 | 139.416 | 5.809 | 4.1 | 4.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 128900 | 1215 | 209.1582 | 0% | 100% | 100% | 100% | 100% | 0% | 11316874 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 118 | 20262472 | 4976 | 119.424 | 4.976 | 4.2 | 4.2 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 129936 | 1036 | 208.1994 | 0% | 0% | 100% | 100% | 100% | 30% | 11316941 | 67 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 116 | 20267330 | 4858 | 116.592 | 4.858 | 4.7 | 4.7 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 130942 | 1006 | 207.0811 | 0% | 0% | 100% | 100% | 100% | 3% | 11317498 | 557 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130648 | 130.648 | 130.648 | [12 empty] | 26600 | 26600 | 203.6005 | [6 empty] | 3421 | 3421 | 1.2317 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 6, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / JEFFREY LAMAYO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26608 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20267330 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 130942 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11317498 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 142 | 108 | 20272040 | 4710 | 113.04 | 4.71 | 5.9 | 5.9 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 131888 | 946 | 200.8493 | 0% | 0% | 100% | 100% | 100% | 60% | 11318686 | 1188 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 104 | 20276632 | 4592 | 110.208 | 4.592 | 7.3 | 7.3 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 132816 | 928 | 202.0906 | 0% | 0% | 100% | 100% | 100% | 60% | 11319782 | 1096 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 120 | 107 | 20281224 | 4592 | 110.208 | 4.592 | 8.4 | 8.4 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 133748 | 932 | 202.9617 | 0% | 0% | 100% | 100% | 100% | 60% | 11320786 | 1004 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 127 | 108 | 20285542 | 4318 | 103.632 | 4.318 | 8.8 | 8.8 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 134618 | 870 | 201.4822 | 0% | 0% | 100% | 100% | 100% | 60% | 11321310 | 524 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 125 | 20290126 | 4584 | 110.016 | 4.584 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 135592 | 974 | 212.4782 | 0% | 0% | 100% | 100% | 100% | 60% | 11321424 | 114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 | 139 | 20295553 | 5427 | 130.248 | 5.427 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 136593 | 1001 | 184.4481 | 0% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 142 | 20301620 | 6067 | 145.608 | 6.067 | 9.3 | 9.3 | 3B+1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 137850 | 1257 | 207.1864 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 20307482 | 5862 | 140.688 | 5.862 | 9 | 9 | 3B+1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 138938 | 1088 | 185.6022 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 141 | 20313390 | 5908 | 141.792 | 5.908 | 8.5 | 8.5 | 3B+1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 140126 | 1188 | 201.0833 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 143 | 20319497 | 6107 | 146.568 | 6.107 | 8 | 8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 141314 | 1188 | 194.5309 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 | 1.09
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 140 | 20325652 | 6155 | 147.72 | 6.155 | 7.4 | 7.4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 142524 | 1210 | 196.5881 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 20331589 | 5937 | 142.488 | 5.937 | 7.1 | 7.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 143684 | 1160 | 195.3849 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 20337748 | 6159 | 147.816 | 6.159 | 6.7 | 6.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 144866 | 1182 | 191.9143 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 138 | 20343854 | 6106 | 146.544 | 6.106 | 6.3 | 6.3 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 146101 | 1235 | 202.2601 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 136 | 20349583 | 5729 | 137.496 | 5.729 | 6 | 6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 147285 | 1184 | 206.6678 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 20355405 | 5822 | 139.728 | 5.822 | 5.8 | 5.8 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 148448 | 1163 | 199.7595 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 20361235 | 5830 | 139.92 | 5.83 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 149620 | 1172 | 201.0292 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 136 | 20367060 | 5825 | 139.8 | 5.825 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 150792 | 1172 | 201.2017 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 132 | 20372756 | 5696 | 136.704 | 5.696 | 5 | 5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 151957 | 1165 | 204.5295 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 133 | 20378438 | 5682 | 136.368 | 5.682 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 153122 | 1165 | 205.0334 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 130 | 20384160 | 5722 | 137.328 | 5.722 | 4.4 | 4.4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 154294 | 1172 | 204.8235 | 100% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 127 | 20389855 | 5695 | 136.68 | 5.695 | 4.1 | 4.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1185 | N/A | N/A | N/A | N/A | 155433 | 1139 | 200 | 0% | 0% | 100% | 100% | 100% | 0% | 11321424 | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 126 | 121 | 20394801 | 4946 | 118.704 | 4.946 | 4.1 | 4.1 | 3B | 0 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 156507 | 1074 | 217.1452 | 0% | 0% | 100% | 100% | 100% | 30% | 11321472 | 48 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 111 | 20399802 | 5001 | 120.024 | 5.001 | 4.6 | 4.6 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 157550 | 1043 | 208.5583 | 0% | 0% | 100% | 100% | 100% | 30% | 11321989 | 517 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132472 | 132.472 | 132.472 | [12 empty] | 26608 | 26608 | 200.8575 | [6 empty] | 4491 | 4491 | 1.095 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 7, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL A. RAMOS / JEFFREY LAMAYO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26618 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20399802 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 157550 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11321989 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 104 | 20404379 | 4577 | 109.848 | 4.577 | 5.4 | 5.4 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 158526 | 976 | 213.2401 | 0% | 0% | 100% | 100% | 100% | 60% | 11322692 | 703 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 122 | 109 | 20409002 | 4623 | 110.952 | 4.623 | 6.4 | 6.4 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 159478 | 952 | 205.9269 | 0% | 0% | 100% | 100% | 100% | 60% | 11323692 | 1000 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 119 | 126 | 20413628 | 4626 | 111.024 | 4.626 | 7.5 | 7.5 | 3B | 0 | 0 | 1106 | 1185 | 1107 | N/A | N/A | N/A | N/A | 160434 | 956 | 206.658 | 0% | 0% | 100% | 100% | 100% | 60% | 11324637 | 945 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 118 | 20417808 | 4180 | 100.32 | 4.18 | 9.1 | 9.1 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 161376 | 942 | 225.3589 | 0% | 0% | 100% | 100% | 100% | 60% | 11324752 | 115 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 117 | 115 | 20421975 | 4167 | 100.008 | 4.167 | 9.5 | 9.5 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 162320 | 944 | 226.5419 | 0% | 0% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 130 | 125 | 20427158 | 5183 | 124.392 | 5.183 | 9.5 | 9.5 | 3B | 0 | 0 | 1086 | 1185 | 1087 | N/A | N/A | N/A | N/A | 163241 | 921 | 177.6963 | 0% | 0% | 100% | 100% | 100% | 0% | 11324752 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 140 | 20432575 | 5417 | 130.008 | 5.417 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 164305 | 1064 | 196.4187 | 0% | 0% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 20438393 | 5818 | 139.632 | 5.818 | 9.2 | 9.2 | 3B + 1S | 0 | 997 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 165455 | 1150 | 197.6624 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 143 | 20444468 | 6075 | 145.8 | 6.075 | 8.6 | 8.6 | 3B + 1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 166662 | 1207 | 198.6831 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 143 | 20450623 | 6155 | 147.72 | 6.155 | 7.9 | 7.9 | 3B + 1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 167883 | 1221 | 198.3753 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 | 1.03
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 142 | 20456860 | 6237 | 149.688 | 6.237 | 7.3 | 7.3 | 3B + 1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 169101 | 1218 | 195.2862 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 20463021 | 6161 | 147.864 | 6.161 | 6.7 | 6.7 | 3B + 1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 170299 | 1198 | 194.449 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 143 | 20468975 | 5954 | 142.896 | 5.954 | 6.1 | 6.1 | 3B + 1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 171481 | 1182 | 198.522 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 20475129 | 6154 | 147.696 | 6.154 | 5.6 | 5.6 | 3B + 1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 172703 | 1222 | 198.57 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 135 | 20480998 | 5869 | 140.856 | 5.869 | 5.2 | 5.2 | 3B + 1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 173839 | 1136 | 193.5594 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 20486755 | 5757 | 138.168 | 5.757 | 4.9 | 4.9 | 3B + 1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 175013 | 1174 | 203.9257 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 20492535 | 5780 | 138.72 | 5.78 | 4.6 | 4.6 | 3B + 1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 176183 | 1170 | 202.4221 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 20498221 | 5686 | 136.464 | 5.686 | 4.3 | 4.3 | 3B + 1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 177346 | 1163 | 204.5375 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 137 | 20504118 | 5897 | 141.528 | 5.897 | 4 | 4 | 3B + 1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 178515 | 1169 | 198.2364 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 130 | 20509965 | 5847 | 140.328 | 5.847 | 3.7 | 3.7 | 3B + 1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 179671 | 1156 | 197.7082 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 128 | 20515528 | 5563 | 133.512 | 5.563 | 3.4 | 3.4 | 3B + 1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 180813 | 1142 | 205.2849 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 132 | 20521707 | 6179 | 148.296 | 6.179 | 3.1 | 3.1 | 3B + 1S | 0 | 1044 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 182140 | 1327 | 214.7597 | 0% | 100% | 100% | 100% | 100% | 0% | 11324752 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 119 | 20526445 | 4738 | 113.712 | 4.738 | 3.2 | 3.2 | 3B | 0 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 183144 | 1004 | 211.9038 | 0% | 0% | 100% | 100% | 100% | 30% | 11324854 | 102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 144 | 110 | 20531311 | 4866 | 116.784 | 4.866 | 4.2 | 4.2 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 184168 | 1024 | 210.4398 | 0% | 0% | 100% | 100% | 100% | 30% | 11325813 | 959 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131509 | 131.509 | 131.509 | [12 empty] | 26618 | 26618 | 202.4044 | [6 empty] | 3824 | 3824 | 1.1217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:42 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 8, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26258 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20531311 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 184168 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11325813 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 146 | 107 | 20535624 | 4313 | 103.512 | 4.313 | 4.9 | 4.9 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 185088 | 920 | 213.3086 | 0% | 0% | 100% | 100% | 100% | 60% | 11326413 | 600 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 106 | 20540068 | 4444 | 106.656 | 4.444 | 5.8 | 5.8 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 186018 | 930 | 209.2709 | 0% | 0% | 100% | 100% | 100% | 60% | 11327314 | 901 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 110 | 20544511 | 4443 | 106.632 | 4.443 | 6.5 | 6.5 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 186938 | 920 | 207.0673 | 0% | 0% | 100% | 100% | 100% | 60% | 11328223 | 909 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 144 | 112 | 20549075 | 4564 | 109.536 | 4.564 | 7.6 | 7.6 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 187865 | 927 | 203.1113 | 0% | 0% | 100% | 100% | 100% | 60% | 11328812 | 589 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 120 | 20553408 | 4333 | 103.992 | 4.333 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 1046 | N/A | N/A | N/A | N/A | 188931 | 1066 | 246.0189 | 0% | 0% | 100% | 100% | 100% | 60% | 11329010 | 198 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 | 138 | 20558943 | 5535 | 132.84 | 5.535 | 9.5 | 9.5 | 3B | 0 | 0 | 1155 | 1185 | 1155 | N/A | N/A | N/A | N/A | 190015 | 1084 | 195.8446 | 0% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 | 1.13 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 141 | 20564820 | 5877 | 141.048 | 5.877 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 191087 | 1072 | 182.406 | 0% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 140 | 20570648 | 5828 | 139.872 | 5.828 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 192168 | 1081 | 185.4839 | 0% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 143 | 20576535 | 5887 | 141.288 | 5.887 | 9.5 | 9.5 | 3B+ 1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 193254 | 1086 | 184.4743 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 145 | 20582308 | 5773 | 138.552 | 5.773 | 8.7 | 8.7 | 3B+ 1S | 997 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 194335 | 1081 | 187.251 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 | 1.07
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 20588193 | 5885 | 141.24 | 5.885 | 8.2 | 8.2 | 3B+ 1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 195429 | 1094 | 185.8963 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 141 | 20593925 | 5732 | 137.568 | 5.732 | 7.7 | 7.7 | 3B+ 1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 196538 | 1109 | 193.4752 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 20599773 | 5848 | 140.352 | 5.848 | 7.4 | 7.4 | 3B+ 1S | 1017 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 197699 | 1161 | 198.5294 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 142 | 20605905 | 6132 | 147.168 | 6.132 | 6.8 | 6.8 | 3B+ 1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 198956 | 1257 | 204.9902 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 137 | 20612047 | 6142 | 147.408 | 6.142 | 6.4 | 6.4 | 3B+ 1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 200170 | 1214 | 197.6555 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 20618088 | 6041 | 144.984 | 6.041 | 6 | 6 | 3B+ 1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 201355 | 1185 | 196.1596 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 20623994 | 5906 | 141.744 | 5.906 | 5.5 | 5.5 | 3B+ 1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 202530 | 1175 | 198.9502 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 132 | 20629860 | 5866 | 140.784 | 5.866 | 5.2 | 5.2 | 3B+ 1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 203709 | 1179 | 200.9887 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 135 | 20635744 | 5884 | 141.216 | 5.884 | 4.8 | 4.8 | 3B+ 1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 204890 | 1181 | 200.7138 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 138 | 20641418 | 5674 | 136.176 | 5.674 | 4.4 | 4.4 | 3B+ 1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 206060 | 1170 | 206.2037 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 132 | 20646938 | 5520 | 132.48 | 5.52 | 4.1 | 4.1 | 3B+ 1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 207224 | 1164 | 210.8696 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 132 | 128 | 20652346 | 5408 | 129.792 | 5.408 | 3.8 | 3.8 | 3B+ 1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 208316 | 1092 | 201.9231 | 100% | 0% | 100% | 100% | 100% | 0% | 11329010 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 121 | 20657848 | 5502 | 132.048 | 5.502 | 3.9 | 3.9 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 209448 | 1132 | 205.7434 | 0% | 0% | 100% | 100% | 100% | 30% | 11329094 | 84 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 110 | 20662564 | 4716 | 113.184 | 4.716 | 4.7 | 4.7 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 210426 | 978 | 207.3791 | 0% | 0% | 100% | 100% | 100% | 30% | 11329844 | 750 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131253 | 131.253 | 131.253 | [12 empty] | 26258 | 26258 | 200.0564 | [6 empty] | 4031 | 4031 | 1.1117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 9, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26442 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20662564 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 210426 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11329844 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 107 | 20667378 | 4814 | 115.536 | 4.814 | 5.6 | 5.6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 211420 | 994 | 206.4811 | 0% | 0% | 100% | 100% | 100% | 60% | 11330698 | 854 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 106 | 20671766 | 4388 | 105.312 | 4.388 | 6.7 | 6.7 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 212320 | 900 | 205.1048 | 0% | 0% | 100% | 100% | 100% | 60% | 11331698 | 1000 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 103 | 20676148 | 4382 | 105.168 | 4.382 | 7.8 | 7.8 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 213222 | 902 | 205.8421 | 0% | 0% | 100% | 100% | 100% | 60% | 11332622 | 924 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 110 | 20680498 | 4350 | 104.4 | 4.35 | 9 | 9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 214164 | 942 | 216.5517 | 0% | 0% | 100% | 100% | 100% | 60% | 11332842 | 220 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 115 | 113 | 20684868 | 4370 | 104.88 | 4.37 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 215120 | 956 | 218.7643 | 0% | 0% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 137 | 20690335 | 5467 | 131.208 | 5.467 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 216110 | 990 | 181.0865 | 0% | 0% | 100% | 100% | 100% | 0% | 11332842 | 0 | 1.15 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 138 | 20696581 | 6246 | 149.904 | 6.246 | 9.2 | 9.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 217347 | 1237 | 198.0467 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 137 | 20702477 | 5896 | 141.504 | 5.896 | 8.8 | 8.8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 218527 | 1180 | 200.1357 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 138 | 20708492 | 6015 | 144.36 | 6.015 | 8.3 | 8.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 219713 | 1186 | 197.1737 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 138 | 20715343 | 6851 | 164.424 | 6.851 | 7.7 | 7.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 221063 | 1350 | 197.0515 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 | 1.17
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 140 | 20720591 | 5248 | 125.952 | 5.248 | 7.3 | 7.3 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 222104 | 1041 | 198.3613 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 137 | 20726887 | 6296 | 151.104 | 6.296 | 6.8 | 6.8 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 223366 | 1262 | 200.4447 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 137 | 20732297 | 5410 | 129.84 | 5.41 | 6.4 | 6.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 224475 | 1109 | 204.9908 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 20738094 | 5797 | 139.128 | 5.797 | 6.1 | 6.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 225645 | 1170 | 201.8285 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 135 | 20743875 | 5781 | 138.744 | 5.781 | 5.8 | 5.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 226814 | 1169 | 202.2141 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 132 | 20749711 | 5836 | 140.064 | 5.836 | 5.5 | 5.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 227980 | 1166 | 199.7944 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 20755351 | 5640 | 135.36 | 5.64 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 229139 | 1159 | 205.4965 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 135 | 20761022 | 5671 | 136.104 | 5.671 | 5 | 5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 230307 | 1168 | 205.9601 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 127 | 20766616 | 5594 | 134.256 | 5.594 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 231471 | 1164 | 208.0801 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 132 | 20772198 | 5582 | 133.968 | 5.582 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 232632 | 1161 | 207.99 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 131 | 20777793 | 5595 | 134.28 | 5.595 | 4.1 | 4.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 233793 | 1161 | 207.5067 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 130 | 20782901 | 5108 | 122.592 | 5.108 | 3.9 | 3.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 234862 | 1069 | 209.2796 | 0% | 100% | 100% | 100% | 100% | 0% | 11332842 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 128 | 119 | 20787915 | 5014 | 120.336 | 5.014 | 4 | 4 | 3B | 0 | 0 | 1146 | 1185 | 1187 | N/A | N/A | N/A | N/A | 235919 | 1057 | 210.8097 | 0% | 0% | 100% | 100% | 100% | 20% | 11332941 | 99 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 106 | 20792522 | 4607 | 110.568 | 4.607 | 5 | 5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 236868 | 949 | 205.9909 | 0% | 0% | 100% | 100% | 100% | 20% | 11333880 | 939 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129958 | 129.958 | 129.958 | [12 empty] | 26442 | 26442 | 203.4657 | [6 empty] | 4036 | 4036 | 1.1567 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## OCT 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26570 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20792522 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 236868 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11333880 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 108 | 20796797 | 4275 | 102.6 | 4.275 | 6.2 | 6.2 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 237758 | 890 | 208.1871 | 0% | 0% | 100% | 100% | 100% | 70% | 11334636 | 756 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 136 | 105 | 20801085 | 4288 | 102.912 | 4.288 | 7.1 | 7.1 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 238663 | 905 | 211.0541 | 0% | 0% | 100% | 100% | 100% | 70% | 11335396 | 760 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 104 | 20805295 | 4210 | 101.04 | 4.21 | 8 | 8 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 239549 | 886 | 210.4513 | 0% | 0% | 100% | 100% | 100% | 70% | 11336016 | 620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 111 | 20809728 | 4433 | 106.392 | 4.433 | 9.1 | 9.1 | 3B | 0 | 0 | 1067 | 1185 | 1047 | N/A | N/A | N/A | N/A | 240451 | 902 | 203.4739 | 0% | 0% | 100% | 100% | 100% | 70% | 11336796 | 780 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 | 115 | 20814361 | 4633 | 111.192 | 4.633 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1137 | N/A | N/A | N/A | N/A | 241372 | 921 | 198.7913 | 0% | 0% | 100% | 100% | 100% | 70% | 11336905 | 109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 145 | 134 | 20820295 | 5934 | 142.416 | 5.934 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 242511 | 1139 | 191.9447 | 0% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 | 1.2 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 139 | 20826361 | 6066 | 145.584 | 6.066 | 9.2 | 9.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 243696 | 1185 | 195.3511 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 141 | 20832407 | 6046 | 145.104 | 6.046 | 8.3 | 8.3 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 244870 | 1174 | 194.178 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 151 | 20838516 | 6109 | 146.616 | 6.109 | 8.3 | 8.3 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 246071 | 1201 | 196.5952 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 147 | 20844585 | 6069 | 145.656 | 6.069 | 7.9 | 7.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 247258 | 1187 | 195.5841 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 | 1.23
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 135 | 20850639 | 6054 | 145.296 | 6.054 | 7.5 | 7.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 248434 | 1176 | 194.2517 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 138 | 20856773 | 6134 | 147.216 | 6.134 | 6.9 | 6.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 249641 | 1207 | 196.7721 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 140 | 20862707 | 5934 | 142.416 | 5.934 | 6.5 | 6.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 250848 | 1207 | 203.4041 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 140 | 20868593 | 5886 | 141.264 | 5.886 | 6.1 | 6.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 252016 | 1168 | 198.437 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 138 | 20874488 | 5895 | 141.48 | 5.895 | 5.7 | 5.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 253194 | 1178 | 199.8304 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 134 | 20880252 | 5764 | 138.336 | 5.764 | 5.4 | 5.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 254370 | 1176 | 204.025 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 20886142 | 5890 | 141.36 | 5.89 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 255541 | 1171 | 198.8115 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 134 | 20891914 | 5772 | 138.528 | 5.772 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 256714 | 1173 | 203.2225 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 20897630 | 5716 | 137.184 | 5.716 | 4.6 | 4.6 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 257883 | 1169 | 204.5136 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 126 | 20903152 | 5522 | 132.528 | 5.522 | 4.3 | 4.3 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 259013 | 1130 | 204.636 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 131 | 20908714 | 5562 | 133.488 | 5.562 | 4.1 | 4.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 260168 | 1155 | 207.6591 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 127 | 20914265 | 5551 | 133.224 | 5.551 | 4 | 4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 261312 | 1144 | 206.089 | 100% | 0% | 100% | 100% | 100% | 0% | 11336905 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 121 | 20919375 | 5110 | 122.64 | 5.11 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 262392 | 1080 | 211.3503 | 0% | 0% | 100% | 100% | 100% | 20% | 11337089 | 184 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 106 | 20924291 | 4916 | 117.984 | 4.916 | 4.9 | 4.9 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 263438 | 1046 | 212.7746 | 0% | 0% | 100% | 100% | 100% | 20% | 11337722 | 633 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131769 | 131.769 | 131.769 | [12 empty] | 26570 | 26570 | 201.6408 | [6 empty] | 3842 | 3842 | 1.185 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## OCT 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | RANDY REGENCIA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/JEFFREY LAMAYO
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26734 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 20924291 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 263438 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11337722 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 101 | 20928876 | 4585 | 110.04 | 4.585 | 5.8 | 5.8 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 264422 | 984 | 214.6129 | 0% | 0% | 100% | 100% | 100% | 70% | 11338608 | 886 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 101 | 20933196 | 4320 | 103.68 | 4.32 | 7 | 7 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 265352 | 930 | 215.2778 | 0% | 0% | 100% | 100% | 100% | 70% | 11339519 | 911 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 103 | 20937507 | 4311 | 103.464 | 4.311 | 8.5 | 8.5 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 266258 | 906 | 210.1601 | 0% | 0% | 100% | 100% | 100% | 70% | 11340437 | 918 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 109 | 103 | 20941820 | 4313 | 103.512 | 4.313 | 9.1 | 9.1 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 267158 | 900 | 208.6715 | 0% | 0% | 100% | 100% | 100% | 70% | 11341307 | 870 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 123 | 20946460 | 4640 | 111.36 | 4.64 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 268152 | 994 | 214.2241 | 0% | 0% | 100% | 100% | 100% | 70% | 11341518 | 211 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 141 | 20952437 | 5977 | 143.448 | 5.977 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 269294 | 1142 | 191.0658 | 0% | 0% | 100% | 100% | 100% | 0% | 11341518 | 0 | 1.02 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 20958442 | 6005 | 144.12 | 6.005 | 9.1 | 9.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 270456 | 1162 | 193.5054 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 145 | 20964470 | 6028 | 144.672 | 6.028 | 8.5 | 8.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 271641 | 1185 | 196.5826 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 146 | 20970370 | 5900 | 141.6 | 5.9 | 8 | 8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 272840 | 1199 | 203.2203 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 144 | 20976698 | 6328 | 151.872 | 6.328 | 7.5 | 7.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 274067 | 1227 | 193.9001 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 | 1.14
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 20982709 | 6011 | 144.264 | 6.011 | 7 | 7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 275211 | 1144 | 190.3178 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 20988927 | 6218 | 149.232 | 6.218 | 6.4 | 6.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 276491 | 1280 | 205.854 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 142 | 20994890 | 5963 | 143.112 | 5.963 | 5.9 | 5.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 277672 | 1181 | 198.0547 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 136 | 21000417 | 5527 | 132.648 | 5.527 | 5.7 | 5.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 278800 | 1128 | 204.089 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 137 | 21006343 | 5926 | 142.224 | 5.926 | 5.5 | 5.5 | 3B+1S | 0 | 1003 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 279951 | 1151 | 194.2288 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 21012127 | 5784 | 138.816 | 5.784 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 281101 | 1150 | 198.8243 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 131 | 21017975 | 5848 | 140.352 | 5.848 | 5.2 | 5.2 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 282279 | 1178 | 201.4364 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 128 | 21023786 | 5811 | 139.464 | 5.811 | 5.1 | 5.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 283446 | 1167 | 200.826 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 136 | 21029484 | 5698 | 136.752 | 5.698 | 4.7 | 4.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 284607 | 1161 | 203.7557 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 129 | 21035057 | 5573 | 133.752 | 5.573 | 4.6 | 4.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 285747 | 1140 | 204.5577 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 130 | 21040746 | 5689 | 136.536 | 5.689 | 4.4 | 4.4 | 3B+1S | 0 | 1009 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 286923 | 1176 | 206.7147 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 124 | 21046312 | 5566 | 133.584 | 5.566 | 4.4 | 4.4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 288068 | 1145 | 205.7133 | 0% | 100% | 100% | 100% | 100% | 0% | 11341518 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 117 | 21051484 | 5172 | 124.128 | 5.172 | 4.5 | 4.5 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 289138 | 1070 | 206.8832 | 0% | 0% | 100% | 100% | 100% | 30% | 11341632 | 114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 111 | 21056442 | 4958 | 118.992 | 4.958 | 5.2 | 5.2 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 290172 | 1034 | 208.5518 | 0% | 0% | 100% | 100% | 100% | 30% | 11342338 | 706 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132151 | 132.151 | 132.151 | [12 empty] | 26734 | 26734 | 202.2989 | [6 empty] | 4616 | 4616 | 1.145 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/JEFFREY LAMAYO
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26534 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21056442 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 290172 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11342338 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 110 | 21061264 | 4822 | 115.728 | 4.822 | 6 | 6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 291148 | 976 | 202.4056 | 0% | 0% | 100% | 100% | 100% | 60% | 11343122 | 784 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 106 | 21065688 | 4424 | 106.176 | 4.424 | 7.1 | 7.1 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 292048 | 900 | 203.4358 | 0% | 0% | 100% | 100% | 100% | 60% | 11344034 | 912 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 103 | 21070102 | 4414 | 105.936 | 4.414 | 8.2 | 8.2 | 3B | 0 | 0 | 1066 | 1185 | 1066 | N/A | N/A | N/A | N/A | 292952 | 904 | 204.8029 | 0% | 0% | 100% | 100% | 100% | 60% | 11345012 | 978 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 110 | 102 | 21074210 | 4108 | 98.592 | 4.108 | 9.5 | 9.5 | 3B | 0 | 0 | 1067 | 1185 | 1067 | N/A | N/A | N/A | N/A | 293828 | 876 | 213.2425 | 0% | 0% | 100% | 100% | 100% | 60% | 11345238 | 226 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 123 | 21078322 | 4112 | 98.688 | 4.112 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 294708 | 880 | 214.0078 | 0% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 133 | 21084612 | 6290 | 150.96 | 6.29 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 295904 | 1196 | 190.1431 | 0% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 138 | 21090090 | 5478 | 131.472 | 5.478 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 296980 | 1076 | 196.4221 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 21095749 | 5659 | 135.816 | 5.659 | 8.7 | 8.7 | 3B+1S | 1038 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 298234 | 1254 | 221.5939 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 140 | 21102206 | 6457 | 154.968 | 6.457 | 8 | 8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 299384 | 1150 | 178.1013 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 142 | 21107932 | 5726 | 137.424 | 5.726 | 7.5 | 7.5 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 300488 | 1104 | 192.8048 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 | 1.22
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 137 | 21114266 | 6334 | 152.016 | 6.334 | 7 | 7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 301716 | 1228 | 193.8743 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 144 | 21120844 | 6578 | 157.872 | 6.578 | 6.2 | 6.2 | 3B+1S | 1148 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 303024 | 1308 | 198.8446 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 134 | 21126672 | 5828 | 139.872 | 5.828 | 5.7 | 5.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 304186 | 1162 | 199.3823 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 131 | 21132368 | 5696 | 136.704 | 5.696 | 5.4 | 5.4 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 305380 | 1194 | 209.6208 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 131 | 21137781 | 5413 | 129.912 | 5.413 | 5.3 | 5.3 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 306513 | 1133 | 209.3109 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 135 | 21143557 | 5776 | 138.624 | 5.776 | 5.1 | 5.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 307678 | 1165 | 201.6967 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 21149123 | 5566 | 133.584 | 5.566 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 308830 | 1152 | 206.9709 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 140 | 21154987 | 5864 | 140.736 | 5.864 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 310018 | 1188 | 202.5921 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 134 | 21160691 | 5704 | 136.896 | 5.704 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 311199 | 1181 | 207.0477 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 129 | 21166175 | 5484 | 131.616 | 5.484 | 4.2 | 4.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 312329 | 1130 | 206.054 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 133 | 21171904 | 5729 | 137.496 | 5.729 | 3.9 | 3.9 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 313524 | 1195 | 208.5879 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 125 | 21177434 | 5530 | 132.72 | 5.53 | 3.8 | 3.8 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 314682 | 1158 | 209.4033 | 100% | 0% | 100% | 100% | 100% | 0% | 11345238 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 118 | 21182466 | 5032 | 120.768 | 5.032 | 4.2 | 4.2 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 315714 | 1032 | 205.0874 | 0% | 0% | 100% | 100% | 100% | 30% | 11345514 | 276 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 110 | 21187296 | 4830 | 115.92 | 4.83 | 5 | 5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 316706 | 992 | 205.383 | 0% | 0% | 100% | 100% | 100% | 30% | 11346308 | 794 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130854 | 130.854 | 130.854 | [12 empty] | 26534 | 26534 | 202.7756 | [6 empty] | 3970 | 3970 | 1.1967 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:46 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26734 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21187296 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 316706 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11346308 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 129 | 104 | 21191864 | 4568 | 109.632 | 4.568 | 5.9 | 5.9 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 317638 | 932 | 204.028 | 0% | 0% | 100% | 100% | 100% | 60% | 11346824 | 516 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 125 | 106 | 21196426 | 4562 | 109.488 | 4.562 | 6.9 | 6.9 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 318574 | 936 | 205.1732 | 0% | 0% | 100% | 100% | 100% | 60% | 11347642 | 818 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 118 | 106 | 21200988 | 4562 | 109.488 | 4.562 | 8 | 8 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 319516 | 942 | 206.4884 | 0% | 0% | 100% | 100% | 100% | 60% | 11348624 | 982 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 | 113 | 21205558 | 4570 | 109.68 | 4.57 | 8.4 | 8.4 | 3B | 0 | 0 | 1116 | 1185 | 1106 | N/A | N/A | N/A | N/A | 320462 | 946 | 207.0022 | 0% | 0% | 100% | 100% | 100% | 60% | 11349347 | 723 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 123 | 21209838 | 4280 | 102.72 | 4.28 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 321444 | 982 | 229.4393 | 0% | 0% | 100% | 100% | 100% | 60% | 11349559 | 212 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 134 | 21215588 | 5750 | 138 | 5.75 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 322564 | 1120 | 194.7826 | 0% | 0% | 100% | 100% | 100% | 0% | 11349559 | 0 | 1.14 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 141 | 21221346 | 5758 | 138.192 | 5.758 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 323712 | 1148 | 199.3748 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 139 | 21227512 | 6166 | 147.984 | 6.166 | 8.6 | 8.6 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 324922 | 1210 | 196.2374 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 140 | 21233614 | 6102 | 146.448 | 6.102 | 8.1 | 8.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 326120 | 1198 | 196.3291 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 142 | 21239726 | 6112 | 146.688 | 6.112 | 7.6 | 7.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 327328 | 1208 | 197.644 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 | 1.2
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 137 | 21245434 | 5708 | 136.992 | 5.708 | 7.2 | 7.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 328440 | 1112 | 194.8143 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 21251678 | 6244 | 149.856 | 6.244 | 6.7 | 6.7 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 329694 | 1254 | 200.8328 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 135 | 21257488 | 5810 | 139.44 | 5.81 | 6.3 | 6.3 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 330850 | 1156 | 198.9673 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 135 | 21263335 | 5847 | 140.328 | 5.847 | 6 | 6 | 3B+1S | 0 | 1017 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 332041 | 1191 | 203.6942 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 132 | 21269210 | 5875 | 141 | 5.875 | 5.6 | 5.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 333215 | 1174 | 199.8298 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 21274897 | 5687 | 136.488 | 5.687 | 5.4 | 5.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 334380 | 1165 | 204.8532 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 21280640 | 5743 | 137.832 | 5.743 | 5.1 | 5.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 335549 | 1169 | 203.5522 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 135 | 21286480 | 5840 | 140.16 | 5.84 | 4.8 | 4.8 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 336715 | 1166 | 199.6575 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 132 | 21292201 | 5721 | 137.304 | 5.721 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 337881 | 1166 | 203.8105 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 130 | 21297957 | 5756 | 138.144 | 5.756 | 4.3 | 4.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 339038 | 1157 | 201.0076 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 128 | 21303489 | 5532 | 132.768 | 5.532 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 340198 | 1160 | 209.6891 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 126 | 21309146 | 5657 | 135.768 | 5.657 | 4.1 | 4.1 | 3B+1S | 0 | 1004 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 341342 | 1144 | 202.2273 | 0% | 100% | 100% | 100% | 100% | 0% | 11349559 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 116 | 21314406 | 5260 | 126.24 | 5.26 | 4.1 | 4.1 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 342442 | 1100 | 209.1255 | 0% | 0% | 100% | 100% | 100% | 30% | 11349609 | 50 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 118 | 21319142 | 4736 | 113.664 | 4.736 | 4.4 | 4.4 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 343440 | 998 | 210.7264 | 0% | 0% | 100% | 100% | 100% | 30% | 11349858 | 249 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131846 | 131.846 | 131.846 | [12 empty] | 26734 | 26734 | 202.7669 | [6 empty] | 3550 | 3550 | 1.1683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[13 empty] | 10pm - 6am | FIDEL RAMOS/JEFREY LAMAYO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26664 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21319142 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 343440 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11349858 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 105 | 21323712 | 4570 | 109.68 | 4.57 | 5.2 | 5.2 | 3B | 0 | 0 | 1115 | 1185 | 1115 | N/A | N/A | N/A | N/A | 344366 | 926 | 202.6258 | 0% | 0% | 100% | 100% | 100% | 60% | 11350680 | 822 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 126 | 106 | 21328336 | 4624 | 110.976 | 4.624 | 6.2 | 6.2 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 345308 | 942 | 203.7197 | 0% | 0% | 100% | 100% | 100% | 60% | 11351472 | 792 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 131 | 105 | 21332964 | 4628 | 111.072 | 4.628 | 7.2 | 7.2 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 346254 | 946 | 204.408 | 0% | 0% | 100% | 100% | 100% | 60% | 11352255 | 783 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 124 | 108 | 21337248 | 4284 | 102.816 | 4.284 | 8.9 | 8.9 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 347252 | 998 | 232.9599 | 0% | 0% | 100% | 100% | 100% | 60% | 11352525 | 270 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 117 | 21341532 | 4284 | 102.816 | 4.284 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 348244 | 992 | 231.5593 | 0% | 0% | 100% | 100% | 100% | 60% | 11352578 | 53 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 130 | 128 | 21346788 | 5256 | 126.144 | 5.256 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 349214 | 970 | 184.551 | 0% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 133 | 21352542 | 5754 | 138.096 | 5.754 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 350260 | 1046 | 181.7866 | 0% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 21358446 | 5904 | 141.696 | 5.904 | 9.3 | 9.3 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 351424 | 1164 | 197.1545 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 139 | 21364582 | 6136 | 147.264 | 6.136 | 8.7 | 8.7 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 352632 | 1208 | 196.8709 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 21370986 | 6404 | 153.696 | 6.404 | 8.1 | 8.1 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 353898 | 1266 | 197.6889 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 | 1.18
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 144 | 21377062 | 6076 | 145.824 | 6.076 | 7.4 | 7.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 355074 | 1176 | 193.5484 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 128 | 21383462 | 6400 | 153.6 | 6.4 | 6.6 | 6.6 | 3B+1S | 1118 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 356330 | 1256 | 196.25 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 133 | 21389522 | 6060 | 145.44 | 6.06 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 357512 | 1182 | 195.0495 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 139 | 21395097 | 5575 | 133.8 | 5.575 | 5.6 | 5.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 358624 | 1112 | 199.4619 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 137 | 21400717 | 5620 | 134.88 | 5.62 | 5.2 | 5.2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 359790 | 1166 | 207.4733 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 141 | 21406593 | 5876 | 141.024 | 5.876 | 4.8 | 4.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 360987 | 1197 | 203.71 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 21412608 | 6015 | 144.36 | 6.015 | 4.5 | 4.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 362163 | 1176 | 195.5112 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 136 | 21418342 | 5734 | 137.616 | 5.734 | 4.1 | 4.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 363334 | 1171 | 204.2204 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 134 | 21424043 | 5701 | 136.824 | 5.701 | 3.7 | 3.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 364515 | 1181 | 207.1566 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 134 | 21429651 | 5608 | 134.592 | 5.608 | 3.4 | 3.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 365679 | 1164 | 207.5606 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 131 | 21435233 | 5582 | 133.968 | 5.582 | 3.2 | 3.2 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 366845 | 1166 | 208.8857 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 126 | 21441222 | 5989 | 143.736 | 5.989 | 3.1 | 3.1 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 368146 | 1301 | 217.2316 | 100% | 0% | 100% | 100% | 100% | 0% | 11352578 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 136 | 116 | 21445979 | 4757 | 114.168 | 4.757 | 3.3 | 3.3 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 369111 | 965 | 202.8589 | 0% | 0% | 100% | 100% | 100% | 30% | 11352861 | 283 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 112 | 21450667 | 4688 | 112.512 | 4.688 | 4.2 | 4.2 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 370104 | 993 | 211.8174 | 0% | 0% | 100% | 100% | 100% | 30% | 11353599 | 738 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131525 | 131.525 | 131.525 | [12 empty] | 26664 | 26664 | 202.7295 | [6 empty] | 3741 | 3741 | 1.1717 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 23706 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21450667 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 370104 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11353599 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 62 | 43.662 | Automatic - Pressure Setting | 38.7324 | 40.1408 | 44.3662 | 14 | A.ONG | 11.4 | 128 | 107 | 21455208 | 4541 | 108.984 | 4.541 | 4.8 | 4.8 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 371056 | 952 | 209.6455 | 0% | 0% | 100% | 100% | 100% | 60% | 11354299 | 700 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 130 | 106 | 21459756 | 4548 | 109.152 | 4.548 | 5.8 | 5.8 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 372006 | 950 | 208.883 | 0% | 0% | 100% | 100% | 100% | 60% | 11355099 | 800 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 141 | 106 | 21464305 | 4549 | 109.176 | 4.549 | 7.7 | 7.7 | 3B | 0 | 0 | 1117 | 1185 | 1116 | N/A | N/A | N/A | N/A | 372954 | 948 | 208.3974 | 0% | 0% | 100% | 100% | 100% | 60% | 11356006 | 907 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 6 | 4.2254 | 65 | 45.7746 | Automatic - Pressure Setting | 40.8451 | 42.2535 | 46.4789 | 14 | A.ONG | 12.8 | 116 | 110 | 21468565 | 4260 | 102.24 | 4.26 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1077 | N/A | N/A | N/A | N/A | 373914 | 960 | 225.3521 | 0% | 0% | 100% | 100% | 100% | 60% | 11356347 | 341 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 116 | 107 | 21472829 | 4264 | 102.336 | 4.264 | 9.5 | 9.5 | 3B | 0 | 0 | 1077 | 1185 | 1077 | N/A | N/A | N/A | N/A | 374868 | 954 | 223.7336 | 0% | 0% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 127 | 121 | 21477986 | 5157 | 123.768 | 5.157 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 375788 | 920 | 178.3983 | 0% | 0% | 100% | 100% | 100% | 0% | 11356347 | 0 | 1.06 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 124 | 21483434 | 5448 | 130.752 | 5.448 | 9.5 | 9.5 | 3B | 0 | 0 | 1056 | 1185 | 1056 | N/A | N/A | N/A | N/A | 376730 | 942 | 172.9075 | 0% | 0% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 137 | 21488888 | 5454 | 130.896 | 5.454 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 377666 | 936 | 171.6172 | 0% | 0% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 140 | 138 | 21495118 | 6230 | 149.52 | 6.23 | 9.3 | 9.3 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 378888 | 1222 | 196.1477 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 155 | 21501422 | 6304 | 151.296 | 6.304 | 8.8 | 8.8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 380134 | 1246 | 197.6523 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 | 1.2
58:00 | 11:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 147 | 21507666 | 6244 | 149.856 | 6.244 | 8.4 | 8.4 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 381338 | 1204 | 192.8251 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 146 | 21513304 | 5638 | 135.312 | 5.638 | 8 | 8 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 382460 | 1122 | 199.0067 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 142 | 21519304 | 6000 | 144 | 6 | 7.5 | 7.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 383658 | 1198 | 199.6667 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 138 | 21525163 | 5859 | 140.616 | 5.859 | 7 | 7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 384854 | 1196 | 204.1304 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 142 | 21530886 | 5723 | 137.352 | 5.723 | 6.6 | 6.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 386027 | 1173 | 204.9624 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 131 | 21536829 | 5943 | 142.632 | 5.943 | 6.2 | 6.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 387207 | 1180 | 198.5529 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 134 | 21542660 | 5831 | 139.944 | 5.831 | 5.7 | 5.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 388364 | 1157 | 198.4222 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 129 | 21548468 | 5808 | 139.392 | 5.808 | 5.4 | 5.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 389532 | 1168 | 201.1019 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 132 | 21554240 | 5772 | 138.528 | 5.772 | 5 | 5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 390694 | 1162 | 201.3167 | 0% | 100% | 100% | 100% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.6 | 102 | 105 | 21559439 | 5199 | 124.776 | 5.199 | 4.4 | 4.4 | 2B+1S | 0 | 1007 | 1077 | 0 | 1077 | N/A | N/A | N/A | N/A | 391481 | 787 | 151.3753 | 0% | 100% | 100% | 0% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 8 | 5.6338 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.1 | 101 | 105 | 21564283 | 4844 | 116.256 | 4.844 | 3.6 | 3.6 | 2B+1S | 0 | 1007 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 392156 | 675 | 139.3476 | 0% | 100% | 100% | 0% | 100% | 0% | 11356347 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 95 | 106 | 21569594 | 5311 | 127.464 | 5.311 | 3 | 3 | 2B | 0 | 1007 | 1017 | 0 | 1017 | N/A | N/A | N/A | N/A | 392828 | 672 | 126.5298 | 0% | 100% | 100% | 0% | 100% | 0% | 11356347 | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 119 | 109 | 21573372 | 3778 | 90.672 | 3.778 | 3.7 | 3.7 | 2B | 0 | 0 | 1047 | 0 | 1048 | N/A | N/A | N/A | N/A | 393368 | 540 | 142.9328 | 0% | 0% | 100% | 0% | 100% | 30% | 11357120 | 773 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 154 | 80 | 21577006 | 3634 | 87.216 | 3.634 | 6.2 | 6.2 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 393810 | 442 | 121.6291 | 0% | 0% | 100% | 0% | 100% | 30% | 11359586 | 2466 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 126339 | 126.339 | 126.339 | [12 empty] | 23706 | 23706 | 187.638 | [6 empty] | 5987 | 5987 | 1.1433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
AS PER ADVISE SIR ALVIN CRUZ,
VILLAMOR TARGET FLOW TONIGHT ONLY:
7PM -11PM 105MLD
11PM - 4AM 80MLD
4AM ON WARDS NORMAL OPERATION.
BP2- STOP @ 7;00 PM DUE TO MEET 105 MLD
DISCHARGE PRESSURE 67 PSI , 105 MLD @ 7:00P TO 9:00PM
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS / JEFFREY LAMAYO
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24738 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21577006 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 393810 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11359586 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 11 | 7.7465 | 62 | 43.662 | Automatic - Pressure Setting | 38.7324 | 40.1408 | 44.3662 | 14 | A.ONG | 11.4 | 135 | 80 | 21580606 | 3600 | 86.4 | 3.6 | 8.4 | 8.4 | 2B | 0 | 0 | 987 | 0 | 987 | N/A | N/A | N/A | N/A | 394340 | 530 | 147.2222 | 0% | 0% | 100% | 0% | 100% | 60% | 11361674 | 2088 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 14 | 9.8592 | 70 | 49.2958 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 94 | 80 | 21584366 | 3760 | 90.24 | 3.76 | 9.5 | 9.5 | 2B | 0 | 0 | 966 | 0 | 966 | N/A | N/A | N/A | N/A | 394788 | 448 | 119.1489 | 0% | 0% | 100% | 0% | 100% | 60% | 11362673 | 999 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 16 | 11.2676 | 66 | 46.4789 | Automatic - Pressure Setting | 41.5493 | 42.9577 | 47.1831 | 14 | A.ONG | 11.2 | 92 | 82 | 21588424 | 4058 | 97.392 | 4.058 | 9.5 | 9.5 | 2B | 0 | 0 | 966 | 0 | 966 | N/A | N/A | N/A | N/A | 395252 | 464 | 114.342 | 0% | 0% | 100% | 0% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 18 | 12.6761 | 65 | 45.7746 | Automatic - Pressure Setting | 40.8451 | 42.2535 | 46.4789 | 14 | A.ONG | 12.8 | 90 | 80 | 21592502 | 4078 | 97.872 | 4.078 | 9.5 | 9.5 | 2B | 0 | 0 | 967 | 0 | 967 | N/A | N/A | N/A | N/A | 395720 | 468 | 114.7621 | 0% | 0% | 100% | 0% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
52:00 | 5:00 | 14 | 9.8592 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 123 | 21597482 | 4980 | 119.52 | 4.98 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 396670 | 950 | 190.7631 | 0% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL LABIAN
53:00 | 6:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 135 | 21603191 | 5709 | 137.016 | 5.709 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1187 | N/A | N/A | N/A | N/A | 397757 | 1087 | 190.4011 | 0% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 | 1.1 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 143 | 21609375 | 6184 | 148.416 | 6.184 | 9.3 | 9.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 398927 | 1170 | 189.1979 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 151 | 21615327 | 5952 | 142.848 | 5.952 | 8.9 | 8.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 400102 | 1175 | 197.4126 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 145 | 21621353 | 6026 | 144.624 | 6.026 | 8.4 | 8.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 401281 | 1179 | 195.6522 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 142 | 21626796 | 5443 | 130.632 | 5.443 | 7.9 | 7.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 402495 | 1214 | 223.0388 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 | 1.13
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 139 | 21632992 | 6196 | 148.704 | 6.196 | 7.4 | 7.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 403689 | 1194 | 192.705 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 139 | 21639278 | 6286 | 150.864 | 6.286 | 6.8 | 6.8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 404877 | 1188 | 188.9914 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 134 | 21646188 | 6910 | 165.84 | 6.91 | 6.3 | 6.3 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 406025 | 1148 | 166.136 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 132 | 21652511 | 6323 | 151.752 | 6.323 | 5.9 | 5.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 407232 | 1207 | 190.8904 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 136 | 21658659 | 6148 | 147.552 | 6.148 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 408421 | 1189 | 193.3962 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 130 | 21664531 | 5872 | 140.928 | 5.872 | 5.5 | 5.5 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 409592 | 1171 | 199.421 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 21670453 | 5922 | 142.128 | 5.922 | 5.2 | 5.2 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 410755 | 1163 | 196.3864 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 134 | 21676531 | 6078 | 145.872 | 6.078 | 5 | 5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 411918 | 1163 | 191.3458 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 130 | 21682366 | 5835 | 140.04 | 5.835 | 4.7 | 4.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 413088 | 1170 | 200.5141 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 130 | 21688140 | 5774 | 138.576 | 5.774 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 414223 | 1135 | 196.5708 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 129 | 21693812 | 5672 | 136.128 | 5.672 | 4.2 | 4.2 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 415379 | 1156 | 203.8082 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 | 125 | 21698935 | 5123 | 122.952 | 5.123 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 416433 | 1054 | 205.7388 | 100% | 0% | 100% | 100% | 100% | 0% | 11362673 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 118 | 21704244 | 5309 | 127.416 | 5.309 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 417513 | 1080 | 203.4281 | 0% | 0% | 100% | 100% | 100% | 25% | 11362708 | 35 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 115 | 21709408 | 5164 | 123.936 | 5.164 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 418548 | 1035 | 200.426 | 0% | 0% | 100% | 100% | 100% | 25% | 11363263 | 555 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132402 | 132.402 | 132.402 | [12 empty] | 24738 | 24738 | 186.8401 | [6 empty] | 3677 | 3677 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
AS PER ADVISE SIR ALVIN CRUZ,
VILLAMOR TARGET FLOW TONIGHT ONLY:
7PM -11PM 105MLD
11PM - 4AM 80MLD
4AM ON WARDS NORMAL OPERATION.
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
XCV2- CLOSED @ 1:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 5:01 AM AS PER SCHEDULE
BP1- STARTED @ 4:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)

## OCT 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY / JEFFREY LAMAYO
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-10-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26758 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21709408 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 418548 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11363263 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 104 | 21713790 | 4382 | 105.168 | 4.382 | 6.1 | 6.1 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 419424 | 876 | 199.9087 | 0% | 0% | 100% | 100% | 100% | 70% | 11364013 | 750 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 106 | 21718200 | 4410 | 105.84 | 4.41 | 7 | 7 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 420319 | 895 | 202.9478 | 0% | 0% | 100% | 100% | 100% | 70% | 11364773 | 760 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 131 | 104 | 21722605 | 4405 | 105.72 | 4.405 | 8.5 | 8.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 421221 | 902 | 204.7673 | 0% | 0% | 100% | 100% | 100% | 70% | 11365558 | 785 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 110 | 21727130 | 4525 | 108.6 | 4.525 | 9.2 | 9.2 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 422156 | 935 | 206.6298 | 0% | 0% | 100% | 100% | 100% | 70% | 11366161 | 603 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 119 | 21731762 | 4632 | 111.168 | 4.632 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 423181 | 1025 | 221.2867 | 0% | 0% | 100% | 100% | 100% | 70% | 11366461 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 132 | 21737909 | 6147 | 147.528 | 6.147 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 424339 | 1158 | 188.3846 | 0% | 0% | 100% | 100% | 100% | 0% | 11366461 | 0 | 1.07 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 141 | 21744241 | 6332 | 151.968 | 6.332 | 9.3 | 9.3 | 3B+1S | 0 | 995 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 425559 | 1220 | 192.6721 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 147 | 21750470 | 6229 | 149.496 | 6.229 | 9.1 | 9.1 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 426724 | 1165 | 187.0284 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 145 | 21757003 | 6533 | 156.792 | 6.533 | 8.5 | 8.5 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 427936 | 1212 | 185.5197 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 134 | 21763207 | 6204 | 148.896 | 6.204 | 7.9 | 7.9 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 429144 | 1208 | 194.7131 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 | 1.1
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 134 | 21769472 | 6265 | 150.36 | 6.265 | 7.3 | 7.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 430332 | 1188 | 189.6249 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 138 | 21775739 | 6267 | 150.408 | 6.267 | 6.7 | 6.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 431521 | 1189 | 189.724 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 21781846 | 6107 | 146.568 | 6.107 | 6.4 | 6.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 432688 | 1167 | 191.0922 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 130 | 21788014 | 6168 | 148.032 | 6.168 | 6 | 6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 433875 | 1187 | 192.4449 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 132 | 21793910 | 5896 | 141.504 | 5.896 | 5.7 | 5.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 435038 | 1163 | 197.2524 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 21799936 | 6026 | 144.624 | 6.026 | 5.5 | 5.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 436204 | 1166 | 193.4949 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 21805877 | 5941 | 142.584 | 5.941 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 437377 | 1173 | 197.4415 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 134 | 21811767 | 5890 | 141.36 | 5.89 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 438544 | 1167 | 198.1324 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 133 | 21817940 | 6173 | 148.152 | 6.173 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 439715 | 1171 | 189.6971 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 125 | 21823903 | 5963 | 143.112 | 5.963 | 4.1 | 4.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 440885 | 1170 | 196.21 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 126 | 128 | 21829780 | 5877 | 141.048 | 5.877 | 3.7 | 3.7 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 442042 | 1157 | 196.8692 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 123 | 123 | 21835812 | 6032 | 144.768 | 6.032 | 3.4 | 3.4 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 443240 | 1198 | 198.6074 | 0% | 100% | 100% | 100% | 100% | 0% | 11366461 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 117 | 21840882 | 5070 | 121.68 | 5.07 | 3.4 | 3.4 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 444290 | 1050 | 207.1006 | 0% | 0% | 100% | 100% | 100% | 30% | 11366512 | 51 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 110 | 21845838 | 4956 | 118.944 | 4.956 | 3.8 | 3.8 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 445306 | 1016 | 205.004 | 0% | 0% | 100% | 100% | 100% | 30% | 11366991 | 479 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136430 | 136.43 | 136.43 | [12 empty] | 26758 | 26758 | 196.1299 | [6 empty] | 3728 | 3728 | 1.1117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 19
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/JEFFREY LAMAYO
[14 empty] | 10pm - 6am | FIDEL RAMOS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27084 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21845838 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 445306 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11366991 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 128 | 106 | 21850664 | 4826 | 115.824 | 4.826 | 4.5 | 4.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 446308 | 1002 | 207.6254 | 0% | 0% | 100% | 100% | 100% | 60% | 11367824 | 833 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 107 | 21855482 | 4818 | 115.632 | 4.818 | 5.8 | 5.8 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 447306 | 998 | 207.1399 | 0% | 0% | 100% | 100% | 100% | 60% | 11368646 | 822 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 106 | 21859644 | 4162 | 99.888 | 4.162 | 6.9 | 6.9 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 448190 | 884 | 212.3979 | 0% | 0% | 100% | 100% | 100% | 60% | 11369094 | 448 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 110 | 21864276 | 4632 | 111.168 | 4.632 | 7.8 | 7.8 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 449266 | 1076 | 232.2971 | 0% | 0% | 100% | 100% | 100% | 60% | 11369572 | 478 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 121 | 21868898 | 4622 | 110.928 | 4.622 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 450340 | 1074 | 232.3669 | 0% | 0% | 100% | 100% | 100% | 60% | 11369823 | 251 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 128 | 21873424 | 4526 | 108.624 | 4.526 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 451204 | 864 | 190.897 | 0% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 | 1.16 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 149 | 21879868 | 6444 | 154.656 | 6.444 | 9.2 | 9.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 452470 | 1266 | 196.4618 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 142 | 21885762 | 5894 | 141.456 | 5.894 | 8.6 | 8.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 453634 | 1164 | 197.489 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 154 | 148 | 21892214 | 6452 | 154.848 | 6.452 | 8 | 8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 454906 | 1272 | 197.1482 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 141 | 21898424 | 6210 | 149.04 | 6.21 | 7.6 | 7.6 | 3B+1S | 1177 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 456106 | 1200 | 193.2367 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 | 1.12
| 58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 142 | 21904636 | 6212 | 149.088 | 6.212 | 7.1 | 7.1 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 457318 | 1212 | 195.1062 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 137 | 21910758 | 6122 | 146.928 | 6.122 | 6.5 | 6.5 | 3B+1S | 1076 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 458528 | 1210 | 197.6478 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 138 | 21917286 | 6528 | 156.672 | 6.528 | 5.8 | 5.8 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 459720 | 1192 | 182.598 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 21922140 | 4854 | 116.496 | 4.854 | 5.5 | 5.5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 460846 | 1126 | 231.9736 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 136 | 21927918 | 5778 | 138.672 | 5.778 | 5.2 | 5.2 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 462012 | 1166 | 201.7999 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 21933822 | 5904 | 141.696 | 5.904 | 4.9 | 4.9 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 463207 | 1195 | 202.4051 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 21939519 | 5697 | 136.728 | 5.697 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 464385 | 1178 | 206.7755 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 136 | 21945260 | 5741 | 137.784 | 5.741 | 4 | 4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 465576 | 1191 | 207.4551 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 138 | 21950912 | 5652 | 135.648 | 5.652 | 3.5 | 3.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 466754 | 1178 | 208.4218 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 132 | 21956489 | 5577 | 133.848 | 5.577 | 3.2 | 3.2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 467911 | 1157 | 207.4592 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 132 | 21962244 | 5755 | 138.12 | 5.755 | 2.8 | 2.8 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 469110 | 1199 | 208.3406 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 125 | 21968242 | 5998 | 143.952 | 5.998 | 2.5 | 2.5 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 470338 | 1228 | 204.7349 | 100% | 0% | 100% | 100% | 100% | 0% | 11369823 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 132 | 121 | 21973064 | 4822 | 115.728 | 4.822 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 471338 | 1000 | 207.3828 | 0% | 0% | 100% | 100% | 100% | 30% | 11369984 | 161 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 108 | 21978118 | 5054 | 121.296 | 5.054 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 472390 | 1052 | 208.152 | 0% | 0% | 100% | 100% | 100% | 30% | 11370775 | 791 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 132280 | 132.28 | 132.28 | [12 empty] | 27084 | 27084 | 204.7475 | [6 empty] | 3784 | 3784 | 1.1517 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 20
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/JEFFREY LAMAYO
[14 empty] | 10pm - 6am | FIDEL RAMOS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26820 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 21978118 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 472390 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11370775 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 130 | 112 | 21983182 | 5064 | 121.536 | 5.064 | 4.8 | 4.8 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 473432 | 1042 | 205.7662 | 0% | 0% | 100% | 100% | 100% | 60% | 11371722 | 947 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 126 | 110 | 21988244 | 5062 | 121.488 | 5.062 | 5.6 | 5.6 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 474470 | 1038 | 205.0573 | 0% | 0% | 100% | 100% | 100% | 60% | 11372624 | 902 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 103 | 21993308 | 5064 | 121.536 | 5.064 | 7.4 | 7.4 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 475502 | 1032 | 203.7915 | 0% | 0% | 100% | 100% | 100% | 60% | 11373412 | 788 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 110 | 21996848 | 3540 | 84.96 | 3.54 | 8.2 | 8.2 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 476328 | 826 | 233.3333 | 0% | 0% | 100% | 100% | 100% | 60% | 11374022 | 610 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 118 | 22000382 | 3534 | 84.816 | 3.534 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1106 | N/A | N/A | N/A | N/A | 477162 | 834 | 235.9932 | 0% | 0% | 100% | 100% | 100% | 60% | 11374095 | 73 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 138 | 22006258 | 5876 | 141.024 | 5.876 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 478228 | 1066 | 181.4159 | 0% | 0% | 100% | 100% | 100% | 0% | 11374095 | 0 | 1.12 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 141 | 22011502 | 5244 | 125.856 | 5.244 | 9.3 | 9.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 479251 | 1023 | 195.0801 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 22017765 | 6263 | 150.312 | 6.263 | 8.8 | 8.8 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 480461 | 1210 | 193.1981 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 148 | 22023905 | 6140 | 147.36 | 6.14 | 8.1 | 8.1 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 481672 | 1211 | 197.2313 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 150 | 22030260 | 6355 | 152.52 | 6.355 | 7.4 | 7.4 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 482895 | 1223 | 192.4469 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 | 1.16
| 58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 140 | 22036403 | 6143 | 147.432 | 6.143 | 6.8 | 6.8 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 484120 | 1225 | 199.414 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 143 | 22042515 | 6112 | 146.688 | 6.112 | 6.1 | 6.1 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 485327 | 1207 | 197.4804 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 132 | 22048569 | 6054 | 145.296 | 6.054 | 5.6 | 5.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 486533 | 1206 | 199.2071 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 131 | 22055019 | 6450 | 154.8 | 6.45 | 5.3 | 5.3 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 487974 | 1441 | 223.4109 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 128 | 22060679 | 5660 | 135.84 | 5.66 | 4.9 | 4.9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 488979 | 1005 | 177.5618 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 22066716 | 6037 | 144.888 | 6.037 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 490137 | 1158 | 191.8171 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 22072499 | 5783 | 138.792 | 5.783 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 491298 | 1161 | 200.7609 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 22078579 | 6080 | 145.92 | 6.08 | 3.9 | 3.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 492483 | 1185 | 194.9013 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 135 | 22084438 | 5859 | 140.616 | 5.859 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 493641 | 1158 | 197.6446 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 157 | 22090381 | 5943 | 142.632 | 5.943 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 494823 | 1182 | 198.8894 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 132 | 22096011 | 5630 | 135.12 | 5.63 | 3.2 | 3.2 | 3B+1S | 0 | 1013 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 495968 | 1145 | 203.3748 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 132 | 22101776 | 5765 | 138.36 | 5.765 | 3.1 | 3.1 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 497146 | 1178 | 204.3365 | 0% | 100% | 100% | 100% | 100% | 0% | 11374095 | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 117 | 22107108 | 5332 | 127.968 | 5.332 | 3.4 | 3.4 | 3B | 0 | 0 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 498222 | 1076 | 201.8005 | 0% | 0% | 100% | 100% | 100% | 30% | 11374354 | 259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 115 | 22111674 | 4566 | 109.584 | 4.566 | 4.2 | 4.2 | 3B | 0 | 0 | 1177 | 1185 | 1176 | N/A | N/A | N/A | N/A | 499210 | 988 | 216.382 | 0% | 0% | 100% | 100% | 1000% | 30% | 11375012 | 658 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 133556 | 133.556 | 133.556 | [12 empty] | 26820 | 26820 | 200.8146 | [6 empty] | 4237 | 4237 | 1.1667 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:46 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:24 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 21
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | FIDEL RAMOS / JEFFREY LAMAYO
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26790 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22111674 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 499210 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11375012 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 142 | 104 | 22116302 | 4628 | 111.072 | 4.628 | 5.8 | 5.8 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 500156 | 946 | 204.408 | 0% | 0% | 100% | 100% | 100% | 60% | 11375546 | 534 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 106 | 22120930 | 4628 | 111.072 | 4.628 | 6.4 | 6.4 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 501104 | 948 | 204.8401 | 0% | 0% | 100% | 100% | 100% | 60% | 11376146 | 600 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 110 | 22125556 | 4626 | 111.024 | 4.626 | 7.3 | 7.3 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 502052 | 948 | 204.9287 | 0% | 0% | 100% | 100% | 100% | 60% | 11377130 | 984 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 118 | 114 | 22130062 | 4506 | 108.144 | 4.506 | 8.1 | 8.1 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 503066 | 1014 | 225.0333 | 0% | 0% | 100% | 100% | 100% | 60% | 11377982 | 852 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 119 | 22134578 | 4516 | 108.384 | 4.516 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 504092 | 1026 | 227.1922 | 0% | 0% | 100% | 100% | 100% | 60% | 11378030 | 48 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 152 | 22139904 | 5326 | 127.824 | 5.326 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 505104 | 1012 | 190.0113 | 0% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 | 1.1 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 141 | 22146168 | 6264 | 150.336 | 6.264 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 506310 | 1206 | 192.5287 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 140 | 22152224 | 6056 | 145.344 | 6.056 | 8.6 | 8.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 507464 | 1154 | 190.5548 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 142 | 22158696 | 6472 | 155.328 | 6.472 | 7.9 | 7.9 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 508704 | 1240 | 191.5946 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 22164886 | 6190 | 148.56 | 6.19 | 7.4 | 7.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 509860 | 1156 | 186.7528 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 | 1.16
| 58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 22170988 | 6102 | 146.448 | 6.102 | 6.8 | 6.8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 511054 | 1194 | 195.6735 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 136 | 22177286 | 6298 | 151.152 | 6.298 | 6.3 | 6.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 512256 | 1202 | 190.8542 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 138 | 22183648 | 6362 | 152.688 | 6.362 | 5.9 | 5.9 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 513498 | 1242 | 195.2216 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 134 | 22189595 | 5947 | 142.728 | 5.947 | 5.5 | 5.5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 514664 | 1166 | 196.0652 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 136 | 22195670 | 6075 | 145.8 | 6.075 | 5.1 | 5.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 515837 | 1173 | 193.0864 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 140 | 22201743 | 6073 | 145.752 | 6.073 | 4.8 | 4.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 517019 | 1182 | 194.632 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 136 | 22207454 | 5711 | 137.064 | 5.711 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 518175 | 1156 | 202.4164 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 131 | 22213242 | 5788 | 138.912 | 5.788 | 4.3 | 4.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 519340 | 1165 | 201.2785 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 128 | 22219012 | 5770 | 138.48 | 5.77 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 520507 | 1167 | 202.253 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 129 | 22224630 | 5618 | 134.832 | 5.618 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 521653 | 1146 | 203.9872 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 131 | 22230153 | 5523 | 132.552 | 5.523 | 3.6 | 3.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 522782 | 1129 | 204.4179 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 132 | 22235637 | 5484 | 131.616 | 5.484 | 3.4 | 3.4 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 523922 | 1140 | 207.8775 | 100% | 0% | 100% | 100% | 100% | 0% | 11378030 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 120 | 22240796 | 5159 | 123.816 | 5.159 | 3.6 | 3.6 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 524984 | 1062 | 205.8538 | 0% | 0% | 100% | 100% | 100% | 30% | 11378213 | 183 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 117 | 22245605 | 4809 | 115.416 | 4.809 | 4.3 | 4.3 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 526000 | 1016 | 211.2705 | 0% | 0% | 100% | 100% | 100% | 30% | 11378819 | 606 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 133931 | 133.931 | 133.931 | [12 empty] | 26790 | 26790 | 200.0284 | [6 empty] | 3807 | 3807 | 1.1783 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 22
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
| WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
[14 empty] | 10pm - 6am | FIDEL RAMOS / JEFFREY LAMAYO
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26907 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22245605 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 526000 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11378819 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 134 | 114 | 22250349 | 4744 | 113.856 | 4.744 | 5.1 | 5.1 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 526985 | 985 | 207.6307 | 0% | 0% | 100% | 100% | 100% | 60% | 11379578 | 759 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 106 | 22254796 | 4447 | 106.728 | 4.447 | 6.2 | 6.2 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 527922 | 937 | 210.7038 | 0% | 0% | 100% | 100% | 100% | 60% | 11380468 | 890 | 1.7 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 104 | 22259244 | 4448 | 106.752 | 4.448 | 7.2 | 7.2 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 528860 | 938 | 210.8813 | 0% | 0% | 100% | 100% | 100% | 60% | 11381308 | 840 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 118 | 108 | 22263516 | 4272 | 102.528 | 4.272 | 9.1 | 9.1 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 529827 | 967 | 226.3577 | 0% | 0% | 100% | 100% | 100% | 60% | 11381608 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 116 | 112 | 22267792 | 4276 | 102.624 | 4.276 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 1096 | N/A | N/A | N/A | N/A | 530792 | 965 | 225.6782 | 0% | 0% | 100% | 100% | 100% | 60% | 11381632 | 24 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 126 | 22273282 | 5490 | 131.76 | 5.49 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 531778 | 986 | 179.5993 | 0% | 0% | 100% | 100% | 100% | 0% | 11381632 | 0 | 1.12 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 144 | 22279506 | 6224 | 149.376 | 6.224 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 532998 | 1220 | 196.0154 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 146 | 22285926 | 6420 | 154.08 | 6.42 | 8.5 | 8.5 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 534258 | 1260 | 196.2617 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 143 | 22292158 | 6232 | 149.568 | 6.232 | 7.9 | 7.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 535426 | 1168 | 187.4198 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 139 | 22298382 | 6224 | 149.376 | 6.224 | 7.3 | 7.3 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 536630 | 1204 | 193.4447 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 | 1.18
| 58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 145 | 22304508 | 6126 | 147.024 | 6.126 | 6.6 | 6.6 | 3B+1S | 0 | 1149 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 537880 | 1250 | 204.0483 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 147 | 22310756 | 6248 | 149.952 | 6.248 | 5.6 | 5.6 | 3B+1S | 0 | 1138 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 539114 | 1234 | 197.5032 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 133 | 136 | 22316814 | 6058 | 145.392 | 6.058 | 4.8 | 4.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 540322 | 1208 | 199.4057 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 135 | 22322519 | 5705 | 136.92 | 5.705 | 4.5 | 4.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 541427 | 1105 | 193.6897 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 139 | 22328324 | 5805 | 139.32 | 5.805 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 542593 | 1166 | 200.8613 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 131 | 22334264 | 5940 | 142.56 | 5.94 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 543773 | 1180 | 198.6532 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 134 | 22340158 | 5894 | 141.456 | 5.894 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 544927 | 1154 | 195.7923 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 135 | 22346241 | 6083 | 145.992 | 6.083 | 3.3 | 3.3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 546093 | 1166 | 191.6817 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 140 | 22351860 | 5619 | 134.856 | 5.619 | 3 | 3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 547254 | 1161 | 206.6204 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 132 | 22357555 | 5695 | 136.68 | 5.695 | 2.9 | 2.9 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 548415 | 1161 | 203.863 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 137 | 22363259 | 5704 | 136.896 | 5.704 | 2.6 | 2.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 549580 | 1165 | 204.2426 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 127 | 22368981 | 5722 | 137.328 | 5.722 | 2.4 | 2.4 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 550816 | 1236 | 216.0084 | 0% | 100% | 100% | 100% | 100% | 0% | 11381632 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 128 | 121 | 22374193 | 5212 | 125.088 | 5.212 | 2.4 | 2.4 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 551909 | 1093 | 209.7084 | 0% | 0% | 100% | 100% | 100% | 0% | 11381762 | 130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 125 | 110 | 22379018 | 4825 | 115.8 | 4.825 | 2.7 | 2.7 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 552907 | 998 | 206.8394 | 0% | 0% | 100% | 100% | 100% | 0% | 11382047 | 285 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 133413 | 133.413 | 133.413 | [12 empty] | 26907 | 26907 | 201.682 | [6 empty] | 3228 | 3228 | 1.2783 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 23
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | FIDEL RAMOS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26823 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22379018 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 552907 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11382047 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 106 | 22383849 | 4831 | 115.944 | 4.831 | 3.5 | 3.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 553914 | 1007 | 208.4455 | 0% | 0% | 100% | 100% | 100% | 60% | 11382786 | 739 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 108 | 22388325 | 4476 | 107.424 | 4.476 | 4.6 | 4.6 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 554874 | 960 | 214.4772 | 0% | 0% | 100% | 100% | 100% | 60% | 11383694 | 908 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 111 | 22392800 | 4475 | 107.4 | 4.475 | 5.8 | 5.8 | 3B | 0 | 0 | 1137 | 1185 | 1136 | N/A | N/A | N/A | N/A | 555832 | 958 | 214.0782 | 0% | 0% | 100% | 100% | 100% | 60% | 11384501 | 807 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 148 | 106 | 22397284 | 4484 | 107.616 | 4.484 | 7.7 | 7.7 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 556883 | 1051 | 234.3889 | 0% | 0% | 100% | 100% | 100% | 60% | 11384822 | 321 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 | 116 | 22401696 | 4412 | 105.888 | 4.412 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 557842 | 959 | 217.3617 | 0% | 0% | 100% | 100% | 100% | 60% | 11384936 | 114 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 130 | 129 | 22406144 | 4448 | 106.752 | 4.448 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 558804 | 962 | 216.277 | 0% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 | 1.14 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 144 | 137 | 22412042 | 5898 | 141.552 | 5.898 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 559842 | 1038 | 175.9919 | 0% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 138 | 139 | 22418304 | 6262 | 150.288 | 6.262 | 9.3 | 9.3 | 3B+1S | 996 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 561052 | 1210 | 193.229 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 142 | 22424382 | 6078 | 145.872 | 6.078 | 8.6 | 8.6 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 562254 | 1202 | 197.7624 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 148 | 22430804 | 6422 | 154.128 | 6.422 | 7.9 | 7.9 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 563486 | 1232 | 191.8405 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 | 0.9
| 58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 147 | 22437028 | 6224 | 149.376 | 6.224 | 7.2 | 7.2 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 564690 | 1204 | 193.4447 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 139 | 22443226 | 6198 | 148.752 | 6.198 | 6.6 | 6.6 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 565914 | 1224 | 197.4831 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 140 | 22449244 | 6018 | 144.432 | 6.018 | 5.9 | 5.9 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 567110 | 1196 | 198.7371 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 134 | 22455118 | 5874 | 140.976 | 5.874 | 5.4 | 5.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 568328 | 1218 | 207.3544 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 140 | 22460995 | 5877 | 141.048 | 5.877 | 5 | 5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 569508 | 1180 | 200.7827 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 137 | 22466868 | 5873 | 140.952 | 5.873 | 4.6 | 4.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 570690 | 1182 | 201.26 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 22472592 | 5724 | 137.376 | 5.724 | 4.3 | 4.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 571861 | 1171 | 204.5772 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 131 | 22478649 | 6057 | 145.368 | 6.057 | 3.8 | 3.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 573038 | 1177 | 194.3206 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 129 | 22484383 | 5734 | 137.616 | 5.734 | 3.5 | 3.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 574212 | 1174 | 204.7436 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 134 | 22490053 | 5670 | 136.08 | 5.67 | 3.4 | 3.4 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 575369 | 1157 | 204.0564 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 130 | 22495813 | 5760 | 138.24 | 5.76 | 3.2 | 3.2 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 576529 | 1160 | 201.3889 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 123 | 22501932 | 6119 | 146.856 | 6.119 | 3.1 | 3.1 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 577744 | 1215 | 198.5619 | 100% | 0% | 100% | 100% | 100% | 0% | 11384936 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 121 | 22506676 | 4744 | 113.856 | 4.744 | 3.4 | 3.4 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 578732 | 988 | 208.2631 | 0% | 0% | 100% | 100% | 100% | 30% | 11385143 | 207 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 140 | 128 | 22511568 | 4892 | 117.408 | 4.892 | 4.3 | 4.3 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 579730 | 998 | 204.0065 | 0% | 0% | 100% | 100% | 100% | 30% | 11385772 | 629 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 132550 | 132.55 | 132.55 | [12 empty] | 26823 | 26823 | 202.3614 | [6 empty] | 3725 | 3725 | 1.0933 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 24
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS / JEFFREY LAMAYO
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | GLITTERS SY
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26885 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22511568 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 579730 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11385772 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 109 | 22516602 | 5034 | 120.816 | 5.034 | 5 | 5 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 580750 | 1020 | 202.6222 | 0% | 0% | 100% | 100% | 100% | 60% | 11386475 | 703 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 110 | 22521164 | 4562 | 109.488 | 4.562 | 6 | 6 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 581678 | 928 | 203.4196 | 0% | 0% | 100% | 100% | 100% | 60% | 11387324 | 849 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 112 | 22525726 | 4562 | 109.488 | 4.562 | 7 | 7 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 582604 | 926 | 202.9811 | 0% | 0% | 100% | 100% | 100% | 60% | 11388207 | 883 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 114 | 22530094 | 4368 | 104.832 | 4.368 | 8.7 | 8.7 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 583594 | 990 | 226.6484 | 0% | 0% | 100% | 100% | 100% | 60% | 11388507 | 300 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 | 117 | 22534468 | 4374 | 104.976 | 4.374 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 584588 | 994 | 227.2519 | 0% | 0% | 100% | 100% | 100% | 60% | 11388531 | 24 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 140 | 22539749 | 5281 | 126.744 | 5.281 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 585619 | 1031 | 195.2282 | 0% | 0% | 100% | 100% | 100% | 0% | 11388531 | 0 | 1.15 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 146 | 22545771 | 6022 | 144.528 | 6.022 | 9.2 | 9.2 | 3B+1S | 0 | 997 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 586807 | 1188 | 197.2767 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 141 | 22551855 | 6084 | 146.016 | 6.084 | 8.8 | 8.8 | 3B+1S | 0 | 997 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 587987 | 1180 | 193.9513 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 144 | 22558176 | 6321 | 151.704 | 6.321 | 8.2 | 8.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 589195 | 1208 | 191.109 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 22564446 | 6270 | 150.48 | 6.27 | 7.5 | 7.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 590411 | 1216 | 193.9394 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 | 1.2
| 58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 145 | 22570909 | 6463 | 155.112 | 6.463 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 591625 | 1214 | 187.8385 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 147 | 22576901 | 5992 | 143.808 | 5.992 | 6.3 | 6.3 | 3B+1S | 0 | 1054 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 592826 | 1201 | 200.4339 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 141 | 22582881 | 5980 | 143.52 | 5.98 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 594017 | 1191 | 199.1639 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 141 | 22589053 | 6172 | 148.128 | 6.172 | 5.1 | 5.1 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 595251 | 1234 | 199.9352 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 136 | 22594874 | 5821 | 139.704 | 5.821 | 4.7 | 4.7 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 596424 | 1173 | 201.5118 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 137 | 22600613 | 5739 | 137.736 | 5.739 | 4.3 | 4.3 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 597600 | 1176 | 204.9137 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 136 | 22606422 | 5809 | 139.416 | 5.809 | 3.8 | 3.8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 598779 | 1179 | 202.9609 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 132 | 22612298 | 5876 | 141.024 | 5.876 | 3.4 | 3.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 599960 | 1181 | 200.9871 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 134 | 22618170 | 5872 | 140.928 | 5.872 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 601131 | 1171 | 199.421 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 129 | 22623820 | 5650 | 135.6 | 5.65 | 2.9 | 2.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 602293 | 1162 | 205.6637 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 127 | 22629324 | 5504 | 132.096 | 5.504 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 603452 | 1159 | 210.5741 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 129 | 22634326 | 5002 | 120.048 | 5.002 | 2.7 | 2.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 604492 | 1040 | 207.9168 | 0% | 100% | 100% | 100% | 100% | 0% | 11388531 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 115 | 22639568 | 5242 | 125.808 | 5.242 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 605572 | 1080 | 206.0282 | 0% | 0% | 100% | 100% | 100% | 20% | 11388661 | 130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 146 | 111 | 22644457 | 4889 | 117.336 | 4.889 | 3.9 | 3.9 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 606615 | 1043 | 213.3361 | 0% | 0% | 100% | 100% | 100% | 20% | 11389661 | 1000 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 132889 | 132.889 | 132.889 | [12 empty] | 26885 | 26885 | 202.3117 | [6 empty] | 3889 | 3889 | 1.2117 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## OCT 25
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY / JEFFREY LAMAYO
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | PAUL LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27073 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22644457 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 606615 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11389661 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 139 | 110 | 22648874 | 4417 | 106.008 | 4.417 | 6.8 | 6.8 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 607526 | 911 | 206.2486 | 0% | 0% | 100% | 100% | 100% | 75% | 11390698 | 1037 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 109 | 22653299 | 4425 | 106.2 | 4.425 | 7.9 | 7.9 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 608451 | 925 | 209.0395 | 0% | 0% | 100% | 100% | 100% | 75% | 11391731 | 1033 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 108 | 22657750 | 4451 | 106.824 | 4.451 | 9.1 | 9.1 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 609410 | 959 | 215.4572 | 0% | 0% | 100% | 100% | 100% | 75% | 11392788 | 1057 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 127 | 115 | 22662260 | 4510 | 108.24 | 4.51 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 610408 | 998 | 221.286 | 0% | 0% | 100% | 100% | 100% | 75% | 11392923 | 135 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 117 | 22666892 | 4632 | 111.168 | 4.632 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 611410 | 1002 | 216.3212 | 0% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 134 | 22672780 | 5888 | 141.312 | 5.888 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 612538 | 1128 | 191.5761 | 0% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 | 1.05 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 139 | 22678822 | 6042 | 145.008 | 6.042 | 9 | 9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 613730 | 1192 | 197.2857 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 22684967 | 6145 | 147.48 | 6.145 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 614932 | 1202 | 195.6062 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 141 | 22691006 | 6039 | 144.936 | 6.039 | 8 | 8 | 3B+1S | 1017 | 0 | 1187 | 1186 | 1187 | N/A | N/A | N/A | N/A | 616131 | 1199 | 100 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 172 | 22697359 | 6353 | 152.472 | 6.353 | 7.4 | 7.4 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 617343 | 1212 | 190.776 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 | 1.09
| 58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 144 | 22703359 | 6000 | 144 | 6 | 6.8 | 6.8 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 618546 | 1203 | 200.5 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 140 | 22709464 | 6105 | 146.52 | 6.105 | 6.3 | 6.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 619746 | 1200 | 196.5602 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 136 | 22715414 | 5950 | 142.8 | 5.95 | 5.8 | 5.8 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 620935 | 1189 | 199.8319 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 139 | 22721285 | 5871 | 140.904 | 5.871 | 5.4 | 5.4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 622136 | 1201 | 204.5648 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 136 | 22727259 | 5974 | 143.376 | 5.974 | 5 | 5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 623325 | 1189 | 199.0291 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 22733046 | 5787 | 138.888 | 5.787 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 624507 | 1182 | 204.2509 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 136 | 22738993 | 5947 | 142.728 | 5.947 | 4.2 | 4.2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 625688 | 1181 | 198.5875 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 131 | 22744660 | 5667 | 136.008 | 5.667 | 3.9 | 3.9 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 626863 | 1175 | 207.3407 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 128 | 22750408 | 5748 | 137.952 | 5.748 | 3.6 | 3.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 628034 | 1171 | 203.723 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 128 | 22756061 | 5653 | 135.672 | 5.653 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 629206 | 1172 | 207.3235 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 127 | 22761763 | 5702 | 136.848 | 5.702 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 630383 | 1177 | 206.4188 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 130 | 22767492 | 5729 | 137.496 | 5.729 | 3 | 3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 631528 | 1145 | 199.8604 | 100% | 0% | 100% | 100% | 100% | 0% | 11392923 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 125 | 22772717 | 5225 | 125.4 | 5.225 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 632614 | 1086 | 207.8469 | 0% | 0% | 100% | 100% | 100% | 35% | 11393190 | 267 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 142 | 116 | 22777884 | 5167 | 124.008 | 5.167 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 633688 | 1074 | 207.8576 | 0% | 0% | 100% | 100% | 100% | 35% | 11393613 | 423 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 133427 | 133.427 | 133.427 | [12 empty] | 27073 | 27073 | 202.905 | [6 empty] | 3952 | 3952 | 1.1033 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (35%)

## OCT 26
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN/JEFFREY LAMAYO
[14 empty] | 10pm - 6am | FIDEL RAMOS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27034 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22777884 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 633688 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11393613 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 140 | 109 | 22782859 | 4975 | 119.4 | 4.975 | 5.8 | 5.8 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 634730 | 1042 | 209.4472 | 0% | 0% | 100% | 100% | 100% | 70% | 11394441 | 828 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 107 | 22787532 | 4673 | 112.152 | 4.673 | 7.1 | 7.1 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 635703 | 973 | 208.2174 | 0% | 0% | 100% | 100% | 100% | 70% | 11395344 | 903 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 111 | 22792043 | 4511 | 108.264 | 4.511 | 8.3 | 8.3 | 3B | 0 | 0 | 1126 | 1185 | 1127 | N/A | N/A | N/A | N/A | 636652 | 949 | 210.3746 | 0% | 0% | 100% | 100% | 100% | 70% | 11396271 | 927 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 114 | 22796620 | 4577 | 109.848 | 4.577 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1127 | N/A | N/A | N/A | N/A | 637650 | 998 | 218.0468 | 0% | 0% | 100% | 100% | 100% | 70% | 11396705 | 434 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 125 | 22801412 | 4792 | 115.008 | 4.792 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 638706 | 1056 | 220.3673 | 0% | 0% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 128 | 22806170 | 4758 | 114.192 | 4.758 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 639764 | 1058 | 222.3623 | 0% | 0% | 100% | 100% | 100% | 0% | 11396705 | 0 | 1.09 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 147 | 22812164 | 5994 | 143.856 | 5.994 | 9.3 | 9.3 | 3B+1S | 0 | 1007 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 640957 | 1193 | 199.0324 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 145 | 22818160 | 5996 | 143.904 | 5.996 | 8.8 | 8.8 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 642158 | 1201 | 200.3002 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 148 | 22824150 | 5990 | 143.76 | 5.99 | 8.2 | 8.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 643365 | 1207 | 100 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 146 | 22830332 | 6182 | 148.368 | 6.182 | 7.6 | 7.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 644591 | 1226 | 198.3177 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 | 1.12
| 58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 141 | 22836564 | 6232 | 149.568 | 6.232 | 7 | 7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 645803 | 1212 | 194.4801 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 139 | 22842721 | 6157 | 147.768 | 6.157 | 6.4 | 6.4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 647056 | 1253 | 203.5082 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 134 | 22848731 | 6010 | 144.24 | 6.01 | 5.8 | 5.8 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 648262 | 1206 | 200.6656 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 134 | 22854652 | 5921 | 142.104 | 5.921 | 5.4 | 5.4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 649488 | 1226 | 207.0596 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 22860150 | 5498 | 131.952 | 5.498 | 5.2 | 5.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 650555 | 1067 | 194.0706 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 138 | 134 | 22866004 | 5854 | 140.496 | 5.854 | 4.7 | 4.7 | 3B+1S | 0 | 1010 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 651759 | 1204 | 205.6713 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 22871630 | 5626 | 135.024 | 5.626 | 4.5 | 4.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 652900 | 1141 | 202.8084 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 129 | 22877414 | 5784 | 138.816 | 5.784 | 4.3 | 4.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 654066 | 1166 | 201.5906 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 121 | 22883356 | 5942 | 142.608 | 5.942 | 4 | 4 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 655243 | 1177 | 198.0815 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 128 | 22888758 | 5402 | 129.648 | 5.402 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 656366 | 1123 | 207.886 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 130 | 22894373 | 5615 | 134.76 | 5.615 | 3.6 | 3.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 657535 | 1169 | 208.1923 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 126 | 22900226 | 5853 | 140.472 | 5.853 | 3.4 | 3.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 658734 | 1199 | 204.8522 | 0% | 100% | 100% | 100% | 100% | 0% | 11396705 | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 120 | 22905014 | 4788 | 114.912 | 4.788 | 3.6 | 3.6 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 659726 | 992 | 207.1846 | 0% | 0% | 100% | 100% | 100% | 30% | 11396942 | 237 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 144 | 121 | 22909942 | 4928 | 118.272 | 4.928 | 4.6 | 4.6 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 660722 | 996 | 202.1104 | 0% | 0% | 100% | 100% | 100% | 30% | 11397710 | 768 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 132058 | 132.058 | 132.058 | [12 empty] | 27034 | 27034 | 204.7131 | [6 empty] | 4097 | 4097 | 1.1617 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 27
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | FIDEL RAMOS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24830 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 22909942 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 660722 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11397710 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 113 | 22914716 | 4774 | 114.576 | 4.774 | 5.4 | 5.4 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 661730 | 1008 | 211.1437 | 0% | 0% | 100% | 100% | 100% | 60% | 11398550 | 840 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 110 | 22919234 | 4518 | 108.432 | 4.518 | 6.6 | 6.6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 662658 | 928 | 205.4006 | 0% | 0% | 100% | 100% | 100% | 60% | 11399468 | 918 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 104 | 22923748 | 4514 | 108.336 | 4.514 | 7.7 | 7.7 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 663586 | 928 | 205.5826 | 0% | 0% | 100% | 100% | 100% | 60% | 11400422 | 954 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 112 | 22928168 | 4420 | 106.08 | 4.42 | 9.3 | 9.3 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 664540 | 954 | 215.8371 | 0% | 0% | 100% | 100% | 100% | 60% | 11400702 | 280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 120 | 22932594 | 4426 | 106.224 | 4.426 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 665502 | 962 | 217.352 | 0% | 0% | 100% | 100% | 100% | 60% | 11400753 | 51 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 133 | 22937756 | 5162 | 123.888 | 5.162 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 666466 | 964 | 186.7493 | 0% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 | 1.2 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 139 | 22943358 | 5602 | 134.448 | 5.602 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 667573 | 1107 | 197.608 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 142 | 22950004 | 6646 | 159.504 | 6.646 | 8.6 | 8.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 668930 | 1357 | 204.183 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 142 | 22955978 | 5974 | 143.376 | 5.974 | 8 | 8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 670295 | 1365 | 228.4901 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 143 | 22962079 | 6101 | 146.424 | 6.101 | 7.3 | 7.3 | 3B+1S | 1118 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 671587 | 1292 | 211.7686 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 | 1.25
| 58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 143 | 22968379 | 6300 | 151.2 | 6.3 | 6.6 | 6.6 | 3B+1S | 1188 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 671587 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 22974829 | 6450 | 154.8 | 6.45 | 5.3 | 5.3 | 3B+1S | 1187 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 671587 | 0 | 0 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 126 | 137 | 22981191 | 6362 | 152.688 | 6.362 | 4.4 | 4.4 | 3B+1S | 1190 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 672941 | 1354 | 212.8262 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 138 | 138 | 22987221 | 6030 | 144.72 | 6.03 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 674140 | 1199 | 198.8391 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 136 | 138 | 22992910 | 5689 | 136.536 | 5.689 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 675270 | 1130 | 198.6289 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 135 | 22998965 | 6055 | 145.32 | 6.055 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 676465 | 1195 | 197.3576 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 140 | 23004808 | 5843 | 140.232 | 5.843 | 3.2 | 3.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 677620 | 1155 | 197.6724 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 134 | 23010593 | 5785 | 138.84 | 5.785 | 3.1 | 3.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 678781 | 1161 | 200.6914 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 | 1.35 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 127 | 23016164 | 5571 | 133.704 | 5.571 | 2.9 | 2.9 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 679950 | 1169 | 209.8367 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 134 | 128 | 23021618 | 5454 | 130.896 | 5.454 | 2.8 | 2.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 681101 | 1151 | 211.0378 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 130 | 23027256 | 5638 | 135.312 | 5.638 | 2.6 | 2.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 682266 | 1165 | 206.6336 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 126 | 23033024 | 5768 | 138.432 | 5.768 | 2.5 | 2.5 | 3B+1S | 1033 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 683440 | 1174 | 203.5368 | 100% | 0% | 100% | 100% | 100% | 0% | 11400753 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 122 | 23038022 | 4998 | 119.952 | 4.998 | 2.8 | 2.8 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 684462 | 1022 | 204.4818 | 0% | 0% | 100% | 100% | 100% | 30% | 11401028 | 275 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 139 | 115 | 23043282 | 5260 | 126.24 | 5.26 | 3.6 | 3.6 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 685552 | 1090 | 207.2243 | 0% | 0% | 100% | 100% | 100% | 30% | 11401858 | 830 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 133340 | 133.34 | 133.34 | [12 empty] | 24830 | 24830 | 186.2157 | [6 empty] | 4148 | 4148 | 1.2117 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
MERALCO OPERATION SHIFTING TO GENSET @10:00AM TO 12:00 PM DUE TO EMESSION TEST
GENSET 2 STARTED @ 10;00AM TO 11:00AM DUE TO GENSET EMESSION TEST
GENSET 1 STARTED @ 11;00AM TO 12:00PM DUE TO GENSET EMESSION TEST
MERALCO RESUMED OPERATION @ 12:00 PM
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 28
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | FIDEL RAMOS / JEFFREY LAMAYO
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26857 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23043282 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 685552 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11401858 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 109 | 23047764 | 4482 | 107.568 | 4.482 | 4.6 | 4.6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 686460 | 908 | 202.5881 | 0% | 0% | 100% | 100% | 100% | 60% | 11402586 | 728 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 126 | 105 | 23052462 | 4698 | 112.752 | 4.698 | 5.7 | 5.7 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 687412 | 952 | 202.6394 | 0% | 0% | 100% | 100% | 100% | 60% | 11403384 | 798 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 108 | 23057164 | 4702 | 112.848 | 4.702 | 6.8 | 6.8 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 688378 | 966 | 205.4445 | 0% | 0% | 100% | 100% | 100% | 60% | 11404002 | 618 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 110 | 23061268 | 4104 | 98.496 | 4.104 | 7.9 | 7.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 689340 | 962 | 234.4055 | 0% | 0% | 100% | 100% | 100% | 60% | 11404502 | 500 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 114 | 23065368 | 4100 | 98.4 | 4.1 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 690296 | 956 | 233.1707 | 0% | 0% | 100% | 100% | 100% | 60% | 11404829 | 327 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 132 | 23070722 | 5354 | 128.496 | 5.354 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 691308 | 1012 | 189.0176 | 0% | 0% | 100% | 100% | 100% | 0% | 11404829 | 0 | 1.08 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 140 | 23076604 | 5882 | 141.168 | 5.882 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 692484 | 1176 | 199.932 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 143 | 23082866 | 6262 | 150.288 | 6.262 | 8.6 | 8.6 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 693736 | 1252 | 199.9361 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Normal operation schedule | Water Interruption | WI
| 56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 141 | 23088848 | 5982 | 143.568 | 5.982 | 7.9 | 7.9 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 694922 | 1186 | 198.2615 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 140 | 23095086 | 6238 | 149.712 | 6.238 | 7.3 | 7.3 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 696152 | 1230 | 197.1786 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 | 1.19
| 58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 131 | 23101188 | 6102 | 146.448 | 6.102 | 6.6 | 6.6 | 3B+1S | 0 | 1056 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 697336 | 1184 | 194.0347 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 137 | 23107108 | 5920 | 142.08 | 5.92 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 698532 | 1196 | 202.027 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 138 | 23112838 | 5730 | 137.52 | 5.73 | 5.6 | 5.6 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 699708 | 1176 | 205.2356 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 135 | 139 | 23118807 | 5969 | 143.256 | 5.969 | 4.9 | 4.9 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 700894 | 1186 | 198.6932 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 135 | 23124716 | 5909 | 141.816 | 5.909 | 4.6 | 4.6 | 3B+1S | 0 | 1037 | 1185 | 1185 | 1187 | N/A | N/A | N/A | N/A | 702117 | 1223 | 206.9724 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 23130706 | 5990 | 143.76 | 5.99 | 4.3 | 4.3 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 703298 | 1181 | 197.1619 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 23136430 | 5724 | 137.376 | 5.724 | 3.8 | 3.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 704469 | 1171 | 204.5772 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 128 | 23142343 | 5913 | 141.912 | 5.913 | 3.5 | 3.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 705649 | 1180 | 199.5603 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 23148145 | 5802 | 139.248 | 5.802 | 3.2 | 3.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 706823 | 1174 | 202.344 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 130 | 23153918 | 5773 | 138.552 | 5.773 | 2.9 | 2.9 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 707994 | 1171 | 202.8408 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 133 | 23159695 | 5777 | 138.648 | 5.777 | 2.6 | 2.6 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 709163 | 1169 | 202.3542 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 132 | 23165291 | 5596 | 134.304 | 5.596 | 2.5 | 2.5 | 3B+1S | 0 | 1034 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 710315 | 1152 | 205.8613 | 0% | 100% | 100% | 100% | 100% | 0% | 11404829 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 120 | 23170480 | 5189 | 124.536 | 5.189 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 711377 | 1062 | 204.6637 | 0% | 0% | 100% | 100% | 100% | 30% | 11404996 | 167 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 138 | 116 | 23175443 | 4963 | 119.112 | 4.963 | 3.2 | 3.2 | 3B | 0 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 712409 | 1032 | 207.9387 | 0% | 0% | 100% | 100% | 100% | 30% | 11405590 | 594 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 132161 | 132.161 | 132.161 | [12 empty] | 26857 | 26857 | 203.2143 | [6 empty] | 3732 | 3732 | 1.1717 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 29
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | GLITTERS SY
| WATER NETWORK | [12 empty] | 2pm - 10pm | GLITTERS SY
10pm - 6am
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26940 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23175443 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 712409 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11405590 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 141 | 111 | 23180142 | 4699 | 112.776 | 4.699 | 4.2 | 4.2 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 713397 | 988 | 210.2575 | 0% | 0% | 100% | 100% | 100% | 60% | 11406355 | 765 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 136 | 109 | 23184853 | 4711 | 113.064 | 4.711 | 5.4 | 5.4 | 3B | 0 | 0 | 1137 | 1185 | 1136 | N/A | N/A | N/A | N/A | 714392 | 995 | 211.2078 | 0% | 0% | 100% | 100% | 100% | 60% | 11407198 | 843 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 106 | 23189543 | 4690 | 112.56 | 4.69 | 6.3 | 6.3 | 3B | 0 | 0 | 1118 | 1185 | 1117 | N/A | N/A | N/A | N/A | 715379 | 987 | 210.4478 | 0% | 0% | 100% | 100% | 100% | 60% | 11407983 | 785 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 108 | 23193559 | 4016 | 96.384 | 4.016 | 8.1 | 8.1 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 716372 | 993 | 247.261 | 0% | 0% | 100% | 100% | 100% | 60% | 11408389 | 406 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 113 | 23197574 | 4015 | 96.36 | 4.015 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1117 | N/A | N/A | N/A | N/A | 717367 | 995 | 247.8207 | 0% | 0% | 100% | 100% | 100% | 60% | 11408533 | 144 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 136 | 23202503 | 4929 | 118.296 | 4.929 | 9.5 | 9.5 | 3B | 0 | 0 | 1177 | 1185 | 1167 | N/A | N/A | N/A | N/A | 718262 | 895 | 181.5784 | 0% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 | 1.06 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 138 | 23208167 | 5664 | 135.936 | 5.664 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 719356 | 1094 | 193.1497 | 0% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 141 | 23214318 | 6151 | 147.624 | 6.151 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 720552 | 1196 | 194.4399 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Normal operation schedule | Water Interruption | WI | RANIEL MANA
| 56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 144 | 23220476 | 6158 | 147.792 | 6.158 | 8.5 | 8.5 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 721727 | 1175 | 190.8087 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 144 | 23226800 | 6324 | 151.776 | 6.324 | 7.9 | 7.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 722975 | 1248 | 197.3435 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 | 1.16
| 58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 147 | 23232758 | 5958 | 142.992 | 5.958 | 7.2 | 7.2 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 724157 | 1182 | 198.3887 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 143 | 23239077 | 6319 | 151.656 | 6.319 | 6.5 | 6.5 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 725399 | 1242 | 196.5501 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 23244705 | 5628 | 135.072 | 5.628 | 6 | 6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 726547 | 1148 | 203.9801 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 140 | 23250826 | 6121 | 146.904 | 6.121 | 5.4 | 5.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 727787 | 1240 | 202.5813 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 132 | 23256479 | 5653 | 135.672 | 5.653 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 728934 | 1147 | 202.9011 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 136 | 23262164 | 5685 | 136.44 | 5.685 | 4.9 | 4.9 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 730071 | 1137 | 200 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 141 | 23267974 | 5810 | 139.44 | 5.81 | 4.6 | 4.6 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 731245 | 1174 | 202.0654 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 134 | 23273903 | 5929 | 142.296 | 5.929 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 732436 | 1191 | 200.877 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 128 | 23279770 | 5867 | 140.808 | 5.867 | 4.1 | 4.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 733601 | 1165 | 198.5683 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 126 | 23285330 | 5560 | 133.44 | 5.56 | 3.8 | 3.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 734769 | 1168 | 210.0719 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 130 | 23291086 | 5756 | 138.144 | 5.756 | 3.5 | 3.5 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 735952 | 1183 | 205.5247 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 125 | 23296939 | 5853 | 140.472 | 5.853 | 3.3 | 3.3 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 737177 | 1225 | 209.2944 | 100% | 0% | 100% | 100% | 100% | 0% | 11408533 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 122 | 23302270 | 5331 | 127.944 | 5.331 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 738281 | 1104 | 207.0906 | 0% | 0% | 100% | 100% | 100% | 30% | 11408642 | 109 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 116 | 23307322 | 5052 | 121.248 | 5.052 | 3.6 | 3.6 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 739349 | 1068 | 211.4014 | 0% | 0% | 100% | 100% | 100% | 30% | 11408806 | 164 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 131879 | 131.879 | 131.879 | [12 empty] | 26940 | 26940 | 204.2782 | [6 empty] | 3216 | 3216 | 1.165 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:28 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 30
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | FIDEL RAMOS
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26651 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23307322 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 739349 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11408806 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 129 | 116 | 23312558 | 5236 | 125.664 | 5.236 | 4.2 | 4.2 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 740344 | 995 | 190.0306 | 0% | 0% | 100% | 100% | 100% | 60% | 11409365 | 559 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 114 | 23317125 | 4567 | 109.608 | 4.567 | 5 | 5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 741327 | 983 | 215.2398 | 0% | 0% | 100% | 100% | 100% | 60% | 11410010 | 645 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 141 | 109 | 23321694 | 4569 | 109.656 | 4.569 | 6 | 6 | 3B | 0 | 0 | 1123 | 1185 | 1125 | N/A | N/A | N/A | N/A | 742311 | 984 | 215.3644 | 0% | 0% | 100% | 100% | 100% | 60% | 11410760 | 750 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 129 | 108 | 23325814 | 4120 | 98.88 | 4.12 | 7.9 | 7.9 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 743337 | 1026 | 249.0291 | 0% | 0% | 100% | 100% | 100% | 60% | 11410960 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 116 | 113 | 23329936 | 4122 | 98.928 | 4.122 | 9.5 | 9.5 | 3B | 0 | 0 | 1077 | 1185 | 1076 | N/A | N/A | N/A | N/A | 744366 | 1029 | 249.6361 | 0% | 0% | 100% | 100% | 100% | 60% | 11410989 | 29 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 129 | 125 | 23335402 | 5466 | 131.184 | 5.466 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 745302 | 936 | 171.2404 | 0% | 0% | 100% | 100% | 100% | 0% | 11410989 | 0 | 1.12 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 139 | 23340816 | 5414 | 129.936 | 5.414 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1127 | N/A | N/A | N/A | N/A | 746266 | 964 | 178.0569 | 0% | 0% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 142 | 144 | 23346918 | 6102 | 146.448 | 6.102 | 9.3 | 9.3 | 3B+1S | 0 | 972 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 747452 | 1186 | 194.3625 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Normal operation schedule | Water Interruption | WI | RANIEL MANA
| 56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 140 | 23353172 | 6254 | 150.096 | 6.254 | 8.9 | 8.9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 748670 | 1218 | 194.7554 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 145 | 23359748 | 6576 | 157.824 | 6.576 | 8.2 | 8.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 749920 | 1250 | 190.0852 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 | 1.18
| 58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 146 | 23365536 | 5788 | 138.912 | 5.788 | 7.6 | 7.6 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 751048 | 1128 | 194.886 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 135 | 23371942 | 6406 | 153.744 | 6.406 | 7 | 7 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 752294 | 1246 | 194.5052 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 143 | 23377834 | 5892 | 141.408 | 5.892 | 6.4 | 6.4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 753480 | 1186 | 201.2899 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 141 | 23383826 | 5992 | 143.808 | 5.992 | 5.9 | 5.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 754670 | 1190 | 198.5981 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 142 | 23389803 | 5977 | 143.448 | 5.977 | 5.6 | 5.6 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 755868 | 1198 | 200.435 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 137 | 23395394 | 5591 | 134.184 | 5.591 | 5.4 | 5.4 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 756992 | 1124 | 201.0374 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 133 | 23401376 | 5982 | 143.568 | 5.982 | 5.1 | 5.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 758202 | 1210 | 202.2735 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 134 | 135 | 23407229 | 5853 | 140.472 | 5.853 | 4.9 | 4.9 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 759377 | 1175 | 200.7518 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 136 | 23412869 | 5640 | 135.36 | 5.64 | 4.7 | 4.7 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 760541 | 1164 | 206.383 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 134 | 23418459 | 5590 | 134.16 | 5.59 | 4.6 | 4.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 761695 | 1154 | 206.4401 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 127 | 23423977 | 5518 | 132.432 | 5.518 | 4.5 | 4.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 762853 | 1158 | 209.8586 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 121 | 23429548 | 5571 | 133.704 | 5.571 | 4.4 | 4.4 | 3B+1S | 0 | 974 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 764004 | 1151 | 206.6056 | 0% | 100% | 100% | 100% | 100% | 0% | 11410989 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 117 | 23434556 | 5008 | 120.192 | 5.008 | 4.6 | 4.6 | 3B | 0 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 765000 | 996 | 198.8818 | 0% | 0% | 100% | 100% | 100% | 30% | 11411136 | 147 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 133 | 114 | 23439392 | 4836 | 116.064 | 4.836 | 5.3 | 5.3 | 3B | 0 | 0 | 1156 | 1185 | 1157 | N/A | N/A | N/A | N/A | 766000 | 1000 | 206.7825 | 0% | 0% | 100% | 100% | 100% | 30% | 11411762 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 132070 | 132.07 | 132.07 | [12 empty] | 26651 | 26651 | 201.7945 | [6 empty] | 2956 | 2956 | 1.165 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:32 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## OCT 31
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | PAUL LABIAN/JEFFREY LAMAYO
| WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[14 empty] | 10pm - 6am | GLITTERS SY
| LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
| DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
| 2016-10-31 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26101 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23439392 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 766000 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11411762 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
| 48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 107 | 23444096 | 4704 | 112.896 | 4.704 | 6.2 | 6.2 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 766996 | 996 | 211.7347 | 0% | 0% | 100% | 100% | 100% | 60% | 11412619 | 857 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
| 49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 109 | 23448522 | 4426 | 106.224 | 4.426 | 7.2 | 7.2 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 767916 | 920 | 207.8626 | 0% | 0% | 100% | 100% | 100% | 60% | 11413657 | 1038 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
| 50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 101 | 23453082 | 4560 | 109.44 | 4.56 | 8.4 | 8.4 | 3B | 0 | 0 | 1095 | 1185 | 1096 | N/A | N/A | N/A | N/A | 768850 | 934 | 204.8246 | 0% | 0% | 100% | 100% | 100% | 60% | 11414796 | 1139 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL LABIAN/JEFFREY LAMAYO
| 51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 | 108 | 23457278 | 4196 | 100.704 | 4.196 | 9.5 | 9.5 | 3B | 0 | 0 | 1075 | 1185 | 1076 | N/A | N/A | N/A | N/A | 769706 | 856 | 204.0038 | 0% | 0% | 100% | 100% | 100% | 60% | 11415768 | 972 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | FIDEL RAMOS / JEFFREY LAMAYO
| 52:00 | 5:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 115 | 117 | 23461866 | 4588 | 110.112 | 4.588 | 9.5 | 9.5 | 3B | 0 | 0 | 1056 | 1185 | 1057 | N/A | N/A | N/A | N/A | 770572 | 866 | 188.7533 | 0% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | GLITTERS SY / JEFFREY LAMAYO
| 53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 128 | 23466941 | 5075 | 121.8 | 5.075 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1116 | N/A | N/A | N/A | N/A | 771499 | 927 | 182.6601 | 0% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 | 1.2 | Normal operation schedule | Error - General | E | RANDY REGENCIA / JEFFREY LAMAYO
| 54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 137 | 23472589 | 5648 | 135.552 | 5.648 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 772556 | 1057 | 187.1459 | 0% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Normal operation schedule | Power Interruption | PI | PAUL LABIAN
| 55:00 | 8:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 142 | 23478492 | 5903 | 141.672 | 5.903 | 9.4 | 9.4 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 773700 | 1144 | 193.7998 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Normal operation schedule | Water Interruption | WI | RANIEL MANA
| 56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 138 | 149 | 23484465 | 5973 | 143.352 | 5.973 | 9 | 9 | 3B+1S | 1007 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 774844 | 1144 | 191.5285 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
| 57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 23490906 | 6441 | 154.584 | 6.441 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 776109 | 1265 | 196.3981 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 | 1.18
| 58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 145 | 23497162 | 6256 | 150.144 | 6.256 | 8 | 8 | 3B+1S | 1017 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 777282 | 1173 | 187.5 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Normal operation schedule
| 59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 134 | 23502894 | 5732 | 137.568 | 5.732 | 7.5 | 7.5 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 778404 | 1122 | 195.7432 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Normal operation schedule | UNITS
| 60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 139 | 23509663 | 6769 | 162.456 | 6.769 | 7 | 7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 779685 | 1281 | 189.2451 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
| 61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 132 | 23515757 | 6094 | 146.256 | 6.094 | 6.5 | 6.5 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 780899 | 1214 | 199.2123 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
| 62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 134 | 23521544 | 5787 | 138.888 | 5.787 | 6.2 | 6.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 782067 | 1168 | 201.8317 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
| 63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 138 | 23527340 | 5796 | 139.104 | 5.796 | 6 | 6 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 783213 | 1146 | 197.7226 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
| 64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 139 | 23533220 | 5880 | 141.12 | 5.88 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 784384 | 1171 | 199.1497 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
| 65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 131 | 23538896 | 5676 | 136.224 | 5.676 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 785549 | 1165 | 205.2502 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
| 66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 133 | 134 | 23544490 | 5594 | 134.256 | 5.594 | 5.3 | 5.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 786714 | 1165 | 208.2588 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
l | 67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 136 | 23550075 | 5585 | 134.04 | 5.585 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 787871 | 1157 | 207.162 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
| 68:00 | 21:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 130 | 23555562 | 5487 | 131.688 | 5.487 | 4.9 | 4.9 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 789025 | 1154 | 210.3153 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
| 69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 129 | 23560496 | 4934 | 118.416 | 4.934 | 4.8 | 4.8 | 3B+1S | 1055 | 0 | 1156 | 1185 | 1137 | N/A | N/A | N/A | N/A | 790031 | 1006 | 203.8914 | 100% | 0% | 100% | 100% | 100% | 0% | 11415768 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
| 70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 117 | 23565587 | 5091 | 122.184 | 5.091 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 1185 | 1136 | N/A | N/A | N/A | N/A | 791074 | 1043 | 204.8713 | 0% | 0% | 100% | 100% | 100% | 20% | 11415844 | 76 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
| 71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 116 | 23570585 | 4998 | 119.952 | 4.998 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 1136 | N/A | N/A | N/A | N/A | 792101 | 1027 | 205.4822 | 0% | 0% | 100% | 100% | 100% | 20% | 11416241 | 397 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[11 empty] | TOTAL | [5 empty] | 131193 | 131.193 | 131.193 | [12 empty] | 26101 | 26101 | 198.9512 | [6 empty] | 4479 | 4479 | 1.1917 |  | MLD | 1
[45 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (60%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (OCT 31, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)