## NOV 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-01 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25881 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23570585 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 792101 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11416241 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 137 | 107 | 23574988 | 4403 | 105.672 | 4.403 | 6.5 | 6.5 | 3B | 0 | 0 | 1147 | 1185 | 1086 | N/A | N/A | N/A | N/A | 793036 | 935 | 212.3552 | 0% | 0% | 100% | 100% | 100% | 75% | 11417004 | 763 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 111 | 23579433 | 4445 | 106.68 | 4.445 | 7.9 | 7.9 | 3B | 0 | 0 | 1147 | 1185 | 1086 | N/A | N/A | N/A | N/A | 793996 | 960 | 215.973 | 0% | 0% | 100% | 100% | 100% | 75% | 11417722 | 718 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 109 | 23583993 | 4560 | 109.44 | 4.56 | 9.2 | 9.2 | 3B | 0 | 0 | 1147 | 1185 | 1086 | N/A | N/A | N/A | N/A | 794985 | 989 | 216.886 | 0% | 0% | 100% | 100% | 100% | 75% | 11418464 | 742 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 111 | 23588495 | 4502 | 108.048 | 4.502 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1046 | N/A | N/A | N/A | N/A | 795917 | 932 | 207.0191 | 0% | 0% | 100% | 100% | 100% | 75% | 11418605 | 141 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 115 | 110 | 23593102 | 4607 | 110.568 | 4.607 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1046 | N/A | N/A | N/A | N/A | 796879 | 962 | 208.8127 | 0% | 0% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 126 | 120 | 23598598 | 5496 | 131.904 | 5.496 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1016 | N/A | N/A | N/A | N/A | 797876 | 997 | 181.4047 | 0% | 0% | 100% | 100% | 100% | 0% | 11418605 | 0 | 1.12 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 137 | 23604207 | 5609 | 134.616 | 5.609 | 9.4 | 9.4 | 3B | 0 | 0 | 1116 | 1185 | 1106 | N/A | N/A | N/A | N/A | 798840 | 964 | 171.8666 | 0% | 0% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 | 135 | 23609977 | 5770 | 138.48 | 5.77 | 9.4 | 9.4 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 799860 | 1020 | 176.7764 | 0% | 0% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 144 | 140 | 23615374 | 5397 | 129.528 | 5.397 | 9.4 | 9.4 | 3B | 0 | 0 | 1177 | 1185 | 1178 | N/A | N/A | N/A | N/A | 800886 | 1026 | 190.1056 | 0% | 0% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 143 | 143 | 23621246 | 5872 | 140.928 | 5.872 | 9.3 | 9.3 | 3B+1S | 0 | 976 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 802059 | 1173 | 199.7616 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 | 0.92
58:00 | 11:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 141 | 156 | 23627526 | 6280 | 150.72 | 6.28 | 9 | 9 | 3B+1S | 0 | 1015 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 803268 | 1209 | 192.5159 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Normal operation schedule
59:00 | 12:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 139 | 146 | 23633484 | 5958 | 142.992 | 5.958 | 8.7 | 8.7 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1886 | N/A | N/A | N/A | N/A | 804452 | 1184 | 198.7244 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 10 | 7.0423 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 132 | 23639964 | 6480 | 155.52 | 6.48 | 8.5 | 8.5 | 3B+1S | 0 | 985 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 805700 | 1248 | 192.5926 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 133 | 23645306 | 5342 | 128.208 | 5.342 | 8.1 | 8.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 806750 | 1050 | 196.5556 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 138 | 23650998 | 5692 | 136.608 | 5.692 | 7.8 | 7.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 807918 | 1168 | 205.2003 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 23656886 | 5888 | 141.312 | 5.888 | 7.5 | 7.5 | 3B+1S | 0 | 996 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 809112 | 1194 | 202.7853 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 137 | 23662722 | 5836 | 140.064 | 5.836 | 7.3 | 7.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 810284 | 1172 | 200.8225 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 136 | 132 | 23668156 | 5434 | 130.416 | 5.434 | 7.2 | 7.2 | 3B+1S | 0 | 965 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 811394 | 1110 | 204.2694 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 7 | 4.9296 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 136 | 135 | 23674098 | 5942 | 142.608 | 5.942 | 7 | 7 | 3B+1S | 0 | 975 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 812582 | 1188 | 199.9327 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 7 | 4.9296 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 124 | 23679730 | 5632 | 135.168 | 5.632 | 6.8 | 6.8 | 3B+1S | 0 | 995 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 813709 | 1127 | 200.1065 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 128 | 23685315 | 5585 | 134.04 | 5.585 | 6.6 | 6.6 | 3B+1S | 0 | 995 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 814848 | 1139 | 203.9391 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 123 | 23690572 | 5257 | 126.168 | 5.257 | 6.4 | 6.4 | 3B+1S | 0 | 995 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 815964 | 1116 | 212.2884 | 0% | 100% | 100% | 100% | 100% | 0% | 11418605 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 124 | 115 | 23695688 | 5116 | 122.784 | 5.116 | 6.6 | 6.6 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 816983 | 1019 | 199.179 | 0% | 0% | 100% | 100% | 100% | 30% | 11418735 | 130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 123 | 110 | 23700691 | 5003 | 120.072 | 5.003 | 6.9 | 6.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 817982 | 999 | 199.6802 | 0% | 0% | 100% | 100% | 100% | 30% | 11418906 | 171 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130106 | 130.106 | 130.106 | [12 empty] | 25881 | 25881 | 198.9224 | 0% | 0% | 0% | 0% | 0% |  | 2665 | 2665 | 1.0333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 9:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 01, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-02 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26484 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23700691 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 817982 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11418906 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 130 | 110 | 23705554 | 4863 | 116.712 | 4.863 | 7.6 | 7.6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 818974 | 992 | 203.9893 | 0% | 0% | 100% | 100% | 100% | 70% | 11419532 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 106 | 23710168 | 4614 | 110.736 | 4.614 | 8.1 | 8.1 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 819884 | 910 | 197.2258 | 0% | 0% | 100% | 100% | 100% | 70% | 11420202 | 670 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 127 | 105 | 23714679 | 4511 | 108.264 | 4.511 | 9.1 | 9.1 | 3B | 0 | 0 | 1096 | 1185 | 1196 | N/A | N/A | N/A | N/A | 820790 | 906 | 200.8424 | 0% | 0% | 100% | 100% | 100% | 70% | 11421098 | 896 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 106 | 107 | 23719296 | 4617 | 110.808 | 4.617 | 9.5 | 9.5 | 3B | 0 | 0 | 1045 | 1185 | 1146 | N/A | N/A | N/A | N/A | 821682 | 892 | 193.199 | 0% | 0% | 100% | 100% | 100% | 70% | 11421378 | 280 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL LABIAN
52:00 | 5:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 117 | 23724029 | 4733 | 113.592 | 4.733 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1116 | N/A | N/A | N/A | N/A | 822565 | 883 | 186.5624 | 0% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 120 | 23729700 | 5671 | 136.104 | 5.671 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 823590 | 1025 | 180.7441 | 0% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 | 1.16 | Normal operation schedule | Error - General | E
54:00 | 7:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 142 | 23735444 | 5744 | 137.856 | 5.744 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 824620 | 1030 | 179.3175 | 0% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 137 | 140 | 23741032 | 5588 | 134.112 | 5.588 | 9.3 | 9.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 825758 | 1138 | 203.6507 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 148 | 23747312 | 6280 | 150.72 | 6.28 | 8.7 | 8.7 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 826950 | 1192 | 189.8089 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 147 | 23753680 | 6368 | 152.832 | 6.368 | 7.9 | 7.9 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 828184 | 1234 | 193.7814 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 | 1.22
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 141 | 23760006 | 6326 | 151.824 | 6.326 | 7.2 | 7.2 | 3B+1S | 1097 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 829436 | 1252 | 197.9134 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Normal operation schedule
59:00 | 12:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 23766188 | 6182 | 148.368 | 6.182 | 6.5 | 6.5 | 3B+1S | 1086 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 830670 | 1234 | 199.6118 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 141 | 23772396 | 6208 | 148.992 | 6.208 | 5.9 | 5.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 831916 | 1246 | 200.7088 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 133 | 136 | 23777998 | 5602 | 134.448 | 5.602 | 5.5 | 5.5 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 833081 | 1165 | 207.9614 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 130 | 23783711 | 5713 | 137.112 | 5.713 | 5.3 | 5.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 834244 | 1163 | 203.5708 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 137 | 144 | 23789686 | 5975 | 143.4 | 5.975 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 835414 | 1170 | 195.8159 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 23795381 | 5695 | 136.68 | 5.695 | 5 | 5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 836564 | 1150 | 201.9315 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 130 | 23801149 | 5768 | 138.432 | 5.768 | 4.8 | 4.8 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 837738 | 1174 | 203.5368 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 120 | 23806809 | 5660 | 135.84 | 5.66 | 4.6 | 4.6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 838899 | 1161 | 205.1237 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 125 | 23812581 | 5772 | 138.528 | 5.772 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 840051 | 1152 | 199.5842 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 122 | 23818082 | 5501 | 132.024 | 5.501 | 4.2 | 4.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 841196 | 1145 | 208.144 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 127 | 23823472 | 5390 | 129.36 | 5.39 | 4 | 4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 842344 | 1148 | 212.987 | 100% | 0% | 100% | 100% | 100% | 0% | 11421378 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 120 | 23828742 | 5270 | 126.48 | 5.27 | 4.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 843436 | 1092 | 207.2106 | 0% | 0% | 100% | 100% | 100% | 30% | 11421513 | 135 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 114 | 23833607 | 4865 | 116.76 | 4.865 | 4.6 | 4.6 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 844466 | 1030 | 211.7163 | 0% | 0% | 100% | 100% | 100% | 30% | 11421841 | 328 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132916 | 132.916 | 132.916 | [12 empty] | 26484 | 26484 | 199.2537 | 0% | 0% | 0% | 0% | 0% |  | 2935 | 2935 | 1.1683 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 02, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | G.SY / RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | G.SY / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-03 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26908 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23833607 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 844466 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11421841 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 129 | 116 | 23838464 | 4857 | 116.568 | 4.857 | 5.8 | 5.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 845500 | 1034 | 212.8886 | 0% | 0% | 100% | 100% | 100% | 70% | 11422520 | 679 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 142 | 113 | 23843204 | 4740 | 113.76 | 4.74 | 7.1 | 7.1 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 846484 | 984 | 207.5949 | 0% | 0% | 100% | 100% | 100% | 70% | 11423212 | 692 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 108 | 23847697 | 4493 | 107.832 | 4.493 | 8.3 | 8.3 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 847426 | 942 | 209.6595 | 0% | 0% | 100% | 100% | 100% | 70% | 11423905 | 693 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 107 | 116 | 23851956 | 4259 | 102.216 | 4.259 | 9.1 | 9.1 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 848376 | 950 | 223.0571 | 0% | 0% | 100% | 100% | 100% | 70% | 11424499 | 594 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 120 | 23856542 | 4586 | 110.064 | 4.586 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 849352 | 976 | 212.8216 | 0% | 0% | 100% | 100% | 100% | 70% | 11424599 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 123 | 23861707 | 5165 | 123.96 | 5.165 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 850349 | 997 | 193.03 | 0% | 0% | 100% | 100% | 100% | 0% | 11424599 | 0 | 1.12 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 138 | 23867416 | 5709 | 137.016 | 5.709 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 851438 | 1089 | 190.7514 | 0% | 0% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 141 | 23873373 | 5957 | 142.968 | 5.957 | 9.2 | 9.2 | 3B+1S | 0 | 1019 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 852620 | 1182 | 198.422 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 146 | 23879444 | 6071 | 145.704 | 6.071 | 8.7 | 8.7 | 3B+1S | 0 | 1019 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 853824 | 1204 | 198.3199 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 149 | 23885619 | 6175 | 148.2 | 6.175 | 8.2 | 8.2 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 855006 | 1182 | 191.417 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 | 1.02
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 138 | 23891762 | 6143 | 147.432 | 6.143 | 7.7 | 7.7 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 856225 | 1219 | 198.4372 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 140 | 23897823 | 6061 | 145.464 | 6.061 | 7.2 | 7.2 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 857420 | 1195 | 197.1622 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 138 | 23903716 | 5893 | 141.432 | 5.893 | 6.6 | 6.6 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 858604 | 1184 | 200.9163 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 130 | 23909714 | 5998 | 143.952 | 5.998 | 6.2 | 6.2 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 859783 | 1179 | 196.5655 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 135 | 23915699 | 5985 | 143.64 | 5.985 | 5.8 | 5.8 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 860967 | 1184 | 197.8279 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 23921692 | 5993 | 143.832 | 5.993 | 5.5 | 5.5 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 862126 | 1159 | 193.3923 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 23927710 | 6018 | 144.432 | 6.018 | 5.2 | 5.2 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 863310 | 1184 | 196.7431 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 129 | 23933438 | 5728 | 137.472 | 5.728 | 5 | 5 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 864472 | 1162 | 202.8631 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 131 | 23939207 | 5769 | 138.456 | 5.769 | 4.8 | 4.8 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 865629 | 1157 | 200.5547 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 128 | 23945103 | 5896 | 141.504 | 5.896 | 4.7 | 4.7 | 3B+1S | 0 | 1004 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 866794 | 1165 | 197.5916 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 130 | 23950822 | 5719 | 137.256 | 5.719 | 4.5 | 4.5 | 3B+1S | 0 | 1025 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 867949 | 1155 | 201.9584 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 120 | 23956413 | 5591 | 134.184 | 5.591 | 4.2 | 4.2 | 3B+1S | 0 | 1005 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 869121 | 1172 | 209.6226 | 0% | 100% | 100% | 100% | 100% | 0% | 11424599 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 133 | 123 | 23961862 | 5449 | 130.776 | 5.449 | 4.7 | 4.7 | 3B | 0 | 0 | 1167 | 1185 | 1166 | N/A | N/A | N/A | N/A | 870280 | 1159 | 212.6996 | 0% | 0% | 100% | 100% | 100% | 30% | 11424872 | 273 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 137 | 120 | 23967051 | 5189 | 124.536 | 5.189 | 5.3 | 5.3 | 3B | 0 | 0 | 1166 | 1185 | 1167 | N/A | N/A | N/A | N/A | 871374 | 1094 | 210.8306 | 0% | 0% | 100% | 100% | 100% | 30% | 11425392 | 520 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133444 | 133.444 | 133.444 | [12 empty] | 26908 | 26908 | 201.6426 | 0% | 0% | 0% | 0% | 0% |  | 3551 | 3551 | 1.1267 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 03, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL RAMOS
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-04 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26808 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 23967051 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 871374 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11425392 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 127 | 107 | 23972305 | 5254 | 126.096 | 5.254 | 5.9 | 5.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 872368 | 994 | 189.1892 | 0% | 0% | 100% | 100% | 100% | 70% | 11425902 | 510 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 104 | 23976484 | 4179 | 100.296 | 4.179 | 7.2 | 7.2 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 873325 | 957 | 229.0022 | 0% | 0% | 100% | 100% | 100% | 70% | 11426420 | 518 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 108 | 23980779 | 4295 | 103.08 | 4.295 | 8.6 | 8.6 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 874227 | 902 | 210.0116 | 0% | 0% | 100% | 100% | 100% | 70% | 11426949 | 529 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 158 | 112 | 23984996 | 4217 | 101.208 | 4.217 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1128 | N/A | N/A | N/A | N/A | 875182 | 955 | 226.4643 | 0% | 0% | 100% | 100% | 100% | 70% | 11427295 | 346 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 | 123 | 23989452 | 4456 | 106.944 | 4.456 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 876212 | 1030 | 231.149 | 0% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 130 | 23995196 | 5744 | 137.856 | 5.744 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 877230 | 1018 | 177.2284 | 0% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 | 1.12 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 139 | 24001622 | 6426 | 154.224 | 6.426 | 9.3 | 9.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 878476 | 1246 | 193.8998 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 144 | 24007294 | 5672 | 136.128 | 5.672 | 8.9 | 8.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 879578 | 1102 | 194.2877 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 137 | 24013402 | 6108 | 146.592 | 6.108 | 8.4 | 8.4 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 880789 | 1211 | 198.2646 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 142 | 24019816 | 6414 | 153.936 | 6.414 | 7.9 | 7.9 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 882040 | 1251 | 195.0421 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 | 1.18
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 149 | 24025862 | 6046 | 145.104 | 6.046 | 7.5 | 7.5 | 3B+1S | 1035 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 883168 | 1128 | 186.5696 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 137 | 24031952 | 6090 | 146.16 | 6.09 | 7.1 | 7.1 | 3B+1S | 1036 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 884366 | 1198 | 196.7159 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 145 | 24038154 | 6202 | 148.848 | 6.202 | 6.6 | 6.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 885628 | 1262 | 203.4827 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 134 | 137 | 24043596 | 5442 | 130.608 | 5.442 | 6.2 | 6.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 886740 | 1112 | 204.3366 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 148 | 24049528 | 5932 | 142.368 | 5.932 | 5.9 | 5.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 887956 | 1216 | 204.9899 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 139 | 24055166 | 5638 | 135.312 | 5.638 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 889096 | 1140 | 202.1994 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 132 | 24061078 | 5912 | 141.888 | 5.912 | 5.4 | 5.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 890278 | 1182 | 199.9323 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 127 | 24066990 | 5912 | 141.888 | 5.912 | 5.3 | 5.3 | 3B+1S | 985 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 891446 | 1168 | 197.5643 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 6 | 4.2254 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 121 | 24072945 | 5955 | 142.92 | 5.955 | 5.1 | 5.1 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 892596 | 1150 | 193.115 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 121 | 24078702 | 5757 | 138.168 | 5.757 | 4.9 | 4.9 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 893749 | 1153 | 200.2779 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 124 | 24084404 | 5702 | 136.848 | 5.702 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 894904 | 1155 | 202.5605 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 123 | 118 | 24090205 | 5801 | 139.224 | 5.801 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 896056 | 1152 | 198.5865 | 100% | 0% | 100% | 100% | 100% | 0% | 11427295 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 126 | 24095276 | 5071 | 121.704 | 5.071 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 897110 | 1054 | 207.8486 | 0% | 0% | 100% | 100% | 100% | 30% | 11427410 | 115 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 118 | 24100462 | 5186 | 124.464 | 5.186 | 5.1 | 5.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 898182 | 1072 | 206.7104 | 0% | 0% | 100% | 100% | 100% | 30% | 11427736 | 326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133411 | 133.411 | 133.411 | [12 empty] | 26808 | 26808 | 200.943 | 0% | 0% | 0% | 0% | 0% |  | 2344 | 2344 | 1.165 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 04, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | G.SY / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-05 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26976 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24100462 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 898182 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11427736 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 112 | 24105542 | 5080 | 121.92 | 5.08 | 5.8 | 5.8 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 899252 | 1070 | 210.6299 | 0% | 0% | 100% | 100% | 100% | 70% | 11428239 | 503 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 111 | 24110409 | 4867 | 116.808 | 4.867 | 6.7 | 6.7 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 900227 | 975 | 200.3287 | 0% | 0% | 100% | 100% | 100% | 70% | 11428751 | 512 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 113 | 24114944 | 4535 | 108.84 | 4.535 | 7.8 | 7.8 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 901179 | 952 | 209.9228 | 0% | 0% | 100% | 100% | 100% | 70% | 11429259 | 508 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 163 | 116 | 24119357 | 4413 | 105.912 | 4.413 | 8.9 | 8.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 902176 | 997 | 225.9234 | 0% | 0% | 100% | 100% | 100% | 70% | 11429757 | 498 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 117 | 24123733 | 4376 | 105.024 | 4.376 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 903179 | 1003 | 229.2048 | 0% | 0% | 100% | 100% | 100% | 70% | 11429867 | 110 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 126 | 24128986 | 5253 | 126.072 | 5.253 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 904110 | 931 | 177.2321 | 0% | 0% | 100% | 100% | 100% | 0% | 11429867 | 0 | 1.2 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 141 | 24134548 | 5562 | 133.488 | 5.562 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 905136 | 1026 | 184.466 | 0% | 0% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Normal operation schedule | Power Interruption | PI
55:00 | 8:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 145 | 24141046 | 6498 | 155.952 | 6.498 | 9.3 | 9.3 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 906384 | 1248 | 192.0591 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Normal operation schedule | Water Interruption | WI
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 142 | 24147366 | 6320 | 151.68 | 6.32 | 8.6 | 8.6 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 907602 | 1218 | 192.7215 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 161 | 24154054 | 6688 | 160.512 | 6.688 | 7.7 | 7.7 | 3B+1S | 0 | 1098 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 908866 | 1264 | 188.9952 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 | 1.28
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 144 | 24160448 | 6394 | 153.456 | 6.394 | 7 | 7 | 3B+1S | 0 | 1087 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 910070 | 1204 | 188.3015 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 141 | 24167022 | 6574 | 157.776 | 6.574 | 6.2 | 6.2 | 3B+1S | 0 | 1088 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 911322 | 1252 | 190.4472 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 138 | 24173544 | 6522 | 156.528 | 6.522 | 5.5 | 5.5 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 912564 | 1242 | 190.4324 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 131 | 24179907 | 6363 | 152.712 | 6.363 | 4.9 | 4.9 | 3B+1S | 0 | 1028 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 913634 | 1070 | 168.1597 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 132 | 24186174 | 6267 | 150.408 | 6.267 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 914807 | 1173 | 187.1709 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 24192637 | 6463 | 155.112 | 6.463 | 4.2 | 4.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 915980 | 1173 | 181.4947 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 127 | 24198750 | 6113 | 146.712 | 6.113 | 3.7 | 3.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 917151 | 1171 | 191.559 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 130 | 24204625 | 5875 | 141 | 5.875 | 3.5 | 3.5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 918312 | 1161 | 197.617 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 131 | 24210517 | 5892 | 141.408 | 5.892 | 3.3 | 3.3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 919471 | 1159 | 196.7074 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 131 | 24216215 | 5698 | 136.752 | 5.698 | 3.1 | 3.1 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 920626 | 1155 | 202.7027 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 134 | 24222058 | 5843 | 140.232 | 5.843 | 2.8 | 2.8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 921791 | 1165 | 199.3839 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 127 | 127 | 24227979 | 5921 | 142.104 | 5.921 | 2.7 | 2.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 922984 | 1193 | 201.4862 | 0% | 100% | 100% | 100% | 100% | 0% | 11429867 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 121 | 24233127 | 5148 | 123.552 | 5.148 | 2.8 | 2.8 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 924119 | 1135 | 220.474 | 0% | 100% | 100% | 100% | 100% | 30% | 11429971 | 104 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 120 | 24238322 | 5195 | 124.68 | 5.195 | 3.2 | 3.2 | 3B |  | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 925158 | 1039 | 200 | 0% | 0% | 100% | 100% | 100% | 30% | 11430282 | 311 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 137860 | 137.86 | 137.86 | [12 empty] | 26976 | 26976 | 195.6768 | 0% | 0% | 0% | 0% | 0% |  | 2546 | 2546 | 1.2033 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 05, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | PAUL LABIAN / JEFF LAMAYO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-06 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26752 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24238322 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 925158 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11430282 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 140 | 110 | 24243483 | 5161 | 123.864 | 5.161 | 4.9 | 4.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 926164 | 1006 | 194.9235 | 0% | 0% | 100% | 100% | 100% | 70% | 11430807 | 525 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 111 | 24248244 | 4761 | 114.264 | 4.761 | 6.2 | 6.2 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 927163 | 999 | 209.8299 | 0% | 0% | 100% | 100% | 100% | 70% | 11431330 | 523 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 108 | 24252583 | 4339 | 104.136 | 4.339 | 7.8 | 7.8 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 928156 | 993 | 228.8546 | 0% | 0% | 100% | 100% | 100% | 70% | 11431857 | 527 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 167 | 116 | 24256701 | 4118 | 98.832 | 4.118 | 8.7 | 8.7 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 929181 | 1025 | 248.9072 | 0% | 0% | 100% | 100% | 100% | 70% | 11432369 | 512 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 117 | 114 | 24260795 | 4094 | 98.256 | 4.094 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 930204 | 1023 | 249.8779 | 0% | 0% | 100% | 100% | 100% | 70% | 11432517 | 148 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 129 | 129 | 24266356 | 5561 | 133.464 | 5.561 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1097 | N/A | N/A | N/A | N/A | 931192 | 988 | 177.6659 | 0% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 142 | 141 | 24271528 | 5172 | 124.128 | 5.172 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 932136 | 944 | 182.5213 | 0% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 143 | 24277878 | 6350 | 152.4 | 6.35 | 9.3 | 9.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 933414 | 1278 | 201.2598 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 160 | 24284066 | 6188 | 148.512 | 6.188 | 8.7 | 8.7 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 934586 | 1172 | 189.3988 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 167 | 24289898 | 5832 | 139.968 | 5.832 | 8.3 | 8.3 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 935708 | 1122 | 192.3868 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 | 1.19
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 142 | 24296208 | 6310 | 151.44 | 6.31 | 7.4 | 7.4 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 936984 | 1276 | 202.2187 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Normal operation schedule
59:00 | 12:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 135 | 24302146 | 5938 | 142.512 | 5.938 | 6.9 | 6.9 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 938140 | 1156 | 194.6783 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 155 | 24308334 | 6188 | 148.512 | 6.188 | 6.3 | 6.3 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 939388 | 1248 | 201.6807 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 136 | 24314324 | 5990 | 143.76 | 5.99 | 5.8 | 5.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 940556 | 1168 | 194.9917 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 133 | 140 | 24320356 | 6032 | 144.768 | 6.032 | 5.3 | 5.3 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 941740 | 1184 | 196.2865 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 138 | 24326906 | 6550 | 157.2 | 6.55 | 4.9 | 4.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 942968 | 1228 | 187.4809 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 135 | 24332718 | 5812 | 139.488 | 5.812 | 4.5 | 4.5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 944108 | 1140 | 196.1459 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 132 | 24338471 | 5753 | 138.072 | 5.753 | 4.2 | 4.2 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 945311 | 1203 | 209.1083 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 133 | 24344040 | 5569 | 133.656 | 5.569 | 3.9 | 3.9 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 946453 | 1142 | 205.0637 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 5 | 3.5211 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 129 | 24349588 | 5548 | 133.152 | 5.548 | 3.7 | 3.7 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 947625 | 1172 | 211.2473 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 124 | 24354879 | 5291 | 126.984 | 5.291 | 3.6 | 3.6 | 3B+1S | 1004 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 948752 | 1127 | 213.0032 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 125 | 122 | 24360277 | 5398 | 129.552 | 5.398 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 949901 | 1149 | 212.8566 | 100% | 0% | 100% | 100% | 100% | 0% | 11432517 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 112 | 24365369 | 5092 | 122.208 | 5.092 | 3.9 | 3.9 | 3B | 0 | 0 | 1148 | 1185 | 1147 | N/A | N/A | N/A | N/A | 950912 | 1011 | 198.5467 | 0% | 0% | 100% | 100% | 100% | 30% | 11432647 | 130 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 109 | 24370271 | 4902 | 117.648 | 4.902 | 4.5 | 4.5 | 3B |  | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 951910 | 998 | 203.5904 | 0% | 0% | 100% | 100% | 100% | 30% | 11433228 | 581 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131949 | 131.949 | 131.949 | [12 empty] | 26752 | 26752 | 202.745 | [6 empty] | 2946 | 2946 | 1.1617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 06, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | GLITTERS SY
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-07 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26707 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24370271 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 951910 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11433228 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 127 | 112 | 24374941 | 4670 | 112.08 | 4.67 | 5.3 | 5.3 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 952880 | 970 | 207.7088 | 0% | 0% | 100% | 100% | 100% | 70% | 11433834 | 606 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 107 | 24379552 | 4611 | 110.664 | 4.611 | 6.1 | 6.1 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 953854 | 974 | 211.234 | 0% | 0% | 100% | 100% | 100% | 70% | 11434415 | 581 | 1.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 106 | 24384079 | 4527 | 108.648 | 4.527 | 7.6 | 7.6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 954793 | 939 | 207.4221 | 0% | 0% | 100% | 100% | 100% | 70% | 11434981 | 566 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 112 | 24388575 | 4496 | 107.904 | 4.496 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 955847 | 1054 | 234.4306 | 0% | 0% | 100% | 100% | 100% | 70% | 11435614 | 633 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 122 | 24393057 | 4482 | 107.568 | 4.482 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 956898 | 1051 | 234.4935 | 0% | 0% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 127 | 24398468 | 5411 | 129.864 | 5.411 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 957888 | 990 | 182.9606 | 0% | 0% | 100% | 100% | 100% | 0% | 11435614 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 140 | 24404608 | 6140 | 147.36 | 6.14 | 9.2 | 9.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 959126 | 1238 | 201.6287 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 144 | 24411047 | 6439 | 154.536 | 6.439 | 8.6 | 8.6 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 960419 | 1293 | 200.8076 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 139 | 24417032 | 5985 | 143.64 | 5.985 | 7.9 | 7.9 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 961611 | 1192 | 199.1646 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 144 | 24423046 | 6014 | 144.336 | 6.014 | 7.2 | 7.2 | 3B+1S | 0 | 1072 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 962768 | 1157 | 192.3844 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 139 | 24428588 | 5542 | 133.008 | 5.542 | 6.6 | 6.6 | 3B+1S | 0 | 1077 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 963874 | 1106 | 199.5669 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 148 | 24434644 | 6056 | 145.344 | 6.056 | 6 | 6 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 965096 | 1222 | 201.7834 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 124 | 24441102 | 6458 | 154.992 | 6.458 | 5.4 | 5.4 | 3B+1S | 0 | 1072 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 966366 | 1270 | 196.6553 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 126 | 130 | 24446506 | 5404 | 129.696 | 5.404 | 4.8 | 4.8 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 967544 | 1178 | 217.9867 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 132 | 24452074 | 5568 | 133.632 | 5.568 | 4.5 | 4.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 968708 | 1164 | 209.0517 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 133 | 24457488 | 5414 | 129.936 | 5.414 | 4.4 | 4.4 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 969798 | 1090 | 201.3299 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 125 | 24463182 | 5694 | 136.656 | 5.694 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 970922 | 1124 | 197.4008 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 125 | 24468448 | 5266 | 126.384 | 5.266 | 4 | 4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 971967 | 1045 | 198.4428 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 130 | 24473832 | 5384 | 129.216 | 5.384 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 973121 | 1154 | 214.3388 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 127 | 24479398 | 5566 | 133.584 | 5.566 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 974271 | 1150 | 206.6116 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 127 | 24484942 | 5544 | 133.056 | 5.544 | 3.4 | 3.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 975427 | 1156 | 208.5137 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 130 | 125 | 24490420 | 5478 | 131.472 | 5.478 | 3.2 | 3.2 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 976581 | 1154 | 210.6608 | 0% | 100% | 100% | 100% | 100% | 0% | 11435614 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 116 | 24495564 | 5144 | 123.456 | 5.144 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1147 | N/A | N/A | N/A | N/A | 977638 | 1057 | 205.4821 | 0% | 0% | 100% | 100% | 100% | 20% | 11435665 | 51 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 108 | 24500269 | 4705 | 112.92 | 4.705 | 3.9 | 3.9 | 3B | 0 | 0 | 1167 | 1185 | 1096 | N/A | N/A | N/A | N/A | 978617 | 979 | 208.0765 | 0% | 0% | 100% | 100% | 100% | 20% | 11436329 | 664 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129998 | 129.998 | 129.998 | [12 empty] | 26707 | 26707 | 205.4416 | 0% | 0% | 0% | 0% | 0% |  | 3101 | 3101 | 1.3117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:45 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 07, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
POWER INTERRUPTION AT 3:56PM
ALL PUMP STOPPED DUE TO INTERRUPTION @ 3:56PM / GENSET I OPERATED
MERALCO POWER RESUME @ 4:00PM
BP2 POWER RESUME @ 3:58PM
BP3 POWER RESUME @ 4:00PM
BP1 POWER RESUME @ 4:02PM
SP2 POWER RESUME @ 4:04PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE

## NOV 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-08 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26991 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24500269 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 978617 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11436329 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 109 | 24504659 | 4390 | 105.36 | 4.39 | 5.1 | 5.1 | 3B | 0 | 0 | 1146 | 1185 | 1097 | N/A | N/A | N/A | N/A | 979520 | 903 | 205.6948 | 0% | 0% | 100% | 100% | 100% | 75% | 11437200 | 871 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 105 | 24509014 | 4355 | 104.52 | 4.355 | 7 | 7 | 3B | 0 | 0 | 1146 | 1185 | 1097 | N/A | N/A | N/A | N/A | 980470 | 950 | 218.1401 | 0% | 0% | 100% | 100% | 100% | 75% | 11438000 | 800 | 1.7 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 139 | 106 | 24513499 | 4485 | 107.64 | 4.485 | 8.8 | 8.8 | 3B | 0 | 0 | 1146 | 1185 | 1097 | N/A | N/A | N/A | N/A | 981479 | 1009 | 224.9721 | 0% | 0% | 100% | 100% | 100% | 75% | 11438804 | 804 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 | 114 | 24518043 | 4544 | 109.056 | 4.544 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1097 | N/A | N/A | N/A | N/A | 982478 | 999 | 219.8504 | 0% | 0% | 100% | 100% | 100% | 75% | 11439092 | 288 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 118 | 24522723 | 4680 | 112.32 | 4.68 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 1185 | 1097 | N/A | N/A | N/A | N/A | 983483 | 1005 | 214.7436 | 0% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 139 | 24529212 | 6489 | 155.736 | 6.489 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 984680 | 1197 | 184.466 | 0% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 | 1.12 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 140 | 24535144 | 5932 | 142.368 | 5.932 | 9 | 9 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 985866 | 1186 | 199.9326 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 154 | 24541088 | 5944 | 142.656 | 5.944 | 8.4 | 8.4 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 987054 | 1188 | 199.8654 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 164 | 24547146 | 6058 | 145.392 | 6.058 | 7.7 | 7.7 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 988246 | 1192 | 196.7646 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 173 | 24553394 | 6248 | 149.952 | 6.248 | 7.1 | 7.1 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 989492 | 1246 | 199.4238 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 138 | 24559698 | 6304 | 151.296 | 6.304 | 6.5 | 6.5 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 990638 | 1146 | 181.7893 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 135 | 24566298 | 6600 | 158.4 | 6.6 | 5.8 | 5.8 | 3B+1S | 1056 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 991918 | 1280 | 193.9394 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 143 | 24572096 | 5798 | 139.152 | 5.798 | 5.3 | 5.3 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 993072 | 1154 | 199.0341 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 137 | 24578284 | 6188 | 148.512 | 6.188 | 4.8 | 4.8 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 994332 | 1260 | 203.6199 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 133 | 24583842 | 5558 | 133.392 | 5.558 | 4.5 | 4.5 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 995490 | 1158 | 208.3483 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 135 | 24589604 | 5762 | 138.288 | 5.762 | 4.3 | 4.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 996624 | 1134 | 196.8067 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 134 | 24595206 | 5602 | 134.448 | 5.602 | 4 | 4 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 997796 | 1172 | 209.211 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 129 | 24600832 | 5626 | 135.024 | 5.626 | 3.7 | 3.7 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 998942 | 1146 | 203.6971 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 140 | 24606399 | 5567 | 133.608 | 5.567 | 3.5 | 3.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1000100 | 1158 | 208.0115 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 126 | 24611893 | 5494 | 131.856 | 5.494 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1001259 | 1159 | 210.9574 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 132 | 125 | 24617293 | 5400 | 129.6 | 5.4 | 3.2 | 3.2 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1002409 | 1150 | 212.963 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 124 | 24622735 | 5442 | 130.608 | 5.442 | 3 | 3 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1003547 | 1138 | 209.1143 | 100% | 0% | 100% | 100% | 100% | 0% | 11439092 | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 128 | 118 | 24627991 | 5256 | 126.144 | 5.256 | 3.3 | 3.3 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1004587 | 1040 | 197.8691 | 0% | 0% | 100% | 100% | 100% | 30% | 11439213 | 121 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 117 | 24632965 | 4974 | 119.376 | 4.974 | 3.7 | 3.7 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1005608 | 1021 | 205.2674 | 0% | 0% | 100% | 100% | 100% | 30% | 11439550 | 337 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132696 | 132.696 | 132.696 | [12 empty] | 26991 | 26991 | 203.4048 | 0% | 0% | 0% | 0% | 0% |  | 3221 | 3221 | 1.19 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 08, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS / JEFF LAMAYO
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-09 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27173 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24632965 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1005608 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11439550 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 113 | 24638022 | 5057 | 121.368 | 5.057 | 5.4 | 5.4 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1006662 | 1054 | 208.424 | 0% | 0% | 100% | 100% | 100% | 70% | 11440149 | 599 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 113 | 24642883 | 4861 | 116.664 | 4.861 | 6.9 | 6.9 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1007669 | 1007 | 207.159 | 0% | 0% | 100% | 100% | 100% | 70% | 11440756 | 607 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 109 | 24647654 | 4771 | 114.504 | 4.771 | 8.4 | 8.4 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1008679 | 1010 | 211.6957 | 0% | 0% | 100% | 100% | 100% | 70% | 11441358 | 602 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 158 | 116 | 24652209 | 4555 | 109.32 | 4.555 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1009729 | 1050 | 230.5159 | 0% | 0% | 100% | 100% | 100% | 70% | 11441569 | 211 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 | 120 | 24656987 | 4778 | 114.672 | 4.778 | 9.5 | 9.5 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1010793 | 1064 | 222.6873 | 0% | 0% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 129 | 135 | 24661678 | 4691 | 112.584 | 4.691 | 9.5 | 9.5 | 3B+1S | 0 | 995 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1011868 | 1075 | 229.1622 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 141 | 24668028 | 6350 | 152.4 | 6.35 | 9 | 9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1013108 | 1240 | 195.2756 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 147 | 24674256 | 6228 | 149.472 | 6.228 | 8.6 | 8.6 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1014324 | 1216 | 195.2473 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 141 | 24680428 | 6172 | 148.128 | 6.172 | 8 | 8 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1015552 | 1228 | 198.9631 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 138 | 138 | 24686488 | 6060 | 145.44 | 6.06 | 7.5 | 7.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1016732 | 1180 | 194.7195 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 | 1.19 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 123 | 24692346 | 5858 | 140.592 | 5.858 | 7 | 7 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1017900 | 1168 | 199.3855 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 143 | 24698164 | 5818 | 139.632 | 5.818 | 6.5 | 6.5 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1019066 | 1166 | 200.4125 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 131 | 24704522 | 6358 | 152.592 | 6.358 | 6 | 6 | 3B+1S | 0 | 1035 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1020328 | 1262 | 198.4901 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 133 | 24710199 | 5677 | 136.248 | 5.677 | 5.6 | 5.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1021485 | 1157 | 203.8048 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 134 | 141 | 24715839 | 5640 | 135.36 | 5.64 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1022634 | 1149 | 203.7234 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 24721529 | 5690 | 136.56 | 5.69 | 5.3 | 5.3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1023792 | 1158 | 203.5149 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 135 | 24727506 | 5977 | 143.448 | 5.977 | 5.1 | 5.1 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1024961 | 1169 | 195.5831 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 121 | 24733466 | 5960 | 143.04 | 5.96 | 4.9 | 4.9 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1026128 | 1167 | 195.8054 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 127 | 24739399 | 5933 | 142.392 | 5.933 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1027290 | 1162 | 195.8537 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 122 | 24745530 | 6131 | 147.144 | 6.131 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1028450 | 1160 | 189.2024 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 134 | 24751435 | 5905 | 141.72 | 5.905 | 4.1 | 4.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1029608 | 1158 | 196.105 | 0% | 100% | 100% | 100% | 100% | 0% | 11441569 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 123 | 126 | 24757087 | 5652 | 135.648 | 5.652 | 3.9 | 3.9 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1030760 | 1152 | 203.8217 | 0% | 0% | 100% | 100% | 100% | 0% | 11441569 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 117 | 24762193 | 5106 | 122.544 | 5.106 | 3.9 | 3.9 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1031788 | 1028 | 201.3318 | 0% | 0% | 100% | 100% | 100% | 30% | 11441828 | 259 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 112 | 24766971 | 4778 | 114.672 | 4.778 | 4.5 | 4.5 |  | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1032781 | 993 | 207.8275 | 0% | 0% | 100% | 100% | 100% | 30% | 11442098 | 270 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134006 | 134.006 | 134.006 | [12 empty] | 27173 | 27173 | 202.7745 | 0% | 0% | 0% | 0% | 0% |  | 2548 | 2548 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 5:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 09, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | G.SY / RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | G.SY / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-10 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26700 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24766971 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1032781 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11442098 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 106 | 24771710 | 4739 | 113.736 | 4.739 | 5.7 | 5.7 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1033763 | 982 | 207.2167 | 0% | 0% | 100% | 100% | 100% | 70% | 11442702 | 604 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 107 | 24776287 | 4577 | 109.848 | 4.577 | 7.2 | 7.2 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1034706 | 943 | 206.0302 | 0% | 0% | 100% | 100% | 100% | 70% | 11443309 | 607 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 122 | 108 | 24780703 | 4416 | 105.984 | 4.416 | 8.6 | 8.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1035630 | 924 | 209.2391 | 0% | 0% | 100% | 100% | 100% | 70% | 11443910 | 601 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 157 | 110 | 24784912 | 4209 | 101.016 | 4.209 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1036668 | 1038 | 246.6144 | 0% | 0% | 100% | 100% | 100% | 70% | 11444225 | 315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 137 | 24789764 | 4852 | 116.448 | 4.852 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1037723 | 1055 | 217.4361 | 0% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 126 | 24795150 | 5386 | 129.264 | 5.386 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1038684 | 961 | 178.4255 | 0% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 | 1.03 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 24801384 | 6234 | 149.616 | 6.234 | 9.1 | 9.1 | 3B+1S | 1006 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1039872 | 1188 | 190.5679 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 136 | 135 | 24807744 | 6360 | 152.64 | 6.36 | 8.7 | 8.7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1041070 | 1198 | 188.3648 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 139 | 24814194 | 6450 | 154.8 | 6.45 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1042270 | 1200 | 186.0465 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Normal operation schedule | Equipment Maintenance | EM
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 136 | 24820487 | 6293 | 151.032 | 6.293 | 7.7 | 7.7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1043469 | 1199 | 190.5292 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 | 1.13 | Normal operation schedule
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 138 | 24826625 | 6138 | 147.312 | 6.138 | 7.4 | 7.4 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1044656 | 1187 | 193.3855 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 133 | 24832594 | 5969 | 143.256 | 5.969 | 7 | 7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1045834 | 1178 | 197.353 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 133 | 24838604 | 6010 | 144.24 | 6.01 | 6.7 | 6.7 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1047001 | 1167 | 194.1764 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 130 | 24844611 | 6007 | 144.168 | 6.007 | 6.4 | 6.4 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1048162 | 1161 | 193.2745 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 132 | 24850284 | 5673 | 136.152 | 5.673 | 6.1 | 6.1 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1049319 | 1157 | 203.9485 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 24856061 | 5777 | 138.648 | 5.777 | 5.9 | 5.9 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1050486 | 1167 | 202.008 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 129 | 24861903 | 5842 | 140.208 | 5.842 | 5.6 | 5.6 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1051600 | 1114 | 190.6881 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 131 | 24867762 | 5859 | 140.616 | 5.859 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1052770 | 1170 | 199.6928 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 134 | 24874027 | 6265 | 150.36 | 6.265 | 5 | 5 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1053935 | 1165 | 185.9537 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 125 | 125 | 24880057 | 6030 | 144.72 | 6.03 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1156 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1055046 | 1111 | 184.2454 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 126 | 124 | 24885699 | 5642 | 135.408 | 5.642 | 4.4 | 4.4 | 3B+1S | 1024 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1056199 | 1153 | 204.3602 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 127 | 24891426 | 5727 | 137.448 | 5.727 | 4.3 | 4.3 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1057366 | 1167 | 203.7716 | 100% | 0% | 100% | 100% | 100% | 0% | 11444225 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 126 | 115 | 24896731 | 5305 | 127.32 | 5.305 | 4.5 | 4.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1058460 | 1094 | 206.2205 | 0% | 0% | 100% | 100% | 100% | 30% | 11444332 | 107 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 110 | 24901776 | 5045 | 121.08 | 5.045 | 4.1 | 4.1 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1059481 | 1021 | 202.3786 | 0% | 0% | 100% | 100% | 100% | 30% | 11444635 | 303 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134805 | 134.805 | 134.805 | [12 empty] | 26700 | 26700 | 198.0639 | 0% | 0% | 0% | 0% | 0% |  | 2537 | 2537 | 1.1183 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:46 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 10, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | G.SY / RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN /GLITTERS SY
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-11 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26747 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 24901776 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1059481 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11444635 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 125 | 112 | 24906572 | 4796 | 115.104 | 4.796 | 5.8 | 5.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1060467 | 986 | 205.588 | 0% | 0% | 100% | 100% | 100% | 70% | 11445141 | 506 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 110 | 24911190 | 4618 | 110.832 | 4.618 | 7.3 | 7.3 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1061453 | 986 | 213.5123 | 0% | 0% | 100% | 100% | 100% | 70% | 11445656 | 515 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 120 | 111 | 24915772 | 4582 | 109.968 | 4.582 | 8.3 | 8.3 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1062411 | 958 | 209.079 | 0% | 0% | 100% | 100% | 100% | 70% | 11446075 | 419 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 116 | 24919940 | 4168 | 100.032 | 4.168 | 9.2 | 9.2 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1063444 | 1033 | 247.8407 | 0% | 0% | 100% | 100% | 100% | 70% | 11446338 | 263 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 | 124 | 24924273 | 4333 | 103.992 | 4.333 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 1064494 | 1050 | 242.3263 | 0% | 0% | 100% | 100% | 100% | 70% | 11446434 | 96 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 131 | 24929741 | 5468 | 131.232 | 5.468 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1065552 | 1058 | 193.4894 | 0% | 0% | 100% | 100% | 100% | 0% | 11446434 | 0 | 1.15 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 145 | 24935279 | 5538 | 132.912 | 5.538 | 9.1 | 9.1 | 3B+1S | 0 | 1006 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1066623 | 1071 | 193.3911 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 139 | 24941647 | 6368 | 152.832 | 6.368 | 8.6 | 8.6 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1067823 | 1200 | 188.4422 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 141 | 24948111 | 6464 | 155.136 | 6.464 | 8.1 | 8.1 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1069014 | 1191 | 184.2512 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 145 | 24954492 | 6381 | 153.144 | 6.381 | 7.6 | 7.6 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1070215 | 1201 | 188.215 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 | 1.02 | Normal operation schedule
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 133 | 24960578 | 6086 | 146.064 | 6.086 | 7.2 | 7.2 | 3B+1S | 0 | 1016 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1071394 | 1179 | 193.7233 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 137 | 24966765 | 6187 | 148.488 | 6.187 | 6.8 | 6.8 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1072580 | 1186 | 191.6923 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 121 | 24973200 | 6435 | 154.44 | 6.435 | 6.3 | 6.3 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1073765 | 1185 | 184.1492 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 128 | 24979487 | 6287 | 150.888 | 6.287 | 6 | 6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1074995 | 1230 | 195.6418 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 135 | 133 | 24985560 | 6073 | 145.752 | 6.073 | 5.9 | 5.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1076198 | 1203 | 198.0899 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 131 | 24991332 | 5772 | 138.528 | 5.772 | 5.7 | 5.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1077360 | 1162 | 201.3167 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 129 | 24997061 | 5729 | 137.496 | 5.729 | 5.6 | 5.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1078516 | 1156 | 201.7804 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 123 | 25003318 | 6257 | 150.168 | 6.257 | 5.3 | 5.3 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1079674 | 1158 | 185.0727 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 134 | 25009260 | 5942 | 142.608 | 5.942 | 5.1 | 5.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1080833 | 1159 | 195.0522 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 130 | 25015170 | 5910 | 141.84 | 5.91 | 4.9 | 4.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1081988 | 1155 | 195.4315 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 126 | 116 | 25020867 | 5697 | 136.728 | 5.697 | 4.6 | 4.6 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1083145 | 1157 | 203.0893 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 122 | 120 | 25026147 | 5280 | 126.72 | 5.28 | 4.4 | 4.4 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1084231 | 1086 | 205.6818 | 0% | 100% | 100% | 100% | 100% | 0% | 11446434 | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 121 | 117 | 25031195 | 5048 | 121.152 | 5.048 | 4.4 | 4.4 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1085237 | 1006 | 199.2868 | 0% | 0% | 100% | 100% | 100% | 30% | 11446563 | 129 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 129 | 110 | 25036101 | 4906 | 117.744 | 4.906 | 4.7 | 4.7 | 3B | 0 | 0 | 1136 | 1185 | 1136 | N/A | N/A | N/A | N/A | 1086228 | 991 | 201.9976 | 0% | 0% | 100% | 100% | 100% | 30% | 11446817 | 254 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134325 | 134.325 | 134.325 | [12 empty] | 26747 | 26747 | 199.1215 | 0% | 0% | 0% | 0% | 0% |  | 2182 | 2182 | 1.165 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:15 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 11, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | G.SY / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-12 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26705 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25036101 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1086228 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11446817 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 128 | 111 | 25040841 | 4740 | 113.76 | 4.74 | 5.8 | 5.8 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1087187 | 959 | 202.3207 | 0% | 0% | 100% | 100% | 100% | 70% | 11447238 | 421 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 126 | 104 | 25045495 | 4654 | 111.696 | 4.654 | 6.9 | 6.9 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1088151 | 964 | 207.1336 | 0% | 0% | 100% | 100% | 100% | 70% | 11447658 | 420 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 118 | 106 | 25049992 | 4497 | 107.928 | 4.497 | 8.2 | 8.2 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1089055 | 904 | 201.0229 | 0% | 0% | 100% | 100% | 100% | 70% | 11448063 | 405 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 | 112 | 25054214 | 4222 | 101.328 | 4.222 | 9.5 | 9.5 | 3B | 0 | 0 | 1128 | 1128 | 1128 | N/A | N/A | N/A | N/A | 1090062 | 1007 | 238.5126 | 0% | 0% | 100% | 100% | 100% | 70% | 11448469 | 406 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 117 | 25058290 | 4076 | 97.824 | 4.076 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 1091042 | 980 | 240.4318 | 0% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 133 | 25063392 | 5102 | 122.448 | 5.102 | 9.5 | 9.5 | 3B | 0 | 0 | 1168 | 1185 | 1168 | N/A | N/A | N/A | N/A | 1092072 | 1030 | 201.8816 | 0% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 | 1.1 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 143 | 140 | 25069022 | 5630 | 135.12 | 5.63 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1093044 | 972 | 172.6465 | 0% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 106 | 25075502 | 6480 | 155.52 | 6.48 | 9.2 | 9.2 | 3B+1S | 1038 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1094326 | 1282 | 197.8395 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 147 | 25081974 | 6472 | 155.328 | 6.472 | 8.5 | 8.5 | 3B+1S | 1038 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1095624 | 1298 | 200.5562 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 177 | 25088602 | 6628 | 159.072 | 6.628 | 8.1 | 8.1 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1096860 | 1236 | 186.4816 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 | 1.16 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 160 | 25095566 | 6964 | 167.136 | 6.964 | 7.5 | 7.5 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1097996 | 1136 | 163.1246 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 154 | 25102546 | 6980 | 167.52 | 6.98 | 6.8 | 6.8 | 3B+1S | 1056 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1099142 | 1146 | 164.1834 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 186 | 25109534 | 6988 | 167.712 | 6.988 | 6.2 | 6.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1100320 | 1178 | 168.5747 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 130 | 25116334 | 6800 | 163.2 | 6.8 | 5.7 | 5.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1101442 | 1122 | 165 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 150 | 25123089 | 6755 | 162.12 | 6.755 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1102610 | 1168 | 172.909 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 136 | 25129909 | 6820 | 163.68 | 6.82 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1103784 | 1174 | 172.1408 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 130 | 25136810 | 6901 | 165.624 | 6.901 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1104967 | 1183 | 171.4244 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 132 | 25143665 | 6855 | 164.52 | 6.855 | 4.5 | 4.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1106135 | 1168 | 170.3866 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 | 1.27 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 137 | 135 | 25150295 | 6630 | 159.12 | 6.63 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1107299 | 1164 | 175.5656 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 138 | 25156855 | 6560 | 157.44 | 6.56 | 3.9 | 3.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1108457 | 1158 | 176.5244 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 134 | 25162961 | 6106 | 146.544 | 6.106 | 3.6 | 3.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1109624 | 1167 | 191.1235 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 127 | 25169122 | 6161 | 147.864 | 6.161 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1110800 | 1176 | 190.8781 | 100% | 0% | 100% | 100% | 100% | 0% | 11448469 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 116 | 25174413 | 5291 | 126.984 | 5.291 | 3.6 | 3.6 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1111920 | 1120 | 211.6802 | 0% | 0% | 100% | 100% | 100% | 30% | 11448582 | 113 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 126 | 114 | 25179384 | 4971 | 119.304 | 4.971 | 4 | 4 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1112933 | 1013 | 203.7819 | 0% | 0% | 100% | 100% | 100% | 30% | 11448884 | 302 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 143283 | 143.283 | 143.283 | [12 empty] | 26705 | 26705 | 186.3794 | 0% | 0% | 0% | 0% | 0% |  | 2067 | 2067 | 1.1333 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:02 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 12, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | PAUL LABIAN / JEFF LAMAYO
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-13 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26539 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25179384 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1112933 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11448884 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 131 | 116 | 25184255 | 4871 | 116.904 | 4.871 | 5.3 | 5.3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1113926 | 993 | 203.8596 | 0% | 0% | 100% | 100% | 100% | 70% | 11449389 | 505 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 109 | 25189012 | 4757 | 114.168 | 4.757 | 6.7 | 6.7 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1114899 | 973 | 204.5407 | 0% | 0% | 100% | 100% | 100% | 70% | 11449919 | 530 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 108 | 25193725 | 4713 | 113.112 | 4.713 | 7.9 | 7.9 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1115875 | 976 | 207.0868 | 0% | 0% | 100% | 100% | 100% | 70% | 11450339 | 420 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 | 114 | 25197776 | 4051 | 97.224 | 4.051 | 9.2 | 9.2 | 3B | 0 | 0 | 1127 | 1185 | 1128 | N/A | N/A | N/A | N/A | 1116876 | 1001 | 247.0995 | 0% | 0% | 100% | 100% | 100% | 70% | 11450778 | 439 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 114 | 25201883 | 4107 | 98.568 | 4.107 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1117891 | 1015 | 247.139 | 0% | 0% | 100% | 100% | 100% | 70% | 11450881 | 103 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 125 | 123 | 25207112 | 5229 | 125.496 | 5.229 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1117 | N/A | N/A | N/A | N/A | 1118844 | 953 | 182.2528 | 0% | 0% | 100% | 100% | 100% | 0% | 11450881 | 0 | 1.16 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 136 | 127 | 25212518 | 5406 | 129.744 | 5.406 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1119856 | 1012 | 187.1994 | 0% | 0% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 135 | 135 | 25218524 | 6006 | 144.144 | 6.006 | 9.3 | 9.3 | 3B+1S | 0 | 994 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1121064 | 1208 | 201.1322 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 140 | 25224586 | 6062 | 145.488 | 6.062 | 8.9 | 8.9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1122228 | 1164 | 192.0158 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 25230704 | 6118 | 146.832 | 6.118 | 8.3 | 8.3 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1123460 | 1232 | 201.373 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 | 1.18 | Normal operation schedule
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 135 | 25236248 | 5544 | 133.056 | 5.544 | 7.7 | 7.7 | 3B+1S | 0 | 1047 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1124592 | 1132 | 204.1847 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 204 | 25242754 | 6506 | 156.144 | 6.506 | 7.1 | 7.1 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1125858 | 1266 | 194.5896 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 195 | 25249698 | 6944 | 166.656 | 6.944 | 6.5 | 6.5 | 3B+1S | 0 | 1066 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1127020 | 1162 | 167.3387 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 125 | 123 | 25256366 | 6668 | 160.032 | 6.668 | 5.9 | 5.9 | 3B+1S | 0 | 1056 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1128222 | 1202 | 180.2639 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 145 | 25262524 | 6158 | 147.792 | 6.158 | 5.4 | 5.4 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1129440 | 1218 | 197.7915 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 165 | 25268246 | 5722 | 137.328 | 5.722 | 5.1 | 5.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1130570 | 1130 | 197.4834 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 137 | 25273894 | 5648 | 135.552 | 5.648 | 4.7 | 4.7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1131714 | 1144 | 202.5496 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 25279919 | 6025 | 144.6 | 6.025 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1132889 | 1175 | 195.0207 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 121 | 25285864 | 5945 | 142.68 | 5.945 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1134067 | 1178 | 198.1497 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 | 124 | 25291777 | 5913 | 141.912 | 5.913 | 4 | 4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1135236 | 1169 | 197.7 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 129 | 25297215 | 5438 | 130.512 | 5.438 | 3.9 | 3.9 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1136367 | 1131 | 207.9809 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 116 | 125 | 25302531 | 5316 | 127.584 | 5.316 | 3.8 | 3.8 | 3B+1S | 0 | 1014 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1137483 | 1116 | 209.9323 | 0% | 100% | 100% | 100% | 100% | 0% | 11450881 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 114 | 25307538 | 5007 | 120.168 | 5.007 | 4.2 | 4.2 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1138485 | 1002 | 200.1198 | 0% | 0% | 100% | 100% | 100% | 30% | 11451052 | 171 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 109 | 25312262 | 4724 | 113.376 | 4.724 | 4.7 | 4.7 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1139472 | 987 | 208.9331 | 0% | 0% | 100% | 100% | 100% | 3% | 11451440 | 388 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132878 | 132.878 | 132.878 | [12 empty] | 26539 | 26539 | 199.7246 | 0% | 0% | 0% | 0% | 0% |  | 2556 | 2556 | 1.1533 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 13, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | G.SY / A. DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-14 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26700 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25312262 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1139472 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11451440 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 113 | 25316919 | 4657 | 111.768 | 4.657 | 5.9 | 5.9 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1140469 | 997 | 214.0863 | 0% | 0% | 100% | 100% | 100% | 70% | 11452028 | 588 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 | 108 | 25321455 | 4536 | 108.864 | 4.536 | 7.2 | 7.2 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1141414 | 945 | 208.3333 | 0% | 0% | 100% | 100% | 100% | 70% | 11452624 | 596 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 114 | 105 | 25325876 | 4421 | 106.104 | 4.421 | 8.5 | 8.5 | 3B | 0 | 0 | 1105 | 1185 | 1105 | N/A | N/A | N/A | N/A | 1142340 | 926 | 209.4549 | 0% | 0% | 100% | 100% | 100% | 70% | 11453189 | 565 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 | 109 | 25330232 | 4356 | 104.544 | 4.356 | 9.5 | 9.5 | 3B | 0 | 0 | 1115 | 1185 | 1115 | N/A | N/A | N/A | N/A | 1143326 | 986 | 226.3545 | 0% | 0% | 100% | 100% | 100% | 70% | 11453679 | 490 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 123 | 25334662 | 4430 | 106.32 | 4.43 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1144341 | 1015 | 229.1196 | 0% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 140 | 131 | 25340200 | 5538 | 132.912 | 5.538 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1145432 | 1091 | 197.0025 | 0% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 148 | 25346148 | 5948 | 142.752 | 5.948 | 9.2 | 9.2 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1146620 | 1188 | 199.731 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 25351776 | 5628 | 135.072 | 5.628 | 8.7 | 8.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1147744 | 1124 | 199.7157 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 135 | 154 | 25358614 | 6838 | 164.112 | 6.838 | 8.1 | 8.1 | 3B+1S | 1037 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1149034 | 1290 | 188.6517 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 143 | 25364562 | 5948 | 142.752 | 5.948 | 7.6 | 7.6 | 3B+1S | 1037 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1150196 | 1162 | 195.3598 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 | 1.19 | Normal operation schedule |  |  | G.SY / A. DIONELA
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 136 | 137 | 25370702 | 6140 | 147.36 | 6.14 | 7.2 | 7.2 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1151374 | 1178 | 191.8567 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Normal operation schedule
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 138 | 25377346 | 6644 | 159.456 | 6.644 | 6.6 | 6.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1152580 | 1206 | 181.5172 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 132 | 25384094 | 6748 | 161.952 | 6.748 | 6.2 | 6.2 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1153760 | 1180 | 174.8666 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 134 | 25389866 | 5772 | 138.528 | 5.772 | 5.8 | 5.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1154898 | 1138 | 197.1587 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 138 | 25396086 | 6220 | 149.28 | 6.22 | 5.4 | 5.4 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1156142 | 1244 | 200 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 123 | 25401968 | 5882 | 141.168 | 5.882 | 5.2 | 5.2 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1157324 | 1182 | 200.9521 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 131 | 25407714 | 5746 | 137.904 | 5.746 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1158426 | 1102 | 191.7856 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 127 | 25413530 | 5816 | 139.584 | 5.816 | 4.7 | 4.7 | 3B+1S | 1004 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1159527 | 1101 | 189.3054 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 128 | 25419597 | 6067 | 145.608 | 6.067 | 4.5 | 4.5 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1160668 | 1141 | 188.0666 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 127 | 25425612 | 6015 | 144.36 | 6.015 | 4.1 | 4.1 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1161833 | 1165 | 193.6825 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 121 | 25431447 | 5835 | 140.04 | 5.835 | 3.7 | 3.7 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1163000 | 1167 | 200 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 129 | 25437051 | 5604 | 134.496 | 5.604 | 3.4 | 3.4 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1164155 | 1155 | 206.1028 | 100% | 0% | 100% | 100% | 100% | 0% | 11453679 | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 119 | 117 | 25442136 | 5085 | 122.04 | 5.085 | 3.5 | 3.5 | 3B | 0 | 0 | 1186 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1165196 | 1041 | 204.7198 | 0% | 0% | 100% | 100% | 100% | 20% | 11453734 | 55 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 103 | 25446956 | 4820 | 115.68 | 4.82 | 4 | 4 | 3B | 0 | 0 | 1147 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1166172 | 976 | 202.4896 | 0% | 0% | 100% | 100% | 100% | 20% | 11454322 | 588 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134694 | 134.694 | 134.694 | [13 empty] | 26700 | 198.2271 | 0% | 0% | 0% | 0% | 0% |  | 2882 | 2882 | 1.1517 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 14, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## NOV 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-15 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24626 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25446956 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1166172 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11454322 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 109 | 25451124 | 4168 | 100.032 | 4.168 | 6.1 | 6.1 | 3B | 0 | 0 | 1126 | 1185 | 1116 | N/A | N/A | N/A | N/A | 1167073 | 901 | 216.1708 | 0% | 0% | 100% | 100% | 100% | 75% | 11454973 | 651 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 134 | 112 | 25455314 | 4190 | 100.56 | 4.19 | 7.5 | 7.5 | 3B | 0 | 0 | 1126 | 1185 | 1116 | N/A | N/A | N/A | N/A | 1167983 | 910 | 217.1838 | 0% | 0% | 100% | 100% | 100% | 75% | 11455493 | 520 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 104 | 25459574 | 4260 | 102.24 | 4.26 | 8.7 | 8.7 | 3B | 0 | 0 | 1126 | 1185 | 1116 | N/A | N/A | N/A | N/A | 1168933 | 950 | 223.0047 | 0% | 0% | 100% | 100% | 100% | 75% | 11456079 | 586 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 129 | 111 | 25463891 | 4317 | 103.608 | 4.317 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1045 | N/A | N/A | N/A | N/A | 1169895 | 962 | 222.8399 | 0% | 0% | 100% | 100% | 100% | 75% | 11456577 | 498 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 | 119 | 25468297 | 4406 | 105.744 | 4.406 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1170927 | 1032 | 234.2261 | 0% | 0% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 126 | 25474518 | 6221 | 149.304 | 6.221 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1156 | N/A | N/A | N/A | N/A | 1172092 | 1165 | 187.2689 | 0% | 0% | 100% | 100% | 100% | 0% | 11456577 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 130 | 143 | 25479998 | 5480 | 131.52 | 5.48 | 9.2 | 9.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1173208 | 1116 | 203.6496 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 138 | 25486386 | 6388 | 153.312 | 6.388 | 8.5 | 8.5 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1174416 | 1208 | 189.1046 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 131 | 140 | 25492546 | 6160 | 147.84 | 6.16 | 7.9 | 7.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1175674 | 1258 | 204.2208 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 141 | 25498778 | 6232 | 149.568 | 6.232 | 7.3 | 7.3 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1176892 | 1218 | 195.4429 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 | 1.34 | Normal operation schedule |  |  | G.SY / A. DIONELA
58:00 | 11:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 138 | 25504498 | 5720 | 137.28 | 5.72 | 6.9 | 6.9 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1178032 | 1140 | 199.3007 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 126 | 132 | 25510322 | 5824 | 139.776 | 5.824 | 6.5 | 6.5 | 3B+1S | 0 | 1047 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1179196 | 1164 | 199.8626 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 131 | 25516053 | 5731 | 137.544 | 5.731 | 6 | 6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1180382 | 1186 | 206.9447 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 130 | 123 | 25521766 | 5713 | 137.112 | 5.713 | 5.8 | 5.8 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1181554 | 1172 | 205.1462 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 128 | 25527842 | 6076 | 145.824 | 6.076 | 5.7 | 5.7 | 3B+1S | 0 | 995 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1182824 | 1270 | 209.0191 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 8 | 5.6338 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 25532554 | 4712 | 113.088 | 4.712 | 5.6 | 5.6 | 3B+1S | 0 | 994 | 1187 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1183796 | 972 | 206.2818 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 130 | 25538268 | 5714 | 137.136 | 5.714 | 5.5 | 5.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1184948 | 1152 | 201.6101 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 5 | 3.5211 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 126 | 25544116 | 5848 | 140.352 | 5.848 | 5.4 | 5.4 | 3B+1S | 0 | 986 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 1186128 | 1180 | 201.7784 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 134 | 25549560 | 5444 | 130.656 | 5.444 | 5.3 | 5.3 | 3B+1S | 0 | 986 | 1177 | 1185 | 1177 | N/A | N/A | N/A | N/A | 1187233 | 1105 | 202.9758 | 0% | 100% | 100% | 100% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 110 | 116 | 25552960 | 3400 | 81.6 | 3.4 | 5 | 5 | 2B+1S | 0 | 1045 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1187663 | 430 | 126.4706 | 0% | 100% | 100% | 0% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 111 | 125 | 25556560 | 3600 | 86.4 | 3.6 | 4.8 | 4.8 | 2B+1S | 0 | 1045 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1188133 | 470 | 130.5556 | 0% | 100% | 100% | 0% | 100% | 0% | 11456577 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 8 | 5.6338 | 74 | 52.1127 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 106 | 119 | 25561141 | 4581 | 109.944 | 4.581 | 4.5 | 4.5 | 2B+1S | 0 | 1045 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1189081 | 948 | 206.9417 | 0% | 100% | 100% | 0% | 100% | 0% | 11456577 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 77 | 54.2254 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.9 | 112 | 115 | 25565667 | 4526 | 108.624 | 4.526 | 4.4 | 4.4 | 2B+1S | 0 | 1045 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1189920 | 839 | 185.3734 | 0% | 100% | 100% | 0% | 100% | 30% | 11456777 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 8 | 5.6338 | 78 | 54.9296 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 11.5 | 113 | 115 | 25570410 | 4743 | 113.832 | 4.743 | 4.5 | 4.5 | 2B+1S | 0 | 1025 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 1190798 | 878 | 185.1149 | 0% | 100% | 100% | 0% | 1000% | 30% | 11457106 | 329 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 123454 | 123.454 | 123.454 | [13 empty] | 24626 | 199.4751 | 0% | 0% | 0% | 0% | 0% |  | 2784 | 2784 | 1.2133 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:48 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 15, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
ALL BOOSTER STOP DUE POWER INTERUPTION @ 7:37 PM
GENSET START @ 7:47 PM
BP1- START @ 7:50 PM
BP3- START @ 7:52 PM
SP2- START @7:54 PM
BP2 FAILED TO OPERATED
RNOG 2B+1S @ 7:55PM
RNOM @8:37 PM
XCV2 -OPENED @ 10:01 PM (20%)

## NOV 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL A. RAMOS / JEFF LAMAYO
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-16 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 22372 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25570410 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1190798 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11457106 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 79 | 55.6338 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.4 | 133 | 108 | 25574923 | 4513 | 108.312 | 4.513 | 5.2 | 5.2 | 2B+1S | 0 | 1045 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1191652 | 854 | 189.2311 | 0% | 100% | 100% | 0% | 100% | 75% | 11457927 | 821 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 79 | 55.6338 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 135 | 104 | 25579494 | 4571 | 109.704 | 4.571 | 6 | 6 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1192471 | 819 | 179.173 | 0% | 0% | 100% | 0% | 100% | 75% | 11458765 | 838 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 79 | 55.6338 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 139 | 101 | 25583763 | 4269 | 102.456 | 4.269 | 7.3 | 7.3 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1193249 | 778 | 182.2441 | 0% | 0% | 100% | 0% | 100% | 75% | 11459683 | 918 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 9 | 6.338 | 79 | 55.6338 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 12.8 | 126 | 107 | 25588218 | 4455 | 106.92 | 4.455 | 8.3 | 8.3 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1194046 | 797 | 178.9001 | 0% | 0% | 100% | 0% | 100% | 75% | 11460518 | 835 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 72 | 50.7042 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 18 | A.ONG | 13.1 | 114 | 108 | 25592295 | 4077 | 97.848 | 4.077 | 9.5 | 9.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1194879 | 833 | 204.3169 | 0% | 0% | 100% | 0% | 100% | 75% | 11461049 | 531 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 8 | 5.6338 | 77 | 54.2254 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 110 | 130 | 25597657 | 5362 | 128.688 | 5.362 | 8.5 | 8.5 | 2B+2S | 0 | 1119 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1195819 | 940 | 175.3077 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 | 1.2 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 76 | 53.5211 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 16.7 | 100 | 130 | 25603199 | 5542 | 133.008 | 5.542 | 8.2 | 8.2 | 2B+2S | 1188 | 1119 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 1196844 | 1025 | 184.9513 | 100% | 100% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 9 | 6.338 | 80 | 56.338 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 100 | 132 | 25608984 | 5785 | 138.84 | 5.785 | 7.5 | 7.5 | 2B+2S | 1189 | 1119 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 1197954 | 1110 | 191.8755 | 100% | 100% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 8 | 5.6338 | 79 | 55.6338 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 103 | 142 | 25614842 | 5858 | 140.592 | 5.858 | 7 | 7 | 2B+2S | 1189 | 1119 | 1190 | 0 | 1189 | N/A | N/A | N/A | N/A | 1199076 | 1122 | 191.5329 | 100% | 100% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 9 | 6.338 | 79 | 55.6338 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 103 | 136 | 25621286 | 6444 | 154.656 | 6.444 | 6.5 | 6.5 | 2B+2S | 1188 | 119 | 1189 | 0 | 1188 | N/A | N/A | N/A | N/A | 1200250 | 1174 | 182.185 | 100% | 100% | 100% | 0% | 100% | 0% | 11461049 | 0 | 1.16 | Normal operation schedule |  |  | G.SY / A. DIONELA
58:00 | 11:00 | 6 | 4.2254 | 62 | 43.662 | Automatic - Pressure Setting | 42.2535 | 43.662 | 45.082 | 19 | A ONG | 17.7 | 124 | 89 | 25626426 | 5140 | 123.36 | 5.14 | 1.3 | 1.3 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 1201108 | 858 | 166.9261 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Normal operation schedule
59:00 | 12:00 | 6 | 4.2254 | 67 | 47.1831 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 48.6031 | 19 | A ONG | 17.3 | 123 | 121 | 25631449 | 5023 | 120.552 | 5.023 | 1.3 | 1.3 | 2B | 0 | 0 | 1188 | 0 | 1188 | N/A | N/A | N/A | N/A | 1201882 | 774 | 154.0912 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 6 | 4.2254 | 63 | 44.3662 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 19 | A ONG | 17.5 | 123 | 123 | 25637434 | 5985 | 143.64 | 5.985 | 1.3 | 1.3 | 2B | 0 | 0 | 1187 | 0 | 1186 | N/A | N/A | N/A | N/A | 1202884 | 1002 | 167.4185 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 65 | 45.7746 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A ONG | 17.3 | 120 | 120 | 25642311 | 4877 | 117.048 | 4.877 | 1.3 | 1.3 | 2B | 0 | 0 | 1188 | 0 | 1187 | N/A | N/A | N/A | N/A | 1203588 | 704 | 144.351 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 65 | 45.7746 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 18 | A ONG | 16.9 | 128 | 128 | 25648072 | 5761 | 138.264 | 5.761 | 1.3 | 1.3 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 1204514 | 926 | 160.736 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 65 | 45.7746 | Automatic - Pressure Setting | 42.2535 | 43.662 | 47.8873 | 18 | A ONG | 16.7 | 138 | 138 | 25652422 | 4350 | 104.4 | 4.35 | 1.4 | 1.4 | 2B | 0 | 0 | 1189 | 0 | 1189 | N/A | N/A | N/A | N/A | 1205175 | 661 | 151.954 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.7 | 127 | 112 | 25657882 | 5460 | 131.04 | 5.46 | 2.9 | 2.9 | 2B | 0 | 0 | 1187 | 0 | 1188 | N/A | N/A | N/A | N/A | 1206084 | 909 | 166.4835 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 67 | 47.1831 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 18 | A ONG | 16.7 | 124 | 114 | 25663158 | 5276 | 126.624 | 5.276 | 3.2 | 3.2 | 2B | 0 | 0 | 1187 | 0 | 1187 | N/A | N/A | N/A | N/A | 1206928 | 844 | 159.9697 | 0% | 0% | 100% | 0% | 100% | 0% | 11461049 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 73 | 51.4085 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 126 | 120 | 25668886 | 5728 | 137.472 | 5.728 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1207958 | 1030 | 179.8184 | 0% | 0% | 100% | 100% | 100% | 0% | 11461049 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 75 | 52.8169 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 126 | 118 | 25673588 | 4702 | 112.848 | 4.702 | 3.3 | 3.3 | 3B | 0 | 0 | 1150 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1208818 | 860 | 182.9009 | 0% | 0% | 100% | 100% | 100% | 0% | 11461049 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 124 | 123 | 25679456 | 5868 | 140.832 | 5.868 | 3 | 3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1209998 | 1180 | 201.0907 | 0% | 100% | 100% | 100% | 100% | 0% | 11461049 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 120 | 125 | 25684594 | 5138 | 123.312 | 5.138 | 2.8 | 2.8 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1211084 | 1086 | 211.3663 | 0% | 100% | 100% | 100% | 100% | 0% | 11461049 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 115 | 25689701 | 5107 | 122.568 | 5.107 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1212141 | 1057 | 206.9708 | 0% | 0% | 100% | 100% | 100% | 30% | 11461364 | 315 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 130 | 111 | 25694630 | 4929 | 118.296 | 4.929 | 3.2 | 3.2 | 3B | 0 | 0 | 1166 | 1185 | 1166 | N/A | N/A | N/A | N/A | 1213170 | 1029 | 208.7645 | 0% | 0% | 100% | 100% | 100% | 30% | 11461787 | 423 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 124220 | 124.22 | 124.22 | [13 empty] | 22372 | 180.0998 | 0% | 0% | 0% | 0% | 0% |  | 4681 | 4681 | 1.145 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:35 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
AS PER ADVISE SIR ALVIN CRUZ STARTED 5:OO AM WE OPERATED 2B+2S TO MEET 83 PSI UNTIL WE REACH A WATER LEVEL LIMIT OF RESERVOIR.
DUE TO BP2 FAILED TO OPERATED
SP2- STARTED @ 5:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1- STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 - STOPPED @ 10:30 AM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
SP2 - STOPPED @ 10:30 AM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 16, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
BP2- STARTED @ 6:26 PM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
SP2- STARTED @ 8:08 PM TO MEET 76 PSI TARGET DISCHARGE PRESSURE

## NOV 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | G.SY / RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | G.SY / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-17 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26832 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25694630 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1213170 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11461787 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 131 | 112 | 25699419 | 4789 | 114.936 | 4.789 | 4.8 | 4.8 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1214178 | 1008 | 210.4824 | 0% | 0% | 100% | 100% | 100% | 75% | 11462651 | 864 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 110 | 25704180 | 4761 | 114.264 | 4.761 | 6.4 | 6.4 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1215167 | 989 | 207.7295 | 0% | 0% | 100% | 100% | 100% | 75% | 11463464 | 813 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 107 | 25708390 | 4210 | 101.04 | 4.21 | 7.8 | 7.8 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1216116 | 949 | 225.4157 | 0% | 0% | 100% | 100% | 100% | 75% | 11464257 | 793 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 131 | 105 | 25712668 | 4278 | 102.672 | 4.278 | 8.9 | 8.9 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1217153 | 1037 | 242.403 | 0% | 0% | 100% | 100% | 100% | 75% | 11464979 | 722 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 | 120 | 25717113 | 4445 | 106.68 | 4.445 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1218204 | 1051 | 236.4454 | 0% | 0% | 100% | 100% | 100% | 75% | 11465179 | 200 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 | 122 | 25721940 | 4827 | 115.848 | 4.827 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1219201 | 997 | 206.5465 | 0% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 | 1.15 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 138 | 25727766 | 5826 | 139.824 | 5.826 | 9.2 | 9.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1220308 | 1107 | 190.0103 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 141 | 25733653 | 5887 | 141.288 | 5.887 | 8.7 | 8.7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1221471 | 1163 | 197.5539 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 140 | 25739744 | 6091 | 146.184 | 6.091 | 8.3 | 8.3 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1222655 | 1184 | 194.3852 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 136 | 25745719 | 5975 | 143.4 | 5.975 | 7.9 | 7.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1223831 | 1176 | 196.8201 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 | 1.1 | Normal operation schedule |  |  | G.SY / A. DIONELA
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 134 | 25751541 | 5822 | 139.728 | 5.822 | 7.5 | 7.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1225041 | 1210 | 207.8324 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Normal operation schedule
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 135 | 25757275 | 5734 | 137.616 | 5.734 | 7 | 7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1226193 | 1152 | 200.9069 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 134 | 25763042 | 5767 | 138.408 | 5.767 | 6.7 | 6.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1227362 | 1169 | 202.705 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 131 | 25768801 | 5759 | 138.216 | 5.759 | 6.4 | 6.4 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1228531 | 1169 | 202.9866 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 131 | 25774482 | 5681 | 136.344 | 5.681 | 6.1 | 6.1 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1229699 | 1168 | 205.5976 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 25780172 | 5690 | 136.56 | 5.69 | 5.8 | 5.8 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1230867 | 1168 | 205.2724 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 25785894 | 5722 | 137.328 | 5.722 | 5.5 | 5.5 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1232034 | 1167 | 203.9497 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 137 | 25791515 | 5621 | 134.904 | 5.621 | 5.2 | 5.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1233207 | 1173 | 208.6817 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 122 | 25797238 | 5723 | 137.352 | 5.723 | 4.9 | 4.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1234372 | 1165 | 203.5646 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 128 | 25802837 | 5599 | 134.376 | 5.599 | 4.7 | 4.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1235536 | 1164 | 207.8943 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 131 | 25808352 | 5515 | 132.36 | 5.515 | 4.4 | 4.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1236687 | 1151 | 208.7035 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 121 | 122 | 25814098 | 5746 | 137.904 | 5.746 | 4.1 | 4.1 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1237875 | 1188 | 206.7525 | 100% | 0% | 100% | 100% | 100% | 0% | 11465179 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 115 | 25819201 | 5103 | 122.472 | 5.103 | 4.3 | 4.3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1239009 | 1134 | 222.2222 | 0% | 0% | 100% | 100% | 100% | 30% | 11465398 | 219 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 132 | 119 | 25824025 | 4824 | 115.776 | 4.824 | 4.8 | 4.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1240002 | 993 | 205.8458 | 0% | 0% | 100% | 100% | 100% | 30% | 11466036 | 638 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129395 | 129.395 | 129.395 | [13 empty] | 26832 | 207.365 | 0% | 0% | 0% | 0% | 0% |  | 4249 | 4249 | 1.1433 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 17, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (25%)

## NOV 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FA.RAMOS / G.SY
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-18 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26952 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25824025 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1240002 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11466036 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 116 | 111 | 25828870 | 4845 | 116.28 | 4.845 | 5.7 | 5.7 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1241008 | 1006 | 207.6367 | 0% | 0% | 100% | 100% | 100% | 70% | 11466458 | 422 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 121 | 111 | 25833453 | 4583 | 109.992 | 4.583 | 6.4 | 6.4 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1241955 | 947 | 206.6332 | 0% | 0% | 100% | 100% | 100% | 70% | 11466885 | 427 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 122 | 108 | 25837829 | 4376 | 105.024 | 4.376 | 7.5 | 7.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1242893 | 938 | 214.351 | 0% | 0% | 100% | 100% | 100% | 70% | 11467294 | 409 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 116 | 25842029 | 4200 | 100.8 | 4.2 | 8.7 | 8.7 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1243873 | 980 | 233.3333 | 0% | 0% | 100% | 100% | 100% | 70% | 11467686 | 392 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 120 | 25846420 | 4391 | 105.384 | 4.391 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1244895 | 1022 | 232.7488 | 0% | 0% | 100% | 100% | 100% | 70% | 11467706 | 20 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 121 | 25851970 | 5550 | 133.2 | 5.55 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1245938 | 1043 | 187.9279 | 0% | 0% | 100% | 100% | 100% | 0% | 11467706 | 0 | 1.12 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 132 | 137 | 25857226 | 5256 | 126.144 | 5.256 | 9.2 | 9.2 | 3B+1S | 0 | 1017 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1246982 | 1044 | 198.6301 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 140 | 25863666 | 6440 | 154.56 | 6.44 | 8.5 | 8.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1248254 | 1272 | 197.5155 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 138 | 25869336 | 5670 | 136.08 | 5.67 | 8.1 | 8.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1249406 | 1152 | 203.1746 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 142 | 25875274 | 5938 | 142.512 | 5.938 | 7.6 | 7.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1250596 | 1190 | 200.4042 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 | 1.32 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 129 | 137 | 25881698 | 6424 | 154.176 | 6.424 | 7 | 7 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1251862 | 1266 | 197.0735 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 134 | 25887512 | 5814 | 139.536 | 5.814 | 6.4 | 6.4 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1253038 | 1176 | 202.2704 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 136 | 25894016 | 6504 | 156.096 | 6.504 | 5.8 | 5.8 | 3B+1S | 0 | 1055 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1254322 | 1284 | 197.417 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 137 | 25899488 | 5472 | 131.328 | 5.472 | 5.3 | 5.3 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1255436 | 1114 | 203.5819 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 135 | 25905506 | 6018 | 144.432 | 6.018 | 4.9 | 4.9 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1256626 | 1190 | 197.7401 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 133 | 25911866 | 6360 | 152.64 | 6.36 | 4.5 | 4.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1257904 | 1278 | 200.9434 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 25917294 | 5428 | 130.272 | 5.428 | 4.2 | 4.2 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1259002 | 1098 | 202.2845 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 136 | 25923334 | 6040 | 144.96 | 6.04 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1260238 | 1236 | 204.6358 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 130 | 25928962 | 5628 | 135.072 | 5.628 | 3.6 | 3.6 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1261366 | 1128 | 200.4264 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 133 | 155 | 25934126 | 5164 | 123.936 | 5.164 | 3.5 | 3.5 | 3B+1S | 0 | 994 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1262430 | 1064 | 206.0418 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 134 | 25940442 | 6316 | 151.584 | 6.316 | 3.1 | 3.1 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1263682 | 1252 | 198.2267 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 127 | 25946183 | 5741 | 137.784 | 5.741 | 2.9 | 2.9 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1264898 | 1216 | 211.8098 | 0% | 100% | 100% | 100% | 100% | 0% | 11467706 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 131 | 114 | 25951446 | 5263 | 126.312 | 5.263 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1265948 | 1050 | 199.506 | 0% | 0% | 100% | 100% | 100% | 30% | 11467798 | 92 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 109 | 25956370 | 4924 | 118.176 | 4.924 | 3.4 | 3.4 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1266954 | 1006 | 204.3054 | 0% | 0% | 100% | 100% | 100% | 3% | 11468055 | 257 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132345 | 132.345 | 132.345 | [13 empty] | 26952 | 203.6496 | 0% | 0% | 0% | 0% | 0% |  | 2019 | 2019 | 1.1617 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 18, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | G.SY / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-19 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26484 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 25956370 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1266954 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11468055 |  | mg /l |  | Automatic - i2O | AI | RANDY REGENCIA
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 127 | 105 | 25960922 | 4552 | 109.248 | 4.552 | 4.6 | 4.6 | 3B | 0 | 0 | 1125 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1267872 | 918 | 201.6696 | 0% | 0% | 100% | 100% | 100% | 70% | 11468601 | 546 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 130 | 102 | 25965369 | 4447 | 106.728 | 4.447 | 5.3 | 5.3 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1268772 | 900 | 202.3836 | 0% | 0% | 100% | 100% | 100% | 70% | 11469142 | 541 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 121 | 104 | 25969709 | 4340 | 104.16 | 4.34 | 7 | 7 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 1269662 | 890 | 205.0691 | 0% | 0% | 100% | 100% | 100% | 70% | 11469767 | 625 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 121 | 114 | 25973709 | 4000 | 96 | 4 | 8.6 | 8.6 | 3B | 0 | 0 | 106 | 1185 | 1076 | N/A | N/A | N/A | N/A | 1270572 | 910 | 227.5 | 0% | 0% | 100% | 100% | 100% | 70% | 11470338 | 571 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 113 | 25978105 | 4396 | 105.504 | 4.396 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1271469 | 897 | 204.0491 | 0% | 0% | 100% | 100% | 100% | 70% | 11470461 | 123 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 | 124 | 25983429 | 5324 | 127.776 | 5.324 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1272361 | 892 | 167.5432 | 0% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 | 1.12 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 | 136 | 25989426 | 5997 | 143.928 | 5.997 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1273498 | 1137 | 189.5948 | 0% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 141 | 25995172 | 5746 | 137.904 | 5.746 | 9 | 9 | 3B+1S | 1077 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1274662 | 1164 | 202.5757 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 144 | 26001484 | 6312 | 151.488 | 6.312 | 8.2 | 8.2 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1275926 | 1264 | 200.2535 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 132 | 26007890 | 6406 | 153.744 | 6.406 | 7.3 | 7.3 | 3B+1S | 1078 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1277202 | 1276 | 199.1883 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 | 1.16 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 141 | 26013998 | 6108 | 146.592 | 6.108 | 6.8 | 6.8 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1278322 | 1120 | 183.3661 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 147 | 26020434 | 6436 | 154.464 | 6.436 | 6.1 | 6.1 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1279504 | 1182 | 183.6544 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 128 | 136 | 26027296 | 6862 | 164.688 | 6.862 | 5.4 | 5.4 | 3B+1S | 1068 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1280786 | 1282 | 186.826 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 137 | 26033341 | 6045 | 145.08 | 6.045 | 4.9 | 4.9 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1281870 | 1084 | 179.3218 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 134 | 26039161 | 5820 | 139.68 | 5.82 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1283030 | 1160 | 199.3127 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 131 | 26045183 | 6022 | 144.528 | 6.022 | 4.1 | 4.1 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1284201 | 1171 | 194.4537 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 133 | 135 | 26050876 | 5693 | 136.632 | 5.693 | 3.8 | 3.8 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1285370 | 1169 | 205.3399 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 | 132 | 26056643 | 5767 | 138.408 | 5.767 | 3.6 | 3.6 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1286537 | 1167 | 202.3582 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 | 1.29 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 129 | 26062220 | 5577 | 133.848 | 5.577 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1287704 | 1167 | 209.2523 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 130 | 26067984 | 5764 | 138.336 | 5.764 | 3.2 | 3.2 | 3B+1S | 1005 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1288862 | 1158 | 200.9022 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 138 | 26073730 | 5746 | 137.904 | 5.746 | 2.9 | 2.9 | 3B+1S | 1035 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1290033 | 1171 | 203.7939 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 123 | 127 | 26079959 | 6229 | 149.496 | 6.229 | 2.6 | 2.6 | 3B+1S | 1034 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1291319 | 1286 | 206.4537 | 100% | 0% | 100% | 100% | 100% | 0% | 11470461 | 0 | 1.3 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 125 | 117 | 26085270 | 5311 | 127.464 | 5.311 | 2.7 | 2.7 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1292379 | 1060 | 199.5858 | 0% | 0% | 100% | 100% | 100% | 30% | 11470503 | 42 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 121 | 26090405 | 5135 | 123.24 | 5.135 | 2.9 | 2.9 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1293438 | 1059 | 206.2317 | 0% | 0% | 100% | 100% | 100% | 30% | 11470804 | 301 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 134035 | 134.035 | 134.035 | [13 empty] | 26484 | 197.5902 | 0% | 0% | 0% | 0% | 0% |  | 2749 | 2749 | 1.2033 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:16 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 19, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-20 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26691 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26090405 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1293438 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11470804 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 136 | 112 | 26095182 | 4777 | 114.648 | 4.777 | 4.5 | 4.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1294373 | 935 | 195.7295 | 0% | 0% | 100% | 100% | 100% | 70% | 11471242 | 438 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 111 | 26099875 | 4693 | 112.632 | 4.693 | 5.7 | 5.7 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1295354 | 981 | 209.0347 | 0% | 0% | 100% | 100% | 100% | 70% | 11471659 | 417 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 125 | 112 | 26104320 | 4445 | 106.68 | 4.445 | 7.2 | 7.2 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 1296264 | 910 | 204.7244 | 0% | 0% | 100% | 100% | 100% | 70% | 11472098 | 439 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 114 | 26108320 | 4000 | 96 | 4 | 8.6 | 8.6 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 1297304 | 1040 | 260 | 0% | 0% | 100% | 100% | 100% | 70% | 11472523 | 425 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 110 | 26112415 | 4095 | 98.28 | 4.095 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1116 | N/A | N/A | N/A | N/A | 1298341 | 1037 | 253.2357 | 0% | 0% | 100% | 100% | 100% | 70% | 11472623 | 100 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 128 | 123 | 26117772 | 5357 | 128.568 | 5.357 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1117 | N/A | N/A | N/A | N/A | 1299350 | 1009 | 188.3517 | 0% | 0% | 100% | 100% | 100% | 0% | 11472623 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 139 | 136 | 26123006 | 5234 | 125.616 | 5.234 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1300354 | 1004 | 191.8227 | 0% | 0% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 140 | 26129032 | 6026 | 144.624 | 6.026 | 9.2 | 9.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1301542 | 1188 | 197.1457 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 107 | 26135418 | 6386 | 153.264 | 6.386 | 8.6 | 8.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1302780 | 1238 | 193.8616 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 148 | 26141612 | 6194 | 148.656 | 6.194 | 8 | 8 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1303946 | 1166 | 188.2467 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 | 1.18 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 134 | 26148034 | 6422 | 154.128 | 6.422 | 7.4 | 7.4 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1305118 | 1172 | 182.4977 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 181 | 26154662 | 6628 | 159.072 | 6.628 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1306362 | 1244 | 187.6886 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 176 | 26161344 | 6682 | 160.368 | 6.682 | 6.2 | 6.2 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1307556 | 1194 | 178.689 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 132 | 120 | 26167566 | 6222 | 149.328 | 6.222 | 5.7 | 5.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1308728 | 1172 | 188.3639 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 132 | 160 | 26173962 | 6396 | 153.504 | 6.396 | 5.3 | 5.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1309894 | 1166 | 182.3014 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 135 | 128 | 26180056 | 6094 | 146.256 | 6.094 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1311052 | 1158 | 190.023 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 26186402 | 6346 | 152.304 | 6.346 | 4.5 | 4.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1312274 | 1222 | 192.5622 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 126 | 26192365 | 5963 | 143.112 | 5.963 | 4.1 | 4.1 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1313447 | 1173 | 196.7131 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 128 | 26198168 | 5803 | 139.272 | 5.803 | 3.7 | 3.7 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1314615 | 1168 | 201.2752 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 129 | 26203881 | 5713 | 137.112 | 5.713 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1315777 | 1162 | 203.3958 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 137 | 26209536 | 5655 | 135.72 | 5.655 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1316937 | 1160 | 205.1282 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 128 | 26215306 | 5770 | 138.48 | 5.77 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1318083 | 1146 | 198.6135 | 0% | 100% | 100% | 100% | 100% | 0% | 11472623 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 | 123 | 26220568 | 5262 | 126.288 | 5.262 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1319129 | 1046 | 198.7837 | 0% | 0% | 100% | 100% | 100% | 30% | 11472832 | 209 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 136 | 117 | 26225530 | 4962 | 119.088 | 4.962 | 4.1 | 4.1 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1320129 | 1000 | 201.5316 | 0% | 0% | 100% | 100% | 100% | 30% | 11473233 | 401 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135125 | 135.125 | 135.125 | [13 empty] | 26691 | 197.5282 | 0% | 0% | 0% | 0% | 0% |  | 2429 | 2429 | 1.1417 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:01 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 20, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | G.SY / A. DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-21 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26531 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26225530 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1320129 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11473233 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 138 | 109 | 26230274 | 4744 | 113.856 | 4.744 | 5.5 | 5.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1321124 | 995 | 209.7386 | 0% | 0% | 100% | 100% | 100% | 70% | 11474135 | 902 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 138 | 106 | 26234905 | 4631 | 111.144 | 4.631 | 7.2 | 7.2 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1322083 | 959 | 207.0827 | 0% | 0% | 100% | 100% | 100% | 70% | 11475045 | 910 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 135 | 108 | 26239509 | 4604 | 110.496 | 4.604 | 8.6 | 8.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1323039 | 956 | 207.6455 | 0% | 0% | 100% | 100% | 100% | 70% | 11475846 | 801 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 | 113 | 26243840 | 4331 | 103.944 | 4.331 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1323979 | 940 | 217.0399 | 0% | 0% | 100% | 100% | 100% | 70% | 11476293 | 447 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 | 121 | 26248531 | 4691 | 112.584 | 4.691 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1325053 | 1074 | 228.9491 | 0% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 | 127 | 26254066 | 5535 | 132.84 | 5.535 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1326128 | 1075 | 194.2186 | 0% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 | 1.16 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 133 | 142 | 26260523 | 6457 | 154.968 | 6.457 | 9.1 | 9.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1327399 | 1271 | 196.8406 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 137 | 26266108 | 5585 | 134.04 | 5.585 | 8.7 | 8.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1328508 | 1109 | 198.5676 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 183 | 26272393 | 6285 | 150.84 | 6.285 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1329683 | 1175 | 186.9531 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 176 | 26278906 | 6513 | 156.312 | 6.513 | 7.7 | 7.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1330846 | 1163 | 178.5659 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 | 1.2 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 132 | 26285368 | 6462 | 155.088 | 6.462 | 7.2 | 7.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1332018 | 1172 | 181.368 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 138 | 26291902 | 6534 | 156.816 | 6.534 | 6.7 | 6.7 | 3B+1S | 1024 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1333202 | 1184 | 181.206 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 133 | 26297932 | 6030 | 144.72 | 6.03 | 6.3 | 6.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1334372 | 1170 | 194.0299 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 132 | 26303904 | 5972 | 143.328 | 5.972 | 5.9 | 5.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1335574 | 1202 | 201.2726 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 | 1.24 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 132 | 26309764 | 5860 | 140.64 | 5.86 | 5.6 | 5.6 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1336776 | 1202 | 205.1195 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 134 | 26315106 | 5342 | 128.208 | 5.342 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1337868 | 1092 | 204.4178 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 125 | 26320588 | 5482 | 131.568 | 5.482 | 5 | 5 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1338998 | 1130 | 206.1291 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 123 | 26326058 | 5470 | 131.28 | 5.47 | 4.8 | 4.8 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1340072 | 1074 | 196.3437 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 126 | 26331924 | 5866 | 140.784 | 5.866 | 4.5 | 4.5 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1341228 | 1156 | 197.0678 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 134 | 26337805 | 5881 | 141.144 | 5.881 | 4.2 | 4.2 | 3B+1S | 1006 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1342373 | 1145 | 194.6948 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 130 | 26343591 | 5786 | 138.864 | 5.786 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1343535 | 1162 | 200.8296 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 121 | 26349349 | 5758 | 138.192 | 5.758 | 3.8 | 3.8 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1344671 | 1136 | 197.2907 | 100% | 0% | 100% | 100% | 100% | 0% | 11476293 | 0 | 1.26 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 115 | 26354313 | 4964 | 119.136 | 4.964 | 3.7 | 3.7 | 3B | 0 | 0 | 1157 | 1185 | 1156 | N/A | N/A | N/A | N/A | 1345698 | 1027 | 206.8896 | 0% | 0% | 100% | 100% | 100% | 20% | 11476306 | 13 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 | 106 | 26359027 | 4714 | 113.136 | 4.714 | 4.4 | 4.4 | 3B | 0 | 0 | 1117 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1346660 | 962 | 204.073 | 0% | 0% | 100% | 100% | 100% | 20% | 11476870 | 564 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133497 | 133.497 | 133.497 | [13 empty] | 26531 | 198.7385 | 0% | 0% | 0% | 0% | 0% |  | 3637 | 3637 | 1.1733 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (75%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:43 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 21, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## NOV 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-22 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26921 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26359027 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1346660 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11476870 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 109 | 26363456 | 4429 | 106.296 | 4.429 | 5.7 | 5.7 | 3B | 0 | 0 | 1117 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1347564 | 904 | 204.1093 | 0% | 0% | 100% | 100% | 100% | 70% | 11477377 | 507 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 112 | 26367906 | 4450 | 106.8 | 4.45 | 7.6 | 7.6 | 3B | 0 | 0 | 1117 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1348474 | 910 | 204.4944 | 0% | 0% | 100% | 100% | 100% | 70% | 11477876 | 499 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 106 | 26372321 | 4415 | 105.96 | 4.415 | 8.9 | 8.9 | 3B | 0 | 0 | 1117 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1349364 | 890 | 201.5855 | 0% | 0% | 100% | 100% | 100% | 70% | 11478386 | 510 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 115 | 26376894 | 4573 | 109.752 | 4.573 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1156 | N/A | N/A | N/A | N/A | 1350394 | 1030 | 225.2351 | 0% | 0% | 100% | 100% | 100% | 70% | 11478513 | 127 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 130 | 119 | 26381576 | 4682 | 112.368 | 4.682 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1351530 | 1136 | 242.6314 | 0% | 0% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 133 | 26387868 | 6292 | 151.008 | 6.292 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1352696 | 1166 | 185.3147 | 0% | 0% | 100% | 100% | 100% | 0% | 11478513 | 0 | 1.13 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 145 | 26394442 | 6574 | 157.776 | 6.574 | 9.1 | 9.1 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1353989 | 1293 | 196.6839 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 139 | 26400202 | 5760 | 138.24 | 5.76 | 8.5 | 8.5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1355116 | 1127 | 195.6597 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 145 | 26406670 | 6468 | 155.232 | 6.468 | 7.9 | 7.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1356390 | 1274 | 196.9697 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 137 | 149 | 26412554 | 5884 | 141.216 | 5.884 | 7.3 | 7.3 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1357544 | 1154 | 196.1251 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 | 1.02 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 150 | 26418682 | 6128 | 147.072 | 6.128 | 6.8 | 6.8 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1358732 | 1188 | 193.8642 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 170 | 26425142 | 6460 | 155.04 | 6.46 | 6.3 | 6.3 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1359918 | 1186 | 183.5913 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 120 | 26431706 | 6564 | 157.536 | 6.564 | 5.8 | 5.8 | 3B+1S | 0 | 1036 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1361172 | 1254 | 191.042 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 132 | 26437786 | 6080 | 145.92 | 6.08 | 5.4 | 5.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1362312 | 1140 | 187.5 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 130 | 26443314 | 5528 | 132.672 | 5.528 | 5.1 | 5.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1363462 | 1150 | 208.0318 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 138 | 26449026 | 5712 | 137.088 | 5.712 | 5 | 5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1364622 | 1160 | 203.0812 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 126 | 26455262 | 6236 | 149.664 | 6.236 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1365878 | 1256 | 201.4112 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 130 | 26460278 | 5016 | 120.384 | 5.016 | 4.5 | 4.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1366916 | 1038 | 206.9378 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 126 | 26465924 | 5646 | 135.504 | 5.646 | 4.4 | 4.4 | 3B+1S | 0 | 996 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1368108 | 1192 | 211.1229 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 124 | 26471486 | 5562 | 133.488 | 5.562 | 4.2 | 4.2 | 3B+1S | 0 | 995 | 1187 | 1187 | 1185 | N/A | N/A | N/A | N/A | 1369263 | 1155 | 207.6591 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 124 | 26477184 | 5698 | 136.752 | 5.698 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1370406 | 1143 | 200.5967 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 123 | 26482697 | 5513 | 132.312 | 5.513 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1371552 | 1146 | 207.8723 | 0% | 100% | 100% | 100% | 100% | 0% | 11478513 | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 110 | 26487719 | 5022 | 120.528 | 5.022 | 4.1 | 4.1 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1372588 | 1036 | 206.2923 | 0% | 0% | 100% | 100% | 100% | 30% | 11478586 | 73 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 135 | 111 | 26492415 | 4696 | 112.704 | 4.696 | 4.9 | 4.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1373581 | 993 | 211.4566 | 0% | 0% | 100% | 100% | 100% | 30% | 11479068 | 482 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 133388 | 133.388 | 133.388 | [13 empty] | 26921 | 201.8248 | 0% | 0% | 0% | 0% | 0% |  | 2198 | 2198 | 1.1067 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:26 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 22, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## NOV 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-23 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26696 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26492415 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1373581 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11479068 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 123 | 108 | 26497045 | 4630 | 111.12 | 4.63 | 5.7 | 5.7 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1374553 | 972 | 209.9352 | 0% | 0% | 100% | 100% | 100% | 70% | 11479951 | 883 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 105 | 26501378 | 4333 | 103.992 | 4.333 | 7.3 | 7.3 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1375496 | 943 | 217.6321 | 0% | 0% | 100% | 100% | 100% | 70% | 11480838 | 887 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 102 | 26505708 | 4330 | 103.92 | 4.33 | 8.7 | 8.7 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1376420 | 924 | 213.3949 | 0% | 0% | 100% | 100% | 100% | 70% | 11481665 | 827 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 | 120 | 26509920 | 4212 | 101.088 | 4.212 | 9.5 | 9.5 | 3B | 0 | 0 | 1087 | 1185 | 1087 | N/A | N/A | N/A | N/A | 1377351 | 931 | 221.0351 | 0% | 0% | 100% | 100% | 100% | 70% | 11481991 | 326 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 | 115 | 26514506 | 4586 | 110.064 | 4.586 | 9.5 | 9.5 | 3B | 0 | 0 | 1085 | 1185 | 1085 | N/A | N/A | N/A | N/A | 1378334 | 983 | 214.348 | 0% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 | 134 | 26520480 | 5974 | 143.376 | 5.974 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1379486 | 1152 | 192.8356 | 0% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 | 1.12 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 131 | 140 | 26526052 | 5572 | 133.728 | 5.572 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1380616 | 1130 | 202.7997 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 143 | 26532046 | 5994 | 143.856 | 5.994 | 8.4 | 8.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1381812 | 1196 | 199.5329 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 130 | 132 | 26538534 | 6488 | 155.712 | 6.488 | 7.8 | 7.8 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1383014 | 1202 | 185.2651 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 137 | 26545166 | 6632 | 159.168 | 6.632 | 7.2 | 7.2 | 3B+1S | 1046 | 0 | 1186 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1384312 | 1298 | 195.7177 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 | 1.18 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 141 | 26551076 | 5910 | 141.84 | 5.91 | 6.7 | 6.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1385440 | 1128 | 190.8629 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 132 | 26556764 | 5688 | 136.512 | 5.688 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1386608 | 1168 | 205.3446 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Normal operation schedule | UNITS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 129 | 26562554 | 5790 | 138.96 | 5.79 | 5.8 | 5.8 | 3B+1S | 1045 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1387766 | 1158 | 200 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 126 | 26568336 | 5782 | 138.768 | 5.782 | 5.4 | 5.4 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1388954 | 1188 | 205.4652 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 128 | 132 | 26573768 | 5432 | 130.368 | 5.432 | 5.1 | 5.1 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1390092 | 1138 | 209.4993 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 127 | 26579492 | 5724 | 137.376 | 5.724 | 4.8 | 4.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1391290 | 1198 | 209.2942 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 112 | 26585212 | 5720 | 137.28 | 5.72 | 4.6 | 4.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1392444 | 1154 | 201.7483 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 128 | 134 | 26590912 | 5700 | 136.8 | 5.7 | 4.1 | 4.1 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1393615 | 1171 | 205.4386 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 135 | 26596808 | 5896 | 141.504 | 5.896 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1394787 | 1172 | 198.7788 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 | 129 | 26602777 | 5969 | 143.256 | 5.969 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1395951 | 1164 | 195.0075 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 130 | 26608644 | 5867 | 140.808 | 5.867 | 3.1 | 3.1 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1397120 | 1169 | 199.25 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 123 | 122 | 26614404 | 5760 | 138.24 | 5.76 | 2.9 | 2.9 | 3B+1S | 1035 | 0 | 1157 | 1185 | 1157 | N/A | N/A | N/A | N/A | 1398264 | 1144 | 198.6111 | 100% | 0% | 100% | 100% | 100% | 0% | 11481991 | 0 | 1.17 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 109 | 26619321 | 4917 | 118.008 | 4.917 | 3.1 | 3.1 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1399299 | 1035 | 210.4942 | 0% | 0% | 100% | 100% | 100% | 30% | 11482171 | 180 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 145 | 108 | 26624154 | 4833 | 115.992 | 4.833 | 4.6 | 4.6 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1400277 | 978 | 202.3588 | 0% | 0% | 100% | 100% | 100% | 30% | 11482767 | 596 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 131739 | 131.739 | 131.739 | [13 empty] | 26696 | 202.6431 | 0% | 0% | 0% | 0% | 0% |  | 3699 | 3699 | 1.1583 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 23, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | G.SY / R.RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-24 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26424 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26624154 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1400277 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11482767 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 | 101 | 26628645 | 4491 | 107.784 | 4.491 | 5.3 | 5.3 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1401237 | 960 | 213.7609 | 0% | 0% | 100% | 100% | 100% | 70% | 11483444 | 677 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 125 | 106 | 26632962 | 4317 | 103.608 | 4.317 | 6.7 | 6.7 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1402197 | 960 | 222.3767 | 0% | 0% | 100% | 100% | 100% | 70% | 11484169 | 725 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 102 | 26637108 | 4146 | 99.504 | 4.146 | 7.9 | 7.9 | 3B | 0 | 0 | 1096 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1403119 | 922 | 222.383 | 0% | 0% | 100% | 100% | 100% | 70% | 11484885 | 716 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 | 111 | 26641117 | 4009 | 96.216 | 4.009 | 9 | 9 | 3B | 0 | 0 | 1097 | 1185 | 1097 | N/A | N/A | N/A | N/A | 1404042 | 923 | 230.232 | 0% | 0% | 100% | 100% | 100% | 70% | 11485557 | 672 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 116 | 26645760 | 4643 | 111.432 | 4.643 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1405042 | 1000 | 215.378 | 0% | 0% | 100% | 100% | 100% | 70% | 11485677 | 120 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 | 127 | 26650823 | 5063 | 121.512 | 5.063 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1405985 | 943 | 186.2532 | 0% | 0% | 100% | 100% | 100% | 0% | 11485677 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 134 | 139 | 26656926 | 6103 | 146.472 | 6.103 | 9.2 | 9.2 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1407164 | 1179 | 193.1837 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 135 | 26663285 | 6359 | 152.616 | 6.359 | 8.7 | 8.7 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1408353 | 1189 | 186.9791 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 134 | 128 | 26669222 | 5937 | 142.488 | 5.937 | 8.3 | 8.3 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1409534 | 1181 | 198.922 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 142 | 26675434 | 6212 | 149.088 | 6.212 | 7.9 | 7.9 | 3B+1S | 0 | 1007 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1410717 | 1183 | 190.4379 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 | 1.31 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 149 | 26681628 | 6194 | 148.656 | 6.194 | 7.5 | 7.5 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1411893 | 1176 | 189.8612 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 133 | 26687473 | 5845 | 140.28 | 5.845 | 7.1 | 7.1 | 3B+1S | 0 | 1016 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1413065 | 1172 | 200.5133 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Normal operation schedule | UNITS |  | G.SY / R.RAMOS
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 133 | 26693200 | 5727 | 137.448 | 5.727 | 6.7 | 6.7 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1414228 | 1163 | 203.0732 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure
61:00 | 14:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 130 | 26698779 | 5579 | 133.896 | 5.579 | 6.4 | 6.4 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1415388 | 1160 | 207.9226 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 | 1.34 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 7 | 4.9296 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 124 | 122 | 26703962 | 5183 | 124.392 | 5.183 | 6.3 | 6.3 | 3B+1S | 0 | 1006 | 1166 | 1185 | 1157 | N/A | N/A | N/A | N/A | 1416478 | 1090 | 210.3029 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 126 | 129 | 26709250 | 5288 | 126.912 | 5.288 | 6.1 | 6.1 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1417576 | 1098 | 207.6399 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 139 | 26714914 | 5664 | 135.936 | 5.664 | 5.9 | 5.9 | 3B+1S | 0 | 1006 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1418722 | 1146 | 202.3305 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 123 | 26720817 | 5903 | 141.672 | 5.903 | 5.6 | 5.6 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1419975 | 1253 | 212.265 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 127 | 124 | 26726684 | 5867 | 140.808 | 5.867 | 5.4 | 5.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1421162 | 1187 | 202.3181 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 | 125 | 26732570 | 5886 | 141.264 | 5.886 | 5.2 | 5.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1422312 | 1150 | 195.3789 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 124 | 26738003 | 5433 | 130.392 | 5.433 | 5.1 | 5.1 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1423466 | 1154 | 212.4057 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 124 | 26743350 | 5347 | 128.328 | 5.347 | 5 | 5 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1424609 | 1143 | 213.7647 | 0% | 100% | 100% | 100% | 100% | 0% | 11485677 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 117 | 26748413 | 5063 | 121.512 | 5.063 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1425680 | 1071 | 211.5347 | 0% | 0% | 100% | 100% | 100% | 30% | 11485782 | 105 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 125 | 107 | 26753430 | 5017 | 120.408 | 5.017 | 5.3 | 5.3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1426701 | 1021 | 203.5081 | 0% | 0% | 100% | 100% | 100% | 30% | 11486042 | 260 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 129276 | 129.276 | 129.276 | [13 empty] | 26424 | 204.3999 | 0% | 0% | 0% | 0% | 0% |  | 3275 | 3275 | 1.205 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:14 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | J. LAMAYO / R. MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN /GLITTERS SY
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-25 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26394 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26753430 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1426701 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11486042 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 123 | 106 | 26757917 | 4487 | 107.688 | 4.487 | 6.2 | 6.2 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 1427631 | 930 | 207.2654 | 0% | 0% | 100% | 100% | 1000% | 70% | 11486662 | 620 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 126 | 104 | 26762240 | 4323 | 103.752 | 4.323 | 7.5 | 7.5 | 3B | 0 | 0 | 1105 | 1185 | 1105 | N/A | N/A | N/A | N/A | 1428559 | 928 | 214.6657 | 0% | 0% | 100% | 100% | 100% | 70% | 11487327 | 665 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 9 | 6.338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 136 | 104 | 26766470 | 4230 | 101.52 | 4.23 | 8.7 | 8.7 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1429484 | 925 | 218.6761 | 0% | 0% | 100% | 100% | 100% | 70% | 11487953 | 626 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 115 | 112 | 26770620 | 4150 | 99.6 | 4.15 | 9.5 | 9.5 | 3B | 0 | 0 | 1108 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1430439 | 955 | 230.1205 | 0% | 0% | 100% | 100% | 100% | 70% | 11488158 | 205 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 | 116 | 26775355 | 4735 | 113.64 | 4.735 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1431401 | 962 | 203.1679 | 0% | 0% | 100% | 100% | 100% |  | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 137 | 132 | 26780845 | 5490 | 131.76 | 5.49 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1432443 | 1042 | 189.7996 | 0% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 | 1.07 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 152 | 26786949 | 6104 | 146.496 | 6.104 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1433625 | 1182 | 193.6435 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 140 | 26793071 | 6122 | 146.928 | 6.122 | 8.7 | 8.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1434832 | 1207 | 197.1578 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 136 | 140 | 26799260 | 6189 | 148.536 | 6.189 | 8.2 | 8.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1436014 | 1182 | 190.984 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 141 | 26805228 | 5968 | 143.232 | 5.968 | 7.9 | 7.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1437208 | 1194 | 200.067 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 | 1.15 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 134 | 26810859 | 5631 | 135.144 | 5.631 | 7.5 | 7.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1438356 | 1148 | 203.8714 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 134 | 26816582 | 5723 | 137.352 | 5.723 | 7.2 | 7.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1439518 | 1162 | 203.0404 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Normal operation schedule | UNITS |  | J. LAMAYO / R. MANA
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 129 | 130 | 26822492 | 5910 | 141.84 | 5.91 | 6.9 | 6.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1440685 | 1167 | 197.4619 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | G.SY / R.RAMOS
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 129 | 125 | 26828156 | 5664 | 135.936 | 5.664 | 6.7 | 6.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1441832 | 1147 | 202.5071 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 132 | 26833790 | 5634 | 135.216 | 5.634 | 6.4 | 6.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1443005 | 1173 | 208.2002 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 132 | 26839374 | 5584 | 134.016 | 5.584 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1444172 | 1167 | 208.99 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 134 | 26845025 | 5651 | 135.624 | 5.651 | 6 | 6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1445326 | 1154 | 204.2116 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 124 | 26850823 | 5798 | 139.152 | 5.798 | 5.7 | 5.7 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1446492 | 1166 | 201.1038 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 131 | 128 | 26856686 | 5863 | 140.712 | 5.863 | 5.4 | 5.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1447662 | 1170 | 199.5565 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 128 | 26862676 | 5990 | 143.76 | 5.99 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1448822 | 1160 | 193.6561 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 130 | 102 | 26868580 | 5904 | 141.696 | 5.904 | 4.9 | 4.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1449984 | 1162 | 196.8157 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 122 | 125 | 26874475 | 5895 | 141.48 | 5.895 | 4.8 | 4.8 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1451128 | 1144 | 194.0628 | 100% | 0% | 100% | 100% | 100% | 0% | 11488158 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 117 | 114 | 26879609 | 5134 | 123.216 | 5.134 | 4.9 | 4.9 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1452141 | 1013 | 197.312 | 0% | 0% | 100% | 100% | 100% | 30% | 11488260 | 102 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 124 | 112 | 26884350 | 4741 | 113.784 | 4.741 | 5 | 5 | 3B | 0 | 0 | 1128 | 1185 | 1128 | N/A | N/A | N/A | N/A | 1453095 | 954 | 201.2234 | 0% | 0% | 100% | 100% | 100% | 30% | 11488365 | 105 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 130920 | 130.92 | 130.92 | [13 empty] | 26394 | 201.604 | 0% | 0% | 0% | 0% | 0% |  | 2323 | 2323 | 1.11 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:23 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 24, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | G.SY / RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | PAUL LABIAN / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-26 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26714 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 26884350 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1453095 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11488365 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 121 | 108 | 26889386 | 5036 | 120.864 | 5.036 | 6.1 | 6.1 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1454097 | 1002 | 198.9674 | 0% | 0% | 100% | 100% | 100% | 70% | 11488790 | 425 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 109 | 26894180 | 4794 | 115.056 | 4.794 | 7.6 | 7.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1455078 | 981 | 204.6308 | 0% | 0% | 100% | 100% | 100% | 70% | 11489217 | 427 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 121 | 107 | 26898850 | 4670 | 112.08 | 4.67 | 8.9 | 8.9 | 3B | 0 | 0 | 1125 | 1185 | 1125 | N/A | N/A | N/A | N/A | 1456063 | 985 | 210.9208 | 0% | 0% | 100% | 100% | 100% | 70% | 11489630 | 413 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 122 | 116 | 26903145 | 4295 | 103.08 | 4.295 | 9.5 | 9.5 | 3B | 0 | 0 | 1125 | 1185 | 1125 | N/A | N/A | N/A | N/A | 1457051 | 988 | 230.0349 | 0% | 0% | 100% | 100% | 100% | 70% | 11489820 | 190 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 120 | 115 | 26907340 | 4195 | 100.68 | 4.195 | 9.5 | 9.5 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 1458039 | 988 | 235.5185 | 0% | 0% | 100% | 100% | 100% |  | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 120 | 126 | 26912235 | 4895 | 117.48 | 4.895 | 9.5 | 9.5 | 3B | 0 | 0 | 1127 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1459046 | 1007 | 205.7201 | 0% | 0% | 100% | 100% | 100% | 0% | 11489820 | 0 | 1.18 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 136 | 26918342 | 6107 | 146.568 | 6.107 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1460103 | 1057 | 173.0801 | 0% | 0% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 148 | 26924243 | 5901 | 141.624 | 5.901 | 9.3 | 9.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1461251 | 1148 | 194.5433 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 137 | 141 | 26930379 | 6136 | 147.264 | 6.136 | 9.1 | 9.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1462450 | 1199 | 195.4042 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 147 | 26936422 | 6043 | 145.032 | 6.043 | 8.6 | 8.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1463648 | 1198 | 198.2459 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 | 1.21 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 135 | 141 | 26942653 | 6231 | 149.544 | 6.231 | 8.1 | 8.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1464829 | 1181 | 189.5362 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 131 | 133 | 26948988 | 6335 | 152.04 | 6.335 | 7.6 | 7.6 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1466029 | 1200 | 189.4238 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Normal operation schedule | UNITS |  | J. LAMAYO / R. MANA
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 132 | 131 | 26955154 | 6166 | 147.984 | 6.166 | 7 | 7 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1467233 | 1204 | 195.2644 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | G.SY / R.RAMOS
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 131 | 26961335 | 6181 | 148.344 | 6.181 | 6.4 | 6.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1468450 | 1217 | 196.8937 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 125 | 26967413 | 6078 | 145.872 | 6.078 | 5.9 | 5.9 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1469646 | 1196 | 196.7753 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 26973704 | 6291 | 150.984 | 6.291 | 5.4 | 5.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1470824 | 1178 | 187.2516 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 135 | 26979852 | 6148 | 147.552 | 6.148 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1472005 | 1181 | 192.095 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 131 | 26986129 | 6277 | 150.648 | 6.277 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1473177 | 1172 | 186.7134 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 131 | 26992136 | 6007 | 144.168 | 6.007 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1474344 | 1167 | 194.2733 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 133 | 26998205 | 6069 | 145.656 | 6.069 | 4 | 4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1475505 | 1161 | 191.3 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 121 | 27004139 | 5934 | 142.416 | 5.934 | 3.7 | 3.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1476662 | 1157 | 194.9781 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 129 | 125 | 27010103 | 5964 | 143.136 | 5.964 | 3.6 | 3.6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1477824 | 1162 | 194.8357 | 0% | 100% | 100% | 100% | 100% | 0% | 11489820 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 114 | 27015428 | 5325 | 127.8 | 5.325 | 3.7 | 3.7 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1478831 | 1007 | 189.108 | 0% | 0% | 100% | 100% | 100% | 30% | 11489886 | 66 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 125 | 117 | 27020566 | 5138 | 123.312 | 5.138 | 3.8 | 3.8 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1479809 | 978 | 190.3464 | 0% | 0% | 100% | 100% | 100% | 30% | 11490076 | 190 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 136216 | 136.216 | 136.216 | [13 empty] | 26714 | 196.115 | 0% | 0% | 0% | 0% | 0% |  | 1711 | 1711 | 1.1117 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 7:32 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 26, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | PAUL LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-27 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26715 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27020566 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1479809 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11490076 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 131 | 110 | 27025298 | 4732 | 113.568 | 4.732 | 5.1 | 5.1 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1480767 | 958 | 202.4514 | 0% | 0% | 100% | 100% | 100% | 70% | 11490507 | 431 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 133 | 111 | 27030056 | 4758 | 114.192 | 4.758 | 6.5 | 6.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1481745 | 978 | 205.5485 | 0% | 0% | 100% | 100% | 100% | 70% | 11490962 | 455 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 137 | 112 | 27034732 | 4676 | 112.224 | 4.676 | 7.8 | 7.8 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1482730 | 985 | 210.6501 | 0% | 0% | 100% | 100% | 100% | 70% | 11491408 | 446 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 136 | 116 | 27039147 | 4415 | 105.96 | 4.415 | 9 | 9 | 3B | 0 | 0 | 1128 | 1185 | 1128 | N/A | N/A | N/A | N/A | 1483732 | 1002 | 226.9536 | 0% | 0% | 100% | 100% | 100% | 70% | 11491832 | 424 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 119 | 114 | 27043650 | 4503 | 108.072 | 4.503 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1484734 | 1002 | 222.5183 | 0% | 0% | 100% | 100% | 100% | 70% | 11492012 | 180 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 10 | 7.0423 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 127 | 129 | 27049082 | 5432 | 130.368 | 5.432 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1485716 | 982 | 180.7806 | 0% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 138 | 135 | 27054282 | 5200 | 124.8 | 5.2 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1486688 | 972 | 186.9231 | 0% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 133 | 133 | 27060444 | 6162 | 147.888 | 6.162 | 9.3 | 9.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1487904 | 1216 | 197.3385 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 144 | 27067086 | 6642 | 159.408 | 6.642 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1489192 | 1288 | 193.9175 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 144 | 27073704 | 6618 | 158.832 | 6.618 | 8 | 8 | 3B+1S | 1046 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1490368 | 1176 | 177.6972 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 | 1.2 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 131 | 160 | 27080302 | 6598 | 158.352 | 6.598 | 7.4 | 7.4 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1491538 | 1170 | 177.3265 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 166 | 27087036 | 6734 | 161.616 | 6.734 | 6.8 | 6.8 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1492740 | 1202 | 178.4972 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Normal operation schedule | UNITS |  | J. LAMAYO / R. MANA
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 131 | 163 | 27093774 | 6738 | 161.712 | 6.738 | 6.2 | 6.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1493934 | 1194 | 177.2039 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | G.SY / R.RAMOS
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 131 | 115 | 27100468 | 6694 | 160.656 | 6.694 | 5.7 | 5.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1495094 | 1160 | 173.2895 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 133 | 27107084 | 6616 | 158.784 | 6.616 | 5.2 | 5.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1496296 | 1202 | 181.6808 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 134 | 130 | 27113668 | 6584 | 158.016 | 6.584 | 4.8 | 4.8 | 3B+1S | 1036 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1497486 | 1190 | 180.7412 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 133 | 27120082 | 6414 | 153.936 | 6.414 | 4.5 | 4.5 | 3B+1S | 1026 | 0 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1498678 | 1192 | 185.8435 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 | 125 | 27126036 | 5954 | 142.896 | 5.954 | 4 | 4 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1499831 | 1153 | 193.6513 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 132 | 128 | 27132134 | 6098 | 146.352 | 6.098 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1500998 | 1167 | 191.3742 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 | 125 | 27138127 | 5993 | 143.832 | 5.993 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1502162 | 1164 | 194.2266 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 131 | 117 | 27144164 | 6037 | 144.888 | 6.037 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1503325 | 1163 | 192.6454 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 126 | 123 | 27150183 | 6019 | 144.456 | 6.019 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1504481 | 1156 | 192.0585 | 100% | 0% | 100% | 100% | 100% | 0% | 11492012 | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 127 | 118 | 27155850 | 5667 | 136.008 | 5.667 | 3.2 | 3.2 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1505518 | 1037 | 182.9892 | 0% | 0% | 100% | 100% | 100% | 30% | 11492073 | 61 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 128 | 114 | 27161387 | 5537 | 132.888 | 5.537 | 3.6 | 3.8 | 3B | 0 | 0 | 1167 | 1185 | 1167 | N/A | N/A | N/A | N/A | 1506524 | 1006 | 181.6868 | 0% | 0% | 100% | 100% | 100% | 30% | 11492320 | 247 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 140821 | 140.821 | 140.821 | [13 empty] | 26715 | 189.7089 | 0% | 0% | 0% | 0% | 0% |  | 2244 | 2244 | 1.12 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:16 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 27, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELIVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## NOV 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | G.SY / A. DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-28 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26931 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27161387 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1506524 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11492320 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 133 | 124 | 27166505 | 5118 | 122.832 | 5.118 | 5.3 | 5.3 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1507532 | 1008 | 196.9519 | 0% | 0% | 100% | 100% | 100% | 70% | 11492738 | 418 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 132 | 115 | 27171312 | 4807 | 115.368 | 4.807 | 6.8 | 6.8 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1508532 | 1000 | 208.03 | 0% | 0% | 100% | 100% | 100% | 70% | 11493158 | 420 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 126 | 108 | 27175769 | 4457 | 106.968 | 4.457 | 8.3 | 8.3 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1509503 | 971 | 217.8595 | 0% | 0% | 100% | 100% | 100% | 70% | 11493582 | 424 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 | 115 | 27180119 | 4350 | 104.4 | 4.35 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1510513 | 1010 | 232.1839 | 0% | 0% | 100% | 100% | 100% | 70% | 11493965 | 383 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 131 | 113 | 27184490 | 4371 | 104.904 | 4.371 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 11185 | 1187 | N/A | N/A | N/A | N/A | 1511596 | 1083 | 247.7694 | 0% | 0% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 142 | 136 | 27190676 | 6186 | 148.464 | 6.186 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1512720 | 1124 | 181.7006 | 0% | 0% | 100% | 100% | 100% | 0% | 11493965 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 | 144 | 27196568 | 5892 | 141.408 | 5.892 | 9.2 | 9.2 | 3B+1S | 0 | 1067 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1513856 | 1136 | 192.8038 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 129 | 141 | 27203016 | 6448 | 154.752 | 6.448 | 8.5 | 8.5 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1515112 | 1256 | 194.7891 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 134 | 27209526 | 6510 | 156.24 | 6.51 | 7.8 | 7.8 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1516344 | 1232 | 189.2473 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 136 | 27215702 | 6176 | 148.224 | 6.176 | 7.2 | 7.2 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1517520 | 1176 | 190.4145 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 | 1.19 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 128 | 175 | 27222322 | 6620 | 158.88 | 6.62 | 6.6 | 6.6 | 3B+1S | 0 | 1056 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1518678 | 1158 | 174.9245 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 127 | 131 | 27229086 | 6764 | 162.336 | 6.764 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1519848 | 1170 | 172.9746 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Normal operation schedule | UNITS |  | J. LAMAYO / R. MANA
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 127 | 129 | 27235894 | 6808 | 163.392 | 6.808 | 5.5 | 5.5 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1521064 | 1216 | 178.6134 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | G.SY / R.RAMOS
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 127 | 127 | 27242506 | 6612 | 158.688 | 6.612 | 5 | 5 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1522254 | 1190 | 179.9758 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 129 | 122 | 27248366 | 5860 | 140.64 | 5.86 | 4.7 | 4.7 | 3B+1S | 0 | 1035 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1523440 | 1186 | 202.3891 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 132 | 132 | 27254044 | 5678 | 136.272 | 5.678 | 4.3 | 4.3 | 3B+1S | 0 | 1035 | 1188 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1524588 | 1148 | 202.1839 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 129 | 123 | 27259912 | 5868 | 140.832 | 5.868 | 3.9 | 3.9 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1525724 | 1136 | 193.5924 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 | 126 | 27265588 | 5676 | 136.224 | 5.676 | 3.6 | 3.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1526784 | 1060 | 186.7512 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 | 1.28 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 128 | 131 | 27271804 | 6216 | 149.184 | 6.216 | 3.4 | 3.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1527936 | 1152 | 185.3282 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 122 | 27278005 | 6201 | 148.824 | 6.201 | 3.3 | 3.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1529083 | 1147 | 184.9702 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 127 | 126 | 27284144 | 6139 | 147.336 | 6.139 | 3.1 | 3.1 | 3B+1S | 0 | 1024 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1530242 | 1159 | 188.793 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 128 | 120 | 27289815 | 5671 | 136.104 | 5.671 | 3 | 3 | 3B+1S | 0 | 1004 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1531384 | 1142 | 201.3754 | 0% | 100% | 100% | 100% | 100% | 0% | 11493965 | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 123 | 103 | 27295036 | 5221 | 125.304 | 5.221 | 3 | 3 | 3B | 0 | 0 | 1188 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1532453 | 1069 | 204.75 | 0% | 0% | 100% | 100% | 100% | 20% | 11493965 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 134 | 106 | 27300117 | 5081 | 121.944 | 5.081 | 3.5 | 3.8 | 3B | 0 | 0 | 1167 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1533455 | 1002 | 197.2053 | 0% | 0% | 100% | 100% | 100% | 20% | 11494481 | 516 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 138730 | 138.73 | 138.73 | [13 empty] | 26931 | 194.1253 | 0% | 0% | 0% | 0% | 0% |  | 2161 | 2161 | 1.16 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 28, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE PLANT SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## NOV 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS/RANIEL MANA
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-29 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26807 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27300117 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1533455 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11494481 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 135 | 108 | 27304333 | 4216 | 101.184 | 4.216 | 5 | 5 | 3B | 0 | 0 | 1166 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1534357 | 902 | 213.9469 | 0% | 0% | 100% | 100% | 100% | 85% | 11495005 | 524 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 131 | 110 | 27308588 | 4255 | 102.12 | 4.255 | 6.2 | 6.2 | 3B | 0 | 0 | 1166 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1535282 | 925 | 217.3913 | 0% | 0% | 100% | 100% | 100% | 85% | 11495515 | 510 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 | 102 | 27312890 | 4302 | 103.248 | 4.302 | 7.8 | 7.8 | 3B | 0 | 0 | 1166 | 1185 | 1096 | N/A | N/A | N/A | N/A | 1536237 | 955 | 221.9898 | 0% | 0% | 100% | 100% | 100% | 85% | 11496063 | 548 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 | 119 | 27317421 | 4531 | 108.744 | 4.531 | 9.1 | 9.1 | 3B | 0 | 0 | 1146 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1537292 | 1055 | 232.8404 | 0% | 0% | 100% | 100% | 100% | 85% | 11496565 | 502 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 | 116 | 27321942 | 4521 | 108.504 | 4.521 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1538369 | 1077 | 238.2216 | 0% | 0% | 100% | 100% | 100% | 85% | 11496724 | 159 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 | 123 | 27328322 | 6380 | 153.12 | 6.38 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1539580 | 1211 | 189.8119 | 0% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 | 1.14 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 | 142 | 27334208 | 5886 | 141.264 | 5.886 | 9.3 | 9.3 | 3B+1S | 996 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1540722 | 1142 | 194.0197 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 132 | 129 | 27340502 | 6294 | 151.056 | 6.294 | 8.7 | 8.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1541942 | 1220 | 193.8354 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 133 | 143 | 27347044 | 6542 | 157.008 | 6.542 | 8 | 8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1543210 | 1268 | 193.8245 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 133 | 146 | 27353492 | 6448 | 154.752 | 6.448 | 7.5 | 7.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1544428 | 1218 | 188.8958 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 | 1.31 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 130 | 138 | 27359484 | 5992 | 143.808 | 5.992 | 7 | 7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1545564 | 1136 | 189.5861 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 128 | 128 | 27365688 | 6204 | 148.896 | 6.204 | 6.5 | 6.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1546694 | 1130 | 182.1406 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Normal operation schedule | UNITS |  | J. LAMAYO / R. MANA
60:00 | 13:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 122 | 131 | 27372402 | 6714 | 161.136 | 6.714 | 5.9 | 5.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1547978 | 1284 | 191.2422 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | G.SY / R.RAMOS
61:00 | 14:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 130 | 27378572 | 6170 | 148.08 | 6.17 | 5.6 | 5.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1188 | N/A | N/A | N/A | N/A | 1549150 | 1172 | 189.9514 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 | 1.46 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 131 | 129 | 27383776 | 5204 | 124.896 | 5.204 | 5.3 | 5.3 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1550254 | 1104 | 212.1445 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 136 | 132 | 27389414 | 5638 | 135.312 | 5.638 | 5.2 | 5.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1551430 | 1176 | 208.5846 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 131 | 122 | 27395016 | 5602 | 134.448 | 5.602 | 5 | 5 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1552574 | 1144 | 204.2128 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 | 129 | 27400872 | 5856 | 140.544 | 5.856 | 4.9 | 4.9 | 3B+1S | 994 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1553739 | 1165 | 198.9413 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 | 1.25 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 130 | 129 | 27406572 | 5700 | 136.8 | 5.7 | 4.7 | 4.7 | 3B+1S | 995 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1554897 | 1158 | 203.1579 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 | 124 | 27412188 | 5616 | 134.784 | 5.616 | 4.6 | 4.6 | 3B+1S | 994 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1556038 | 1141 | 203.1695 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 129 | 122 | 27417693 | 5505 | 132.12 | 5.505 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1557185 | 1147 | 208.356 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 119 | 122 | 27423124 | 5431 | 130.344 | 5.431 | 4.2 | 4.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1558322 | 1137 | 209.3537 | 100% | 0% | 100% | 100% | 100% | 0% | 11496724 | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 5 | 5 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 118 | 112 | 27427995 | 4871 | 116.904 | 4.871 | 4.5 | 4.5 | 3B | 0 | 0 | 1127 | 1185 | 1127 | N/A | N/A | N/A | N/A | 1559311 | 989 | 203.0384 | 0% | 0% | 100% | 100% | 100% | 30% | 11496892 | 168 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 126 | 108 | 27432599 | 4604 | 110.496 | 4.604 | 4.8 | 3.8 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1560262 | 951 | 206.5595 | 0% | 0% | 100% | 100% | 100% | 30% | 11497101 | 209 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 132482 | 132.482 | 132.482 | [13 empty] | 26807 | 202.3445 | 0% | 0% | 0% | 0% | 0% |  | 2620 | 2620 | 1.2217 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (85%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:12 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1- STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 29, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE PLANT SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## NOV 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [12 empty] | 6am - 2pm | FIDEL RAMOS
WATER NETWORK | [12 empty] | 2pm - 10pm | FIDEL A. RAMOS / JEFF LAMAYO
[13 empty] | 10pm - 6am | P. LABIAN /A.DIONELA
LOCATION: |  | Villamor Pump Station and Reservoir | [7 empty] | 2014-02-16
DATE |  | UNIT |  |  |  | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING |  |  |  |  | RESERVOIR REFILL |  |  | Res. Chl.
2016-11-30 |  | m of H2O |  |  |  |  | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26475 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  | Discharge |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | psi | (m) |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 27432599 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 1560262 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | 11497101 |  | mg /l |  | Automatic - i2O | AI | PAUL LABIAN
48:00 | 1:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 120 | 105 | 27437137 | 4538 | 108.912 | 4.538 | 5.6 | 5.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1561221 | 959 | 211.3266 | 0% | 0% | 100% | 100% | 100% | 75% | 11497661 | 560 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | GLITTERS SY
49:00 | 2:00 | 7 | 4.9296 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 128 | 104 | 27441487 | 4350 | 104.4 | 4.35 | 7 | 7 | 3B | 0 | 0 | 1126 | 1185 | 1126 | N/A | N/A | N/A | N/A | 1562181 | 960 | 220.6897 | 0% | 0% | 100% | 100% | 100% | 75% | 11498226 | 565 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | FIDEL RAMOS
50:00 | 3:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 125 | 102 | 27445772 | 4285 | 102.84 | 4.285 | 8.3 | 8.3 | 3B | 0 | 0 | 1107 | 1185 | 1107 | N/A | N/A | N/A | N/A | 1563139 | 958 | 223.5706 | 0% | 0% | 100% | 100% | 100% | 75% | 11498766 | 540 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | FIDEL RAMOS/RANIEL MANA
51:00 | 4:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 110 | 110 | 27449995 | 4223 | 101.352 | 4.223 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1564085 | 946 | 224.0114 | 0% | 0% | 100% | 100% | 100% | 75% | 11499253 | 487 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | P. LABIAN /A.DIONELA
52:00 | 5:00 | 11 | 7.7465 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 112 | 106 | 27454155 | 4160 | 99.84 | 4.16 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 1076 | N/A | N/A | N/A | N/A | 1565011 | 926 | 222.5962 | 0% | 0% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | G.SY / RANIEL MANA
53:00 | 6:00 | 12 | 8.4507 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 130 | 125 | 27459612 | 5457 | 130.968 | 5.457 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 1106 | N/A | N/A | N/A | N/A | 1565990 | 979 | 179.4026 | 0% | 0% | 100% | 100% | 100% | 0% | 11499253 | 0 | 1.12 | Normal operation schedule | Error - General | E | G.SY / JEFF LAMAYO
54:00 | 7:00 | 8 | 5.6338 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 140 | 136 | 27464692 | 5080 | 121.92 | 5.08 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1566940 | 950 | 187.0079 | 0% | 0% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Normal operation schedule | Power Interruption | PI | FIDEL A. RAMOS / JEFF LAMAYO
55:00 | 8:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 134 | 143 | 27470646 | 5954 | 142.896 | 5.954 | 9.3 | 9.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1568130 | 1190 | 199.8656 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Normal operation schedule | Water Interruption | WI | PAUL LABIAN / JEFF LAMAYO
56:00 | 9:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 132 | 140 | 27476686 | 6040 | 144.96 | 6.04 | 8.7 | 8.7 | 3B+1S | 0 | 1057 | 1188 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1569334 | 1204 | 199.3377 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Normal operation schedule | Equipment Maintenance | EM | PAUL LABIAN /GLITTERS SY
57:00 | 10:00 | 5 | 3.5211 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 132 | 143 | 27482952 | 6266 | 150.384 | 6.266 | 8.1 | 8.1 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1570580 | 1246 | 198.8509 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 | 1.19 | Normal operation schedule |  |  | F.A.RAMOS / G.SY
58:00 | 11:00 | 6 | 4.2254 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 134 | 139 | 27488686 | 5734 | 137.616 | 5.734 | 7.4 | 7.4 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1571716 | 1136 | 198.1165 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Normal operation schedule |  |  | G.SY / A. DIONELA
59:00 | 12:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 130 | 144 | 27494884 | 6198 | 148.752 | 6.198 | 6.8 | 6.8 | 3B+1S | 0 | 1057 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1572968 | 1252 | 202.0006 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Normal operation schedule | UNITS |  | J. LAMAYO / R. MANA
60:00 | 13:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 130 | 122 | 27501466 | 6582 | 157.968 | 6.582 | 6.2 | 6.2 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1574136 | 1168 | 177.4537 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | G.SY / R.RAMOS
61:00 | 14:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 17.3 | 128 | 133 | 27508416 | 6950 | 166.8 | 6.95 | 5.6 | 5.6 | 3B+1S | 0 | 1045 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1575382 | 1246 | 179.2806 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7
62:00 | 15:00 | 5 | 3.5211 | 81 | 57.0423 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 130 | 136 | 27515216 | 6800 | 163.2 | 6.8 | 5.2 | 5.2 | 3B+1S | 0 | 1045 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1576552 | 1170 | 172.0588 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36
63:00 | 16:00 | 6 | 4.2254 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 130 | 133 | 27521406 | 6190 | 148.56 | 6.19 | 4.8 | 4.8 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1577738 | 1186 | 191.5994 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132
64:00 | 17:00 | 4 | 2.8169 | 81 | 57.0423 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 128 | 160 | 27527682 | 6276 | 150.624 | 6.276 | 4.3 | 4.3 | 3B+1S | 0 | 1046 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1578898 | 1160 | 184.8311 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1
65:00 | 18:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 | 131 | 27533996 | 6314 | 151.536 | 6.314 | 3.8 | 3.8 | 3B+1S | 0 | 1025 | 1186 | 1185 | 1186 | N/A | N/A | N/A | N/A | 1580100 | 1202 | 190.3706 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325
66:00 | 19:00 | 4 | 2.8169 | 78 | 54.9296 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 129 | 121 | 27540285 | 6289 | 150.936 | 6.289 | 3.5 | 3.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1581255 | 1155 | 183.654 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
67:00 | 20:00 | 4 | 2.8169 | 76 | 53.5211 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 | 134 | 27546463 | 6178 | 148.272 | 6.178 | 3.2 | 3.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1582419 | 1164 | 188.4105 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value)
68:00 | 21:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 128 | 111 | 27552520 | 6057 | 145.368 | 6.057 | 3 | 3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1583578 | 1159 | 191.3489 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi
69:00 | 22:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 124 | 117 | 27558372 | 5852 | 140.448 | 5.852 | 2.8 | 2.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | N/A | N/A | N/A | N/A | 1584734 | 1156 | 197.5393 | 0% | 100% | 100% | 100% | 100% | 0% | 11499253 | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 129 | 110 | 27563450 | 5078 | 121.872 | 5.078 | 2.9 | 2.9 | 3B | 0 | 0 | 1147 | 1185 | 1147 | N/A | N/A | N/A | N/A | 1585745 | 1011 | 199.0941 | 0% | 0% | 100% | 100% | 100% | 30% | 11499426 | 173 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 83 | 58.4507 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 128 | 103 | 27568190 | 4740 | 113.76 | 4.74 | 3.6 | 3.6 | 3B | 0 | 0 | 1146 | 1185 | 1146 | N/A | N/A | N/A | N/A | 1586737 | 992 | 209.2827 | 0% | 0% | 100% | 100% | 100% | 30% | 11499854 | 428 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[10 empty] | TOTAL | [5 empty] | 135591 | 135.591 | 135.591 | [13 empty] | 26475 | 195.2563 | 0% | 0% | 0% | 0% | 0% |  | 2753 | 2753 | 1.145 |  | MLD | 1
[44 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [43 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 am to 5am as per request of Engr.Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83psi @ 12:01 am as per request of Engr.FRANCIS MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 aM AS PER SCHEDULE
Change operation as per advise sir Alvin Cruz effective tonight SEPTEMBER 7.2016,target pressure for 12MN-3AM will be changed to from 75 psi to 83 psi only. This was requested by sir GIGI effective tonight until further notice.
XCV2- INCREASE OPENING @ 12:01 AM (85%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM (NOV 30, 2016) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:00 PM TO 5:00PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE PLANT SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)