## MAR 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / PAUL G. LABIAN
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-01 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27368 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 86922175 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13671374 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.4 | 120 |  | 86925075 | 2900 | 69.6 | 2.9 | 2.7 | 2.7 | 3B | 0 | 0 | 1157 | 0 | 1156 | 1185 | N/A | N/A | N/A | 13672388 | 1014 | 349.6552 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.2 | 124 |  | 86928091 | 3016 | 72.384 | 3.016 | 2.8 | 2.8 | 3B | 0 | 0 | 1156 | 0 | 1156 | 1185 | N/A | N/A | N/A | 13673384 | 996 | 330.2387 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 81 | 57.0423 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A.ONG | 11.2 | 116 |  | 86931020 | 2929 | 70.296 | 2.929 | 3 | 3 | 3B | 0 | 0 | 0 | 1185 | 1135 | 1185 | N/A | N/A | N/A | 13674370 | 986 | 336.6337 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 77 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 12.8 | 121 |  | 86933971 | 2951 | 70.824 | 2.951 | 5.6 | 5.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13675389 | 1019 | 345.3067 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 4 | 71 | 50 | 77 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 18 | A.ONG | 13.1 | 129 |  | 86936958 | 2987 | 71.688 | 2.987 | 8.3 | 8.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13676547 | 1158 | 387.6799 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 5 | 82 | 57.7465 | 79 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | 135 |  | 86939743 | 2785 | 66.84 | 2.785 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13677746 | 1199 | 430.5206 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.97 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 133 |  | 86943706 | 3963 | 95.112 | 3.963 | 9 | 9 | 3B+1S | 1037 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13678935 | 1189 | 300.0252 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 123 |  | 86947651 | 3945 | 94.68 | 3.945 | 8.2 | 8.2 | 3B+1S | 1189 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13680135 | 1200 | 304.1825 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 123 |  | 86951714 | 4063 | 97.512 | 4.063 | 7.2 | 7.2 | 3B+1S | 1189 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13681390 | 1255 | 308.8851 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 124 |  | 86955738 | 4024 | 96.576 | 4.024 | 6.3 | 6.3 | 3B+1S | 1188 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13682654 | 1264 | 314.1153 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 123 |  | 86959740 | 4002 | 96.048 | 4.002 | 5.2 | 5.2 | 3B+1S | 1177 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13683906 | 1252 | 312.8436 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 121 |  | 86963679 | 3939 | 94.536 | 3.939 | 4.2 | 4.2 | 3B+1S | 1177 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13685151 | 1245 | 316.0701 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 128 |  | 86967285 | 3606 | 86.544 | 3.606 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13686317 | 1166 | 323.35 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 130 |  | 86970764 | 3479 | 83.496 | 3.479 | 3.4 | 3.4 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13687460 | 1143 | 328.5427 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 133 |  | 86974248 | 3484 | 83.616 | 3.484 | 3.2 | 3.2 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13688634 | 1174 | 336.969 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 135 |  | 86977702 | 3454 | 82.896 | 3.454 | 3 | 3 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13689783 | 1149 | 332.6578 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 86981050 | 3348 | 80.352 | 3.348 | 2.9 | 2.9 | 3B+1S | 1006 | 0 | 0 | 1185 | 1185 | 1185 | N/A | N/A | N/A | 13690892 | 1109 | 343.19 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 86984505 | 3455 | 82.92 | 3.455 | 2.7 | 2.7 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13692056 | 1164 | 320.9841 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 86987990 | 3485 | 83.64 | 3.485 | 2.4 | 2.4 | 3B+1S | 1007 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13693220 | 1164 | 334.0029 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 86991430 | 3440 | 82.56 | 3.44 | 2.2 | 2.2 | 3B+1S | 994 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 13694340 | 1120 | 325.5814 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 129 |  | 86994800 | 3370 | 80.88 | 3.37 | 2 | 2 | 3B+1S | 995 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13695474 | 1134 | 336.4985 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 123 |  | 86998222 | 3422 | 82.128 | 3.422 | 1.8 | 1.8 | 3B+1S | 1045 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13696620 | 1146 | 334.8919 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.9 | 126 |  | 87001300 | 3078 | 73.872 | 3.078 | 2 | 2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13697686 | 1066 | 346.3288 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 79 | 55.6338 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 11.5 | 125 |  | 87004264 | 2964 | 71.136 | 2.964 | 2.1 | 2.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13698742 | 1056 | 356.2753 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 82089 | 1970.136 | 82.089 | [13 empty] | 27368 | 333.3942 | [7 empty] | 0 | 0 | 0.96667 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 5:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
MR. MARIO MIRANDA OF SOUTH MAINTENANCE AND TEAM ARRIVE @ 8:01 AM TO CONDUCT MONTHLY PREVENTIVE MAINTENANCE.
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 1, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-02 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27671 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87004264 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13698742 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 130 |  | 87007070 | 2806 | 67.344 | 2.806 | 2.7 | 2.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13699860 | 1118 | 398.4319 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.2 | 129 |  | 87009834 | 2764 | 66.336 | 2.764 | 3.4 | 3.4 | 3B | 0 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 13700918 | 1058 | 382.7786 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 141 |  | 87012384 | 2550 | 61.2 | 2.55 | 5 | 5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13702000 | 1082 | 424.3137 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 12.8 | 140 |  | 87015112 | 2728 | 65.472 | 2.728 | 7.4 | 7.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13703130 | 1130 | 414.2229 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 127 |  | 87017986 | 2874 | 68.976 | 2.874 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13704320 | 1190 | 414.0571 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 6 | 81 | 57.0423 | 77 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 128 |  | 87021380 | 3394 | 81.456 | 3.394 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13705396 | 1076 | 317.0301 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.11 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 127 |  | 87025140 | 3760 | 90.24 | 3.76 | 9 | 9 | 3B+1S | 0 | 1088 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13706560 | 1164 | 309.5745 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 123 |  | 87029090 | 3950 | 94.8 | 3.95 | 8.1 | 8.1 | 3B+1S | 0 | 1189 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13707792 | 1232 | 311.8987 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 74 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 125 |  | 87033017 | 3927 | 94.248 | 3.927 | 7.1 | 7.1 | 3B+1S | 0 | 1188 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13709044 | 1252 | 318.8184 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 74 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 123 |  | 87037112 | 4095 | 98.28 | 4.095 | 6 | 6 | 3B+1S | 0 | 1188 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13710328 | 1284 | 313.5531 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.89 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 2 | 79 | 55.6338 | 74 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 123 |  | 87041030 | 3918 | 94.032 | 3.918 | 5 | 5 | 3B+1S | 0 | 1188 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13711575 | 1247 | 318.2746 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 79 | 55.6338 | 74 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 121 |  | 87044852 | 3822 | 91.728 | 3.822 | 3.7 | 3.7 | 3B+1S | 0 | 1188 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13712830 | 1255 | 328.3621 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 129 |  | 87048555 | 3703 | 88.872 | 3.703 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13714025 | 1195 | 322.7113 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 87052101 | 3546 | 85.104 | 3.546 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13715194 | 1169 | 329.6672 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 129 |  | 87055436 | 3335 | 80.04 | 3.335 | 2.7 | 2.7 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13716319 | 1125 | 337.3313 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 133 |  | 87058907 | 3471 | 83.304 | 3.471 | 2.5 | 2.5 | 3B+1S | 0 | 994 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13717476 | 1157 | 333.3333 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 87062350 | 3443 | 82.632 | 3.443 | 2.4 | 2.4 | 3B+1S | 0 | 995 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13718628 | 1152 | 336.0441 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 131 |  | 87065800 | 3450 | 82.8 | 3.45 | 2.2 | 2.2 | 3B+1S | 0 | 995 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13719752 | 1124 | 333.913 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 87069350 | 3550 | 85.2 | 3.55 | 2.1 | 2.1 | 3B+1S | 0 | 995 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13720923 | 1171 | 329.8592 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 87072796 | 3446 | 82.704 | 3.446 | 1.9 | 1.9 | 3B+1S | 0 | 996 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13722028 | 1105 | 320.6616 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 87076114 | 3318 | 79.632 | 3.318 | 1.7 | 1.7 | 3B+1S | 0 | 1006 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13723169 | 1141 | 343.8819 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 |  | 87079331 | 3217 | 77.208 | 3.217 | 1.6 | 1.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13724303 | 1134 | 352.5023 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 11.9 | 124 |  | 87082397 | 3066 | 73.584 | 3.066 | 1.5 | 1.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13725373 | 1070 | 348.9889 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.5 | 126 |  | 87085637 | 3240 | 77.76 | 3.24 | 1.7 | 1.7 | 3B | 0 | 0 | 0 | 1185 | 1146 | 1185 | N/A | N/A | N/A | 13726413 | 1040 | 320.9877 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 81373 | 1952.952 | 81.373 | [13 empty] | 27671 | 340.0514 | [7 empty] | 0 | 0 | 0.97 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:34 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 2, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | PAUL G. LABIAN / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-03 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27487 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87085637 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13726413 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 2 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.4 | 122 |  | 87088631 | 2994 | 71.856 | 2.994 | 1.9 | 1.9 | 3B | 0 | 0 | 0 | 1185 | 1146 | 1185 | N/A | N/A | N/A | 13727454 | 1041 | 347.6954 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 129 |  | 87091386 | 2755 | 66.12 | 2.755 | 3.1 | 3.1 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 13728514 | 1060 | 384.755 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 125 |  | 87093979 | 2593 | 62.232 | 2.593 | 4.6 | 4.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13729605 | 1091 | 420.7482 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 77 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 12.8 | 120 |  | 87096599 | 2620 | 62.88 | 2.62 | 7.2 | 7.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13730699 | 1094 | 417.5573 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 5 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 |  | 87099299 | 2700 | 64.8 | 2.7 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 13731865 | 1166 | 431.8519 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 |  | 87102868 | 3569 | 85.656 | 3.569 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13732913 | 1048 | 293.6397 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 127 |  | 87106645 | 3777 | 90.648 | 3.777 | 9.4 | 9.4 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13734026 | 1113 | 294.6783 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 124 |  | 87110667 | 4022 | 96.528 | 4.022 | 8.6 | 8.6 | 3B+1S | 1188 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13735254 | 1228 | 305.3207 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 122 |  | 87114685 | 4018 | 96.432 | 4.018 | 7.7 | 7.7 | 3B+1S | 1188 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13736505 | 1251 | 311.3489 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 124 |  | 87118675 | 3990 | 95.76 | 3.99 | 6.6 | 6.6 | 3B+1S | 1188 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13737771 | 1266 | 317.2932 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.96 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 124 |  | 87122763 | 4088 | 98.112 | 4.088 | 5.6 | 5.6 | 3B+1S | 1188 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13739037 | 1266 | 309.6869 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 122 |  | 87126738 | 3975 | 95.4 | 3.975 | 4.4 | 4.4 | 3B+1S | 1188 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13740306 | 1269 | 319.2453 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 19 | A ONG | 17.5 | 129 |  | 87130760 | 4022 | 96.528 | 4.022 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13741549 | 1243 | 309.0502 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 17.3 | 132 |  | 87134472 | 3712 | 89.088 | 3.712 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13742769 | 1220 | 328.6638 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | 131 |  | 87137691 | 3219 | 77.256 | 3.219 | 2.7 | 2.7 | 3B+1S | 996 | 0 | 0 | 1185 | 1185 | 1185 | N/A | N/A | N/A | 13743863 | 1094 | 339.8571 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 87141283 | 3592 | 86.208 | 3.592 | 2.5 | 2.5 | 3B+1S | 996 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13745041 | 1178 | 327.951 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 87144730 | 3447 | 82.728 | 3.447 | 2.3 | 2.3 | 3B+1S | 995 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13746170 | 1129 | 341.7464 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 87148182 | 3452 | 82.848 | 3.452 | 2 | 2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13747318 | 1148 | 327.0568 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 87151788 | 3606 | 86.544 | 3.606 | 1.7 | 1.7 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13748462 | 1144 | 317.249 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 131 |  | 87155281 | 3493 | 83.832 | 3.493 | 1.3 | 1.3 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13749619 | 1157 | 331.2339 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 69 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | 132 |  | 87158520 | 3239 | 77.736 | 3.239 | 1.3 | 1.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13750711 | 1092 | 337.1411 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 128 |  | 87161834 | 3314 | 79.536 | 3.314 | 1.3 | 1.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13751798 | 1087 | 328.0024 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 136 |  | 87164998 | 3164 | 75.936 | 3.164 | 1.4 | 1.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13752824 | 1026 | 324.2731 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | 131 |  | 87167944 | 2946 | 70.704 | 2.946 | 2.1 | 2.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13753900 | 1076 | 365.241 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 82307 | 1975.368 | 82.307 | [13 empty] | 27487 | 333.957 | [7 empty] | 0 | 0 | 0.93833 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:33 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:45 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 3, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 7:55 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-04 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27734 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87167944 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13753900 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.4 | 129 |  | 87170728 | 2784 | 66.816 | 2.784 | 2.8 | 2.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13754982 | 1082 | 388.6494 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 140 |  | 87173542 | 2814 | 67.536 | 2.814 | 4.5 | 4.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13756080 | 1098 | 390.1919 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 2 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 141 |  | 87176286 | 2744 | 65.856 | 2.744 | 5.7 | 5.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13757140 | 1060 | 386.2974 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | 143 |  | 87178732 | 2446 | 58.704 | 2.446 | 8.3 | 8.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 13758216 | 1076 | 439.9019 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 |  | 87181972 | 3240 | 77.76 | 3.24 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13759314 | 1098 | 338.8889 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 76 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 128 |  | 87185594 | 3622 | 86.928 | 3.622 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1157 | 0 | N/A | N/A | N/A | 13760397 | 1083 | 299.0061 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 73 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 141 |  | 87189658 | 4064 | 97.536 | 4.064 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13761486 | 1089 | 267.9626 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 73 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 125 |  | 87194012 | 4354 | 104.496 | 4.354 | 9.2 | 9.2 | 3B+1S | 0 | 1138 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13762644 | 1158 | 265.9623 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 71 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 124 |  | 87198629 | 4617 | 110.808 | 4.617 | 8.2 | 8.2 | 3B+1S | 0 | 1189 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13763912 | 1268 | 274.6372 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 71 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 125 |  | 87203022 | 4393 | 105.432 | 4.393 | 7.2 | 7.2 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13765194 | 1282 | 291.8279 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.06 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 70 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 124 |  | 87207313 | 4291 | 102.984 | 4.291 | 6.1 | 6.1 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13766473 | 1279 | 298.0657 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 68 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 121 |  | 87211364 | 4051 | 97.224 | 4.051 | 4.9 | 4.9 | 3B+1S | 0 | 1188 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13767757 | 1284 | 316.9588 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 68 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 122 |  | 87215707 | 4343 | 104.232 | 4.343 | 4 | 4 | 3B+1S | 0 | 1146 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13769030 | 1273 | 293.1154 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 130 |  | 87219711 | 4004 | 96.096 | 4.004 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13770273 | 1243 | 310.4396 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 87223560 | 3849 | 92.376 | 3.849 | 3 | 3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13771413 | 1140 | 296.1808 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 131 |  | 87227403 | 3843 | 92.232 | 3.843 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13772575 | 1162 | 302.3679 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 87231488 | 4085 | 98.04 | 4.085 | 2.4 | 2.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13773744 | 1169 | 284.4553 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 87235240 | 3752 | 90.048 | 3.752 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13774904 | 1160 | 311.5672 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 87239118 | 3878 | 93.072 | 3.878 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13776065 | 1161 | 299.3811 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 126 |  | 87242987 | 3869 | 92.856 | 3.869 | 1.5 | 1.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13777244 | 1179 | 304.7299 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 130 |  | 87246866 | 3879 | 93.096 | 3.879 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13778369 | 1125 | 290.0232 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 |  | 87250544 | 3678 | 88.272 | 3.678 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13779462 | 1093 | 297.1724 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 68 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 137 |  | 87253788 | 3244 | 77.856 | 3.244 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13780546 | 1084 | 334.1554 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 136 |  | 87256842 | 3054 | 73.296 | 3.054 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13781634 | 1088 | 356.2541 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 88898 | 2133.552 | 88.898 | [13 empty] | 27734 | 311.9755 | [7 empty] | 0 | 0 | 1.0067 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
BP4 - STOPPED @ 4:20 AM DUE TO SHIFTING BP1 OPERATION.
BP1 - STARTED @ 4:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:26 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
WATER SAMPLING / CENTRAL LAB. Res. Chl. 1.07 mg/l BY MR. CHRISTOPHER VIDAD ARRIVE AT 8:11 AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 4, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 8:20 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-05 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26980 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87256842 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13781634 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 142 |  | 87260538 | 3696 | 88.704 | 3.696 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 13782788 | 1154 | 312.2294 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 138 |  | 87263646 | 3108 | 74.592 | 3.108 | 6.8 | 6.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13783974 | 1186 | 381.5959 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 142 |  | 87266980 | 3334 | 80.016 | 3.334 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13785166 | 1192 | 357.5285 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 |  | 87269602 | 2622 | 62.928 | 2.622 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13786090 | 924 | 352.4027 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A.ONG | 13.1 | 124 |  | 87272864 | 3262 | 78.288 | 3.262 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13787150 | 1060 | 324.954 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 13.1 | 133 |  | 87276820 | 3956 | 94.944 | 3.956 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13788287 | 1137 | 287.4115 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.06 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 127 |  | 87281015 | 4195 | 100.68 | 4.195 | 9.1 | 9.1 | 3B+1S | 1026 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13789453 | 1166 | 277.9499 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 87285261 | 4246 | 101.904 | 4.246 | 8.4 | 8.4 | 3B+1S | 1038 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13790661 | 1208 | 284.5031 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 18.4 | 142 |  | 87289566 | 4305 | 103.32 | 4.305 | 7.8 | 7.8 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 13791875 | 1214 | 281.9977 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 141 |  | 87294119 | 4553 | 109.272 | 4.553 | 7.4 | 7.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13793078 | 1203 | 264.2214 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.19 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 141 |  | 87298598 | 4479 | 107.496 | 4.479 | 7 | 7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13794288 | 1210 | 270.1496 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 141 |  | 87303052 | 4454 | 106.896 | 4.454 | 6.7 | 6.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13795507 | 1219 | 273.6866 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 4 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 19 | A ONG | 17.5 | 141 |  | 87307593 | 4541 | 108.984 | 4.541 | 6.4 | 6.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13796708 | 1201 | 264.4792 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 17.3 | 145 |  | 87312214 | 4621 | 110.904 | 4.621 | 6.3 | 6.3 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13797957 | 1249 | 270.2878 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 16.9 | 146 |  | 87316401 | 4187 | 100.488 | 4.187 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1167 | 0 | N/A | N/A | N/A | 13799123 | 1166 | 278.481 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.7 | 145 |  | 87320580 | 4179 | 100.296 | 4.179 | 6.2 | 6.2 | 3B+1S | 1005 | 0 | 1127 | 1185 | 1127 | 0 | N/A | N/A | N/A | 13800177 | 1054 | 252.2134 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.7 | 146 |  | 87324870 | 4290 | 102.96 | 4.29 | 6.2 | 6.2 | 3B | 0 | 0 | 1147 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13801243 | 1066 | 245.6876 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 3 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.7 | 146 |  | 87329440 | 4570 | 109.68 | 4.57 | 6.2 | 6.2 | 3B | 0 | 0 | 1147 | 1185 | 1147 | 0 | N/A | N/A | N/A | 13802365 | 1122 | 233.2604 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 139 |  | 87333515 | 4075 | 97.8 | 4.075 | 6.2 | 6.2 | 3B | 0 | 0 | 1098 | 1185 | 1097 | 0 | N/A | N/A | N/A | 13803409 | 1044 | 256.1963 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 137 |  | 87337270 | 3755 | 90.12 | 3.755 | 6.2 | 6.2 | 3B | 0 | 0 | 1127 | 1185 | 1127 | 0 | N/A | N/A | N/A | 13804381 | 972 | 258.8549 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 143 |  | 87341310 | 4040 | 96.96 | 4.04 | 6.2 | 6.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13805434 | 1053 | 260.6436 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 131 |  | 87345646 | 4336 | 104.064 | 4.336 | 6.2 | 6.2 | 3B | 0 | 0 | 1157 | 1185 | 1157 | 0 | N/A | N/A | N/A | 13806574 | 1140 | 262.9151 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 140 |  | 87349186 | 3540 | 84.96 | 3.54 | 6.6 | 6.6 | 3B | 0 | 0 | 1126 | 1185 | 1126 | 0 | N/A | N/A | N/A | 13807568 | 994 | 280.791 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 131 |  | 87352908 | 3722 | 89.328 | 3.722 | 7.2 | 7.2 | 3B | 0 | 0 | 1126 | 1185 | 1096 | 0 | N/A | N/A | N/A | 13808614 | 1046 | 281.0317 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 96066 | 2305.584 | 96.066 | [13 empty] | 26980 | 280.8486 | [7 empty] | 0 | 0 | 1.0567 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:38 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 5, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 4:00 PM DUE TO HIGH DISCHARGE PRESSURE, PARAMETER CAPACITY OF 6.2 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
MR. JIMMY DIOKNO AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 11:10 PM TO PULLOUT FILTER OF VFD 5PCS / ABB FAN 2UNITS / BATTERY VFD 2PCS

## MAR 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY PROVIDENCIA / PAUL G. LABIAN
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-06 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 24824 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87352908 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13808614 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 132 |  | 87355992 | 3084 | 74.016 | 3.084 | 7.7 | 7.7 | 3B | 0 | 0 | 1096 | 1185 | 1097 | 0 | N/A | N/A | N/A | 13809520 | 906 | 293.7743 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 124 |  | 87359004 | 3012 | 72.288 | 3.012 | 8.3 | 8.3 | 3B | 0 | 0 | 1056 | 1185 | 1156 | 0 | N/A | N/A | N/A | 13810424 | 904 | 300.1328 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 129 |  | 87361832 | 2828 | 67.872 | 2.828 | 9 | 9 | 3B | 0 | 0 | 1056 | 1185 | 1056 | 0 | N/A | N/A | N/A | 13811288 | 864 | 305.5163 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 |  | 87364744 | 2912 | 69.888 | 2.912 | 9.5 | 9.5 | 3B | 0 | 0 | 1027 | 1185 | 1127 | 0 | N/A | N/A | N/A | 13812150 | 862 | 296.0165 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 |  | 87367856 | 3112 | 74.688 | 3.112 | 9.5 | 9.5 | 3B | 0 | 0 | 1056 | 1185 | 1136 | 0 | N/A | N/A | N/A | 13813026 | 876 | 281.491 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 |  | 87371855 | 3999 | 95.976 | 3.999 | 9.5 | 9.5 | 3B | 0 | 0 | 1157 | 1185 | 1137 | 0 | N/A | N/A | N/A | 13814020 | 994 | 248.5621 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.09 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 149 |  | 87376230 | 4375 | 105 | 4.375 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13815145 | 1125 | 257.1429 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 142 |  | 87380675 | 4445 | 106.68 | 4.445 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13816300 | 1155 | 259.8425 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 18.4 | 142 |  | 87385050 | 4375 | 105 | 4.375 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13817445 | 1145 | 261.7143 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 147 |  | 87389780 | 4730 | 113.52 | 4.73 | 9.1 | 9.1 | 3B+1S | 0 | 1010 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13818680 | 1235 | 261.0994 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.98 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.7 | 145 |  | 87394264 | 4484 | 107.616 | 4.484 | 8.7 | 8.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13819890 | 1210 | 269.8483 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 143 |  | 87398665 | 4401 | 105.624 | 4.401 | 8.4 | 8.4 | 3B+1S | 0 | 1015 | 1168 | 1185 | 1167 | 0 | N/A | N/A | N/A | 13821069 | 1179 | 267.8937 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 5 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 19 | A ONG | 17.5 | 145 |  | 87403261 | 4596 | 110.304 | 4.596 | 8.2 | 8.2 | 3B | 0 | 0 | 1177 | 1185 | 1177 | 0 | N/A | N/A | N/A | 13822234 | 1165 | 253.4813 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 5 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 62.6761 | 18 | A ONG | 17.3 | 139 |  | 87407715 | 4454 | 106.896 | 4.454 | 8.2 | 8.2 | 3B | 0 | 0 | 1176 | 1185 | 1177 | 0 | N/A | N/A | N/A | 13823362 | 1128 | 253.2555 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 5 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 61.2676 | 18 | A ONG | 16.9 | 140 |  | 87411530 | 3815 | 91.56 | 3.815 | 8.2 | 8.2 | 3B | 0 | 0 | 1096 | 1185 | 1096 | 0 | N/A | N/A | N/A | 13824336 | 974 | 255.308 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 6 | 81 | 57.0423 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 |  | 87415330 | 3800 | 91.2 | 3.8 | 8.2 | 8.2 | 3B | 0 | 0 | 1098 | 1185 | 1096 | 0 | N/A | N/A | N/A | 13825330 | 994 | 261.5789 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 6 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.7 | 140 |  | 87419250 | 3920 | 94.08 | 3.92 | 8.2 | 8.2 | 3B | 0 | 0 | 1097 | 1185 | 1097 | 0 | N/A | N/A | N/A | 13826328 | 998 | 253.5714 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 139 |  | 87423100 | 3850 | 92.4 | 3.85 | 8.2 | 8.2 | 3B | 0 | 0 | 1097 | 1185 | 1097 | 0 | N/A | N/A | N/A | 13827293 | 965 | 259.2208 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.9 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.6 | 140 |  | 87426967 | 3867 | 92.808 | 3.867 | 8.2 | 8.2 | 3B | 0 | 0 | 1097 | 1185 | 1097 | 0 | N/A | N/A | N/A | 13828293 | 1000 | 258.5984 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 139 |  | 87430790 | 3823 | 91.752 | 3.823 | 8.2 | 8.2 | 3B | 0 | 0 | 1097 | 1185 | 1098 | 0 | N/A | N/A | N/A | 13829270 | 977 | 255.5585 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.1 | 142 |  | 87435105 | 4315 | 103.56 | 4.315 | 8.2 | 8.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13830421 | 1151 | 266.7439 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 14 | A ONG | 12.6 | 139 |  | 87439136 | 4031 | 96.744 | 4.031 | 8.2 | 8.2 | 3B | 0 | 0 | 1147 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13831496 | 1075 | 266.6832 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.9 | 130 |  | 87442926 | 3790 | 90.96 | 3.79 | 8.2 | 8.2 | 3B | 0 | 0 | 1107 | 1185 | 1107 | 0 | N/A | N/A | N/A | 13832534 | 1038 | 273.8786 | 0% | 0% | 100% | 100% | 100% | 0% | 10% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A ONG | 11.5 | 122 |  | 87446086 | 3160 | 75.84 | 3.16 | 8.2 | 8.2 | 3B | 0 | 0 | 1076 | 1185 | 1077 | 0 | N/A | N/A | N/A | 13833438 | 904 | 286.0759 | 0% | 0% | 100% | 100% | 100% | 0% | 10% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 93178 | 2236.272 | 93.178 | [13 empty] | 24824 | 266.4148 | [7 empty] | 0 | 0 | 0.98333 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (30%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:40 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 9:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 6, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 12:37 PM DUE TO HIGH DISCHARGE PRESSURE, PARAMETER CAPACITY OF 8.2 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (10%)

## MAR 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-07 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26560 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87446086 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13833438 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.4 | 118 |  | 87449200 | 3114 | 74.736 | 3.114 | 8.2 | 8.2 | 3B | 0 | 0 | 1046 | 1185 | 1046 | 0 | N/A | N/A | N/A | 13834384 | 946 | 303.7893 | 0% | 0% | 100% | 100% | 100% | 0% | 15% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 116 |  | 87452112 | 2912 | 69.888 | 2.912 | 8.3 | 8.3 | 3B | 0 | 0 | 1026 | 1185 | 1006 | 0 | N/A | N/A | N/A | 13835214 | 830 | 285.0275 | 0% | 0% | 100% | 100% | 100% | 0% | 15% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 114 |  | 87455028 | 2916 | 69.984 | 2.916 | 8.5 | 8.5 | 3B | 0 | 0 | 1007 | 1185 | 1007 | 0 | N/A | N/A | N/A | 13836074 | 860 | 294.9246 | 0% | 0% | 100% | 100% | 100% | 0% | 15% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 126 |  | 87457996 | 2968 | 71.232 | 2.968 | 8.9 | 8.9 | 3B | 0 | 0 | 1066 | 1185 | 1066 | 0 | N/A | N/A | N/A | 13836930 | 856 | 288.4097 | 0% | 0% | 100% | 100% | 100% | 0% | 15% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 |  | 87461076 | 3080 | 73.92 | 3.08 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1186 | 0 | N/A | N/A | N/A | 13837912 | 982 | 318.8312 | 0% | 0% | 100% | 100% | 100% | 0% | 15% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 128 |  | 87465068 | 3992 | 95.808 | 3.992 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13839044 | 1132 | 283.5671 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.11 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 126 |  | 87469538 | 4470 | 107.28 | 4.47 | 8.7 | 8.7 | 3B+1S | 1107 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13840280 | 1236 | 276.5101 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 124 |  | 87474033 | 4495 | 107.88 | 4.495 | 7.9 | 7.9 | 3B+1S | 1189 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13841542 | 1262 | 280.7564 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 126 |  | 87478389 | 4356 | 104.544 | 4.356 | 6.8 | 6.8 | 3B+1S | 1189 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 13842812 | 1270 | 291.5519 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 125 |  | 87482775 | 4386 | 105.264 | 4.386 | 5.9 | 5.9 | 3B+1S | 0 | 1157 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13843927 | 1115 | 254.218 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.94 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 124 |  | 87487485 | 4710 | 113.04 | 4.71 | 5 | 5 | 3B+1S | 0 | 1179 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13845153 | 1226 | 260.2972 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 1 | 81 | 57.0423 | 79 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.3 | 123 |  | 87492079 | 4594 | 110.256 | 4.594 | 4 | 4 | 3B+1S | 0 | 1158 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13846386 | 1233 | 268.3936 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | -2 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 126 |  | 87496571 | 4492 | 107.808 | 4.492 | 3.1 | 3.1 | 3B+1S | 0 | 1077 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13847600 | 1214 | 270.2582 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 130 |  | 87500756 | 4185 | 100.44 | 4.185 | 2.7 | 2.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13848777 | 1177 | 281.2425 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 129 |  | 87504945 | 4189 | 100.536 | 4.189 | 2.5 | 2.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13849901 | 1124 | 268.3218 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 129 |  | 87509221 | 4276 | 102.624 | 4.276 | 2.3 | 2.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13851063 | 1162 | 271.7493 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 87513536 | 4315 | 103.56 | 4.315 | 2 | 2 | 3B+1S | 0 | 1025 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13852235 | 1172 | 269.2932 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 87517850 | 4314 | 103.536 | 4.314 | 1.7 | 1.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13853392 | 1157 | 271.6736 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 128 |  | 87522170 | 4320 | 103.68 | 4.32 | 1.4 | 1.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13854560 | 1168 | 270.3704 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 132 |  | 87526373 | 4203 | 100.872 | 4.203 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13855668 | 1108 | 263.6212 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 131 |  | 87530402 | 4029 | 96.696 | 4.029 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13856753 | 1085 | 269.2976 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 87534927 | 4525 | 108.6 | 4.525 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13857908 | 1155 | 255.2486 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 136 |  | 87537894 | 2967 | 71.208 | 2.967 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13858912 | 1004 | 338.3889 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 137 |  | 87541042 | 3148 | 75.552 | 3.148 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13859998 | 1086 | 344.9809 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 94956 | 2278.944 | 94.956 | [13 empty] | 26560 | 279.7085 | [7 empty] | 0 | 0 | 1.0583 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (15%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP 1,BP3, BP2 FAULT @ 9:07 AM RESET @ 9:18 AM
BP2 STARTED @ 9:19 AM
BP4 START @ 9:20 DUE TO BP3 FAULT LINK AB LOST AND TO MEET THE TARGET DISCHARGE PRESSURE.
SP 2 STARTED @ 9:21 AM DUE TO SP1 TRIPLOOP FAULT.
RESUME NORMAL OPERATION @ 9:21 AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 7, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 7:05 PM DUE TO MINIMUM CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / GEORGE O. HERNANDEZ
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-08 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27665 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87541042 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13859998 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 135 |  | 87544394 | 3352 | 80.448 | 3.352 | 4.7 | 4.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13861138 | 1140 | 340.0955 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 134 |  | 87547692 | 3298 | 79.152 | 3.298 | 5.8 | 5.8 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13862214 | 1076 | 326.2583 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.2 | 131 |  | 87551460 | 3768 | 90.432 | 3.768 | 7.2 | 7.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13863442 | 1228 | 325.9023 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 12.8 | 131 |  | 87554120 | 2660 | 63.84 | 2.66 | 8.1 | 8.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13864364 | 922 | 346.6165 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 126 |  | 87557638 | 3518 | 84.432 | 3.518 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13865522 | 1158 | 329.1643 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 135 |  | 87562101 | 4463 | 107.112 | 4.463 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13866637 | 1115 | 249.832 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 126 |  | 87566732 | 4631 | 111.144 | 4.631 | 9 | 9 | 3B+1S | 0 | 1098 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13867809 | 1172 | 253.0771 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 5.5 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 125 |  | 87571593 | 4861 | 116.664 | 4.861 | 8.1 | 8.1 | 3B+1S | 0 | 1128 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13869042 | 1233 | 253.6515 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 124 |  | 87576410 | 4817 | 115.608 | 4.817 | 7.2 | 7.2 | 3B+1S | 0 | 1188 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13870296 | 1254 | 260.328 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 124 |  | 87581226 | 4816 | 115.584 | 4.816 | 6.1 | 6.1 | 3B+1S | 0 | 1168 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13871561 | 1265 | 262.6661 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 123 |  | 87585957 | 4731 | 113.544 | 4.731 | 5.1 | 5.1 | 3B+1S | 0 | 1169 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13872807 | 1246 | 263.3693 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 121 |  | 87590474 | 4517 | 108.408 | 4.517 | 4.2 | 4.2 | 3B+1S | 0 | 1168 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13874070 | 1263 | 279.6104 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 124 |  | 87594807 | 4333 | 103.992 | 4.333 | 3.3 | 3.3 | 3B+1S | 0 | 1097 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13875266 | 1196 | 276.0212 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 87599135 | 4328 | 103.872 | 4.328 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13876413 | 1147 | 265.0185 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 130 |  | 87603238 | 4103 | 98.472 | 4.103 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13877544 | 1131 | 275.652 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 |  | 87607635 | 4397 | 105.528 | 4.397 | 2.5 | 2.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13878717 | 1173 | 266.7728 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 87611862 | 4227 | 101.448 | 4.227 | 2.3 | 2.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13879843 | 1126 | 277.5018 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 87616074 | 4212 | 101.088 | 4.212 | 2 | 2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13880992 | 1149 | 267.3314 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 87620313 | 4239 | 101.736 | 4.239 | 1.8 | 1.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13882132 | 1140 | 268.9314 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 126 |  | 87624504 | 4191 | 100.584 | 4.191 | 1.5 | 1.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13883284 | 1152 | 274.8747 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 75 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | 129 |  | 87628491 | 3987 | 95.688 | 3.987 | 1.3 | 1.3 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13884399 | 1115 | 279.6589 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 126 |  | 87632682 | 4191 | 100.584 | 4.191 | 1.3 | 1.3 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13885501 | 1102 | 262.9444 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 71 | 50 | 72 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 140 |  | 87635946 | 3264 | 78.336 | 3.264 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13886566 | 1065 | 326.2868 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 136 |  | 87639329 | 3383 | 81.192 | 3.383 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13887663 | 1097 | 324.2684 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 98287 | 2358.888 | 98.287 | [13 empty] | 27665 | 281.4716 | [7 empty] | 0 | 0 | 1.0683 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 8, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 8:30 PM DUE TO CRITICAL WATER LEVEL ( 1.3M )
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-09 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27438 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87639329 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13887663 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 144 |  | 87642507 | 3178 | 76.272 | 3.178 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13888761 | 1098 | 345.5003 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 143 |  | 87645560 | 3053 | 73.272 | 3.053 | 6.8 | 6.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13889844 | 1083 | 354.733 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 2 | 71 | 50 | 72 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 144 |  | 87648930 | 3370 | 80.88 | 3.37 | 8.7 | 8.7 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13890970 | 1126 | 334.1246 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 5 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | 113 |  | 87652271 | 3341 | 80.184 | 3.341 | 9.5 | 9.5 | 3B | 0 | 0 | 1115 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13892032 | 1062 | 317.8689 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A.ONG | 13.1 | 124 |  | 87655890 | 3619 | 86.856 | 3.619 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13892995 | 963 | 266.0956 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 135 |  | 87660405 | 4515 | 108.36 | 4.515 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13894134 | 1139 | 252.2702 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 138 |  | 87664889 | 4484 | 107.616 | 4.484 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13895227 | 1093 | 243.7556 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 127 |  | 87669464 | 4575 | 109.8 | 4.575 | 9 | 9 | 3B+1S | 1096 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13896416 | 1189 | 259.8907 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 76 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 123 |  | 87673992 | 4528 | 108.672 | 4.528 | 8.1 | 8.1 | 3B+1S | 1188 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13897618 | 1202 | 265.4594 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.7 | 126 |  | 87679019 | 5027 | 120.648 | 5.027 | 7.1 | 7.1 | 3B+1S | 1189 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13898915 | 1297 | 258.0068 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3.5 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 125 |  | 87683735 | 4716 | 113.184 | 4.716 | 6 | 6 | 3B+1S | 1149 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13900161 | 1246 | 264.207 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 76 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 122 |  | 87688340 | 4605 | 110.52 | 4.605 | 5.2 | 5.2 | 3B+1S | 1138 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13901385 | 1224 | 265.798 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 19 | A ONG | 17.5 | 124 |  | 87692760 | 4420 | 106.08 | 4.42 | 4.5 | 4.5 | 3B+1S | 1076 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13902590 | 1205 | 272.6244 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 128 |  | 87697124 | 4364 | 104.736 | 4.364 | 3.9 | 3.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13903768 | 1178 | 269.9358 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 79 | 55.6338 | 73 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 16.9 | 129 |  | 87701346 | 4222 | 101.328 | 4.222 | 3.5 | 3.5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13904927 | 1159 | 274.5144 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 |  | 87705740 | 4394 | 105.456 | 4.394 | 3.2 | 3.2 | 3B+1S | 1035 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13906071 | 1144 | 260.355 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 127 |  | 87710064 | 4324 | 103.776 | 4.324 | 2.9 | 2.9 | 3B+1S | 1035 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13907224 | 1153 | 264.5698 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 127 |  | 87714506 | 4442 | 106.608 | 4.442 | 2.5 | 2.5 | 3B+1S | 1035 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13908393 | 1169 | 259.5678 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 69 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 |  | 87718731 | 4225 | 101.4 | 4.225 | 2.2 | 2.2 | 3B+1S | 1035 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13909545 | 1152 | 272.6627 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 68 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 126 |  | 87723012 | 4281 | 102.744 | 4.281 | 1.8 | 1.8 | 3B+1S | 1035 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13910701 | 1156 | 270.0304 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 67 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 |  | 87727312 | 4300 | 103.2 | 4.3 | 1.6 | 1.6 | 3B+1S | 1035 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13911839 | 1138 | 264.6512 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 87731503 | 4191 | 100.584 | 4.191 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13912921 | 1082 | 258.1723 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 137 |  | 87735368 | 3865 | 92.76 | 3.865 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13914051 | 1130 | 292.3674 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | 136 |  | 87738615 | 3247 | 77.928 | 3.247 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13915101 | 1050 | 323.3754 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 99286 | 2382.864 | 99.286 | [13 empty] | 27438 | 276.3532 | [7 empty] | 0 | 0 | 1.04 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 9, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:15PM DUE TO PARAMETER CAPACITY ( 1.3M )
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | PAUL G. LABIAN / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-10 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26045 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87738615 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13915101 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 145 |  | 87741957 | 3342 | 80.208 | 3.342 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13915496 | 395 | 118.1927 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 147 |  | 87744955 | 2998 | 71.952 | 2.998 | 6.4 | 6.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13916603 | 1107 | 369.2462 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 144 |  | 87748063 | 3108 | 74.592 | 3.108 | 8.3 | 8.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13917719 | 1116 | 359.0734 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 3 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 |  | 87751495 | 3432 | 82.368 | 3.432 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13918795 | 1076 | 313.5198 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 2 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 116 |  | 87754943 | 3448 | 82.752 | 3.448 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13918795 | 0 | 0 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 131 |  | 87758883 | 3940 | 94.56 | 3.94 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13920289 | 1494 | 379.1878 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.06 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 139 |  | 87763154 | 4271 | 102.504 | 4.271 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13921354 | 1065 | 249.3561 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 132 |  | 87767895 | 4741 | 113.784 | 4.741 | 9.3 | 9.3 | 3B+1S | 0 | 1036 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13922526 | 1172 | 247.2052 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 123 |  | 87772676 | 4781 | 114.744 | 4.781 | 8.5 | 8.5 | 3B+1S | 0 | 1189 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13923743 | 1217 | 254.5493 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 125 |  | 87777439 | 4763 | 114.312 | 4.763 | 7.4 | 7.4 | 3B+1S | 0 | 1187 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13924998 | 1255 | 263.4894 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 76 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 124 |  | 87782209 | 4770 | 114.48 | 4.77 | 6.4 | 6.4 | 3B+1S | 0 | 1189 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13926256 | 1258 | 263.7317 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 120 |  | 87786803 | 4594 | 110.256 | 4.594 | 5.4 | 5.4 | 3B+1S | 0 | 1187 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13927500 | 1244 | 270.788 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 124 |  | 87791261 | 4458 | 106.992 | 4.458 | 4.5 | 4.5 | 3B+1S | 0 | 1097 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13928731 | 1231 | 276.1328 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 127 |  | 87795679 | 4418 | 106.032 | 4.418 | 3.7 | 3.7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13929927 | 1196 | 270.7107 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 72 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 124 |  | 87799885 | 4206 | 100.944 | 4.206 | 3.3 | 3.3 | 3B+1S | 0 | 1045 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13931093 | 1166 | 277.223 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 |  | 87804377 | 4492 | 107.808 | 4.492 | 2.8 | 2.8 | 3B+1S | 0 | 1045 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13932292 | 1199 | 266.919 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 87808577 | 4200 | 100.8 | 4.2 | 2.4 | 2.4 | 3B+1S | 0 | 1045 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13933438 | 1146 | 285.4762 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 69 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 126 |  | 87812910 | 4333 | 103.992 | 4.333 | 1.9 | 1.9 | 3B+1S | 0 | 1045 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13934598 | 1160 | 264.4819 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 126 |  | 87817087 | 4177 | 100.248 | 4.177 | 1.5 | 1.5 | 3B+1S | 0 | 1045 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13935760 | 1162 | 278.1901 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 67 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 130 |  | 87821136 | 4049 | 97.176 | 4.049 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13936834 | 1074 | 265.2507 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -6 | 74 | 52.1127 | 66 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 130 |  | 87825283 | 4147 | 99.528 | 4.147 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13937902 | 1068 | 257.5356 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 87829391 | 4108 | 98.592 | 4.108 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13938972 | 1070 | 260.4674 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 74 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 129 |  | 87832714 | 3323 | 79.752 | 3.323 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13940057 | 1085 | 326.5122 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 131 |  | 87836246 | 3532 | 84.768 | 3.532 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13941146 | 1089 | 308.3239 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 97631 | 2343.144 | 97.631 | [13 empty] | 26045 | 266.7698 | [7 empty] | 0 | 0 | 1.0633 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
ALL PUMP STOPPED @ 12:05 AM DUE TO POWER INTERUPTION
GENSET START @ 12:05 AM
BP4 START @12:07 AM
BP2 START @ 12:09 AM
BP1 START @ 12:10 AM
RESUME NORMAL OPERATION OF GENSET @12:10 AM
RESUME NORMAL OPERATION OF MERALCO @12:45 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
ALL PUMP STOPPED @ 4:30 AM DUE TO POWER INTERUPTION
GENSET START @ 4:30 AM
BP4 START @4:32 AM
BP2 START @ 4:33 AM
BP1 START @ 4:35 AM
RESUME NORMAL OPERATION OF GENSET @4:37 AM
RESUME NORMAL OPERATION OF MERALCO @5:03 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 10, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 7:05PM DUE TO PARAMETER CAPACITY ( 1.3M )
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
MAYNILA A&I LEAD BY MAYNARD PAR ARRIVE @ 7:25PM FOR CONDUCT FULL OUT OLD FLOWMETER AND ISTALL NEW UNIT, TOGETHER WITH ICI PERSONEL.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE

## MAR 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | A.RAYALA II /J. LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-11 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27147 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87836246 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13941146 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 77 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 133 |  | 87839652 | 3406 | 81.744 | 3.406 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13942241 | 1095 | 321.4915 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 79 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 135 |  | 87842993 | 3341 | 80.184 | 3.341 | 6 | 6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13943340 | 1099 | 328.9434 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 80 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 |  | 87846894 | 3901 | 93.624 | 3.901 | 7.4 | 7.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13944444 | 1104 | 283.0044 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 |  | 87850308 | 3414 | 81.936 | 3.414 | 9.5 | 9.5 | 3B | 0 | 0 | 1106 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13945543 | 1099 | 321.9098 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 117 |  | 87853886 | 3578 | 85.872 | 3.578 | 9.5 | 9.5 | 3B | 0 | 0 | 1066 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13946519 | 976 | 272.7781 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 124 |  | 87857830 | 3944 | 94.656 | 3.944 | 9.5 | 9.5 | 3B | 0 | 0 | 987 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13947522 | 1003 | 254.3103 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 136 |  | 87861837 | 4007 | 96.168 | 4.007 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13948501 | 979 | 244.3224 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 133 |  | 87866437 | 4600 | 110.4 | 4.6 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13949608 | 1107 | 240.6522 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 127 |  | 87871112 | 4675 | 112.2 | 4.675 | 8.8 | 8.8 | 3B+1S | 1098 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13950792 | 1184 | 253.262 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 127 |  | 87876108 | 4996 | 119.904 | 4.996 | 7.9 | 7.9 | 3B+1S | 1139 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13952070 | 1278 | 255.8046 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.06 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 126 |  | 87880842 | 4734 | 113.616 | 4.734 | 7 | 7 | 3B+1S | 1157 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13953257 | 1187 | 250.7393 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 124 |  | 87885656 | 4814 | 115.536 | 4.814 | 6 | 6 | 3B+1S | 1156 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13954518 | 1261 | 261.9443 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 19 | A ONG | 17.5 | 122 |  | 87890179 | 4523 | 108.552 | 4.523 | 5 | 5 | 3B+1S | 1158 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13955760 | 1242 | 274.5965 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 126 |  | 87894640 | 4461 | 107.064 | 4.461 | 4.3 | 4.3 | 3B+1S | 1045 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13956991 | 1231 | 275.9471 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 127 |  | 87899021 | 4381 | 105.144 | 4.381 | 3.7 | 3.7 | 3B+1S | 1045 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13958144 | 1153 | 263.1819 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 127 |  | 87903315 | 4294 | 103.056 | 4.294 | 3.2 | 3.2 | 3B+1S | 1045 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13959315 | 1171 | 272.7061 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 127 |  | 87907463 | 4148 | 99.552 | 4.148 | 2.7 | 2.7 | 3B+1S | 1045 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13960485 | 1170 | 282.3047 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 127 |  | 87911820 | 4357 | 104.568 | 4.357 | 2.3 | 2.3 | 3B+1S | 1045 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13961642 | 1157 | 268.5334 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 126 |  | 87916077 | 4257 | 102.168 | 4.257 | 1.9 | 1.9 | 3B+1S | 1045 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13962825 | 1183 | 277.8952 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 69 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 126 |  | 87920449 | 4372 | 104.928 | 4.372 | 1.5 | 1.5 | 3B+1S | 1045 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13963973 | 1148 | 262.5801 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 130 |  | 87924619 | 4170 | 100.08 | 4.17 | 1.3 | 1.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13965053 | 1080 | 258.9928 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 87928620 | 4001 | 96.024 | 4.001 | 1.4 | 1.4 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13966101 | 1048 | 261.9345 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 139 |  | 87932210 | 3590 | 86.16 | 3.59 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13967189 | 1088 | 303.0641 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.5 | 135 |  | 87935750 | 3540 | 84.96 | 3.54 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13968293 | 1104 | 311.8644 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 99504 | 2388.096 | 99.504 | [13 empty] | 27147 | 272.8232 | [7 empty] | 0 | 0 | 1.035 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 11, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
MAINTENANCE TEAM LEAD BY BUNDA GERARDO ARRIVE @ 7:05PM FOR CHECK UP BP2 CHECK VALVE BOLT
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 8:10PM DUE TO PARAMETER CAPACITY ( 1.3M )
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-12 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27360 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 87935750 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13968293 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 144 |  | 87938969 | 3219 | 77.256 | 3.219 | 4.7 | 4.7 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13969374 | 1081 | 335.8186 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 71 | 50 | 71 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 144 |  | 87942215 | 3246 | 77.904 | 3.246 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13970485 | 1111 | 342.2674 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 143 |  | 87945310 | 3095 | 74.28 | 3.095 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13971608 | 1123 | 362.8433 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 3 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | 113 |  | 87948902 | 3592 | 86.208 | 3.592 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13972717 | 1109 | 308.7416 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 2 | 82 | 57.7465 | 81 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 128 |  | 87952526 | 3624 | 86.976 | 3.624 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13973663 | 946 | 261.0375 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 137 |  | 87957039 | 4513 | 108.312 | 4.513 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13974791 | 1128 | 249.9446 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 131 |  | 87961537 | 4498 | 107.952 | 4.498 | 9.4 | 9.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13975901 | 1110 | 246.7763 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 127 |  | 87966332 | 4795 | 115.08 | 4.795 | 8.9 | 8.9 | 3B+1S | 0 | 1097 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13977126 | 1225 | 255.4745 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 125 |  | 87970996 | 4664 | 111.936 | 4.664 | 7.9 | 7.9 | 3B+1S | 0 | 1138 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13978349 | 1223 | 262.2213 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 2 | 81 | 57.0423 | 79 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.7 | 126 |  | 87975730 | 4734 | 113.616 | 4.734 | 7 | 7 | 3B+1S | 0 | 1137 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13979584 | 1235 | 260.8787 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.92 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 127 |  | 87980464 | 4734 | 113.616 | 4.734 | 6.1 | 6.1 | 3B+1S | 0 | 1137 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13980831 | 1247 | 263.4136 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 87984883 | 4419 | 106.056 | 4.419 | 5.6 | 5.6 | 3B+1S | 0 | 1015 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13982009 | 1178 | 266.5761 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 128 |  | 87989098 | 4215 | 101.16 | 4.215 | 5.2 | 5.2 | 3B+1S | 0 | 1016 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13983141 | 1132 | 268.5647 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 129 |  | 87993569 | 4471 | 107.304 | 4.471 | 4.8 | 4.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13984317 | 1176 | 263.0284 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 130 |  | 87997712 | 4143 | 99.432 | 4.143 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13985445 | 1128 | 272.2665 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -2 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 132 |  | 88002148 | 4436 | 106.464 | 4.436 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13986601 | 1156 | 260.5951 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 130 |  | 88006515 | 4367 | 104.808 | 4.367 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13987752 | 1151 | 264.7126 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 88010781 | 4266 | 102.384 | 4.266 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13988906 | 1154 | 269.8078 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88015151 | 4370 | 104.88 | 4.37 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13990048 | 1142 | 261.3272 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -6 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88019421 | 4270 | 102.48 | 4.27 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13991185 | 1137 | 266.2763 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -7 | 75 | 52.8169 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 88023735 | 4314 | 103.536 | 4.314 | 2.6 | 2.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13992337 | 1152 | 267.0376 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -2 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 128 |  | 88027855 | 4120 | 98.88 | 4.12 | 2.3 | 2.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13993466 | 1129 | 274.0291 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 140 |  | 88031377 | 3522 | 84.528 | 3.522 | 3 | 3 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13994564 | 1098 | 311.7547 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 137 |  | 88034805 | 3428 | 82.272 | 3.428 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13995653 | 1089 | 317.6779 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 99055 | 2377.32 | 99.055 | [13 empty] | 27360 | 276.2102 | [7 empty] | 0 | 0 | 1.0633 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:50 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 11, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / REY PROVIDENCIA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-13 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27612 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88034805 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 13995653 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 134 |  | 88038096 | 3291 | 78.984 | 3.291 | 5 | 5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13996750 | 1097 | 333.3333 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A.ONG | 11.2 | 133 |  | 88041535 | 3439 | 82.536 | 3.439 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13997845 | 1095 | 318.4065 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 131 |  | 88044939 | 3404 | 81.696 | 3.404 | 6.8 | 6.8 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 13998927 | 1082 | 317.8613 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 12.8 | 135 |  | 88047995 | 3056 | 73.344 | 3.056 | 8.1 | 8.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14000315 | 1388 | 454.1885 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 2 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 155 |  | 88051775 | 3780 | 90.72 | 3.78 | 9.2 | 9.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14001296 | 981 | 259.5238 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 136 |  | 88055988 | 4213 | 101.112 | 4.213 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14002255 | 959 | 227.6288 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.09 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 129 |  | 88060503 | 4515 | 108.36 | 4.515 | 9.2 | 9.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14003426 | 1171 | 259.3577 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 127 |  | 88065111 | 4608 | 110.592 | 4.608 | 8.5 | 8.5 | 3B+1S | 1067 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14004622 | 1196 | 259.5486 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 128 |  | 88069529 | 4418 | 106.032 | 4.418 | 7.8 | 7.8 | 3B+1S | 1068 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14005844 | 1222 | 276.5957 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 129 |  | 88073797 | 4268 | 102.432 | 4.268 | 7.1 | 7.1 | 3B+1S | 1067 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14007043 | 1199 | 280.9278 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 130 |  | 88078050 | 4253 | 102.072 | 4.253 | 6.4 | 6.4 | 3B+1S | 1067 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14008254 | 1211 | 284.7402 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 88081885 | 3835 | 92.04 | 3.835 | 5.8 | 5.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14009445 | 1191 | 310.5606 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 126 |  | 88086001 | 4116 | 98.784 | 4.116 | 5.2 | 5.2 | 3B+1S | 1046 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14010631 | 1186 | 288.1438 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 129 |  | 88090287 | 4286 | 102.864 | 4.286 | 4.7 | 4.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14011833 | 1202 | 280.448 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 16.9 | 129 |  | 88094560 | 4273 | 102.552 | 4.273 | 4.5 | 4.5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14012990 | 1157 | 270.77 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.7 | 130 |  | 88098735 | 4175 | 100.2 | 4.175 | 4.1 | 4.1 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14014133 | 1143 | 273.7725 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 129 |  | 88102915 | 4180 | 100.32 | 4.18 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14015292 | 1159 | 273.445 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 88102915 | 0 | 0 | 0 | 3.3 | 3.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14016477 | 1185 | #DIV/0! | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88102915 | 0 | 0 | 0 | 3 | 3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14017616 | 1139 | #DIV/0! | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 126 |  | 88102915 | 0 | 0 | 0 | 2.6 | 2.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14018802 | 1186 | #DIV/0! | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -6 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 126 |  | 88102915 | 0 | 0 | 0 | 2.3 | 2.3 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14019924 | 1122 | #DIV/0! | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -3 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 126 |  | 88102915 | 0 | 0 | 0 | 2 | 2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14021049 | 1125 | #DIV/0! | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 140 |  | 88102915 | 0 | 0 | 0 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14022155 | 1106 | #DIV/0! | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 139 |  | 88102915 | 0 | 0 | 0 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14023265 | 1110 | #DIV/0! | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 68110 | 1634.64 | 68.11 | [13 empty] | 27612 | 405.403 | [7 empty] | 0 | 0 | 1.09 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:55 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 13, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
ICI SYSTEMS INC. LEAD BY RALPH BONTO ARRIVE @ 3:30PM FOR INSTALLATION OF TRANSMITTER
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
A&I LEAD BY JAY-R VGONA ARRIVE @ 5:10PM FOR INSTALLATION OF FLOW METER
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-14 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27673 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88102915 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14023265 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 6 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 145 |  | 88102915 | 0 | 0 | 0 | 5.7 | 5.7 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14024392 | 1127 | #DIV/0! | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 144 |  | 88102915 | 0 | 0 | 0 | 7.7 | 7.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14025528 | 1136 | #DIV/0! | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 132 |  | 88104828 | 1913 | 45.912 | 1.913 | 9.1 | 9.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14026626 | 1098 | 573.9676 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 82 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 |  | 88109380 | 4552 | 109.248 | 4.552 | 9.5 | 9.5 | 3B | 0 | 0 | 1115 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14027644 | 1018 | 223.638 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 5 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 124 |  | 88114235 | 4855 | 116.52 | 4.855 | 9.5 | 9.5 | 3B | 0 | 0 | 1150 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14028656 | 1012 | 208.4449 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 128 |  | 88119304 | 5069 | 121.656 | 5.069 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14029789 | 1133 | 223.5155 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.97 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 127 |  | 88124862 | 5558 | 133.392 | 5.558 | 8.9 | 8.9 | 3B+1S | 0 | 1068 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14031005 | 1216 | 218.7837 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 125 |  | 88129540 | 4678 | 112.272 | 4.678 | 8 | 8 | 3B+1S | 0 | 1137 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14032188 | 1183 | 252.8858 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 125 |  | 88134648 | 5108 | 122.592 | 5.108 | 7 | 7 | 3B+1S | 0 | 1156 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14033490 | 1302 | 254.8943 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 126 |  | 88139395 | 4747 | 113.928 | 4.747 | 6.1 | 6.1 | 3B+1S | 0 | 1158 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14034720 | 1230 | 259.111 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 126 |  | 88144262 | 4867 | 116.808 | 4.867 | 5.1 | 5.1 | 3B+1S | 0 | 1159 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14035963 | 1243 | 255.3935 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 88148821 | 4559 | 109.416 | 4.559 | 4.5 | 4.5 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14037146 | 1183 | 259.4867 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 129 |  | 88153305 | 4484 | 107.616 | 4.484 | 4.1 | 4.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14038323 | 1177 | 262.4888 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 129 |  | 88157849 | 4544 | 109.056 | 4.544 | 3.6 | 3.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14039488 | 1165 | 256.382 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 130 |  | 88162579 | 4730 | 113.52 | 4.73 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14040672 | 1184 | 250.3171 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 132 |  | 88167133 | 4554 | 109.296 | 4.554 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14041844 | 1172 | 257.3562 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 88171421 | 4288 | 102.912 | 4.288 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14042975 | 1131 | 273.3209 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88176010 | 4589 | 110.136 | 4.589 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14044158 | 1183 | 246.4589 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 88180484 | 4474 | 107.376 | 4.474 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14045300 | 1142 | 255.2526 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 88184974 | 4490 | 107.76 | 4.49 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14046473 | 1173 | 261.2472 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -6 | 75 | 52.8169 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 88189248 | 4274 | 102.576 | 4.274 | 1.7 | 1.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14047626 | 1153 | 269.7707 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 88193758 | 4510 | 108.24 | 4.51 | 1.5 | 1.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14048744 | 1118 | 247.8936 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | -1 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 140 |  | 88197228 | 3470 | 83.28 | 3.47 | 2.3 | 2.3 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14049831 | 1087 | 313.2565 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 138 |  | 88201025 | 3797 | 91.128 | 3.797 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14050938 | 1107 | 291.546 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 98110 | 2354.64 | 98.11 | [13 empty] | 27673 | 282.061 | [7 empty] | 0 | 0 | 1.0817 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:20 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
PHILIP ROY MELO AND TEAM OF SOUTH MAINTENANCE ARRIVE @7:50 AM TO CONDUCT GENSET 1 & 2 WARM UP FOR 5 MINS.
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 14, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MICROFIX LEAD BY RENATO DUGANG ARRIVE @ 2:45PM FOR TERMINATION OF COPPER CABLE (RJ45) TERMINATION OF FIBER OPTIC AND FLUKE TEST
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / GEORGE O. HERNANDEZ
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-15 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27589 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88201025 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14050938 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 6 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 150 |  | 88204420 | 3395 | 81.48 | 3.395 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14052063 | 1125 | 331.3697 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 141 |  | 88207951 | 3531 | 84.744 | 3.531 | 7.1 | 7.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14053207 | 1144 | 323.9875 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 140 |  | 88211650 | 3699 | 88.776 | 3.699 | 8.8 | 8.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14054298 | 1091 | 294.9446 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 81 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 113 |  | 88216159 | 4509 | 108.216 | 4.509 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14055364 | 1066 | 236.4161 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 5 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 125 |  | 88220950 | 4791 | 114.984 | 4.791 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14056381 | 1017 | 212.273 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 135 |  | 88226276 | 5326 | 127.824 | 5.326 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14057508 | 1127 | 211.6035 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.09 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 129 |  | 88231105 | 4829 | 115.896 | 4.829 | 9.1 | 9.1 | 3B+1S | 1045 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14058647 | 1139 | 235.8666 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 128 |  | 88235899 | 4794 | 115.056 | 4.794 | 8.3 | 8.3 | 3B+1S | 1098 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14059867 | 1220 | 254.4848 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 126 |  | 88240712 | 4813 | 115.512 | 4.813 | 7.5 | 7.5 | 3B+1S | 1139 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14061094 | 1227 | 254.9346 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 128 |  | 88245420 | 4708 | 112.992 | 4.708 | 6.6 | 6.6 | 3B+1S | 1097 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14062319 | 1225 | 260.1954 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 130 |  | 88250321 | 4901 | 117.624 | 4.901 | 5.9 | 5.9 | 3B+1S | 1098 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14063545 | 1226 | 250.153 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 88255070 | 4749 | 113.976 | 4.749 | 5.3 | 5.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14064739 | 1194 | 251.4214 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 128 |  | 88259528 | 4458 | 106.992 | 4.458 | 4.8 | 4.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14065923 | 1184 | 265.59 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 129 |  | 88263822 | 4294 | 103.056 | 4.294 | 4.5 | 4.5 | 3B+1S | 1014 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14067067 | 1144 | 266.4183 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 16.9 | 128 |  | 88268116 | 4294 | 103.056 | 4.294 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14068211 | 1144 | 266.4183 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 |  | 88272413 | 4297 | 103.128 | 4.297 | 3.8 | 3.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14069362 | 1151 | 267.8613 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 88276880 | 4467 | 107.208 | 4.467 | 3.5 | 3.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14070520 | 1158 | 257.6673 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88281527 | 4647 | 111.528 | 4.647 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14071684 | 1164 | 249.193 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88286155 | 4628 | 111.072 | 4.628 | 2.9 | 2.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14072849 | 1165 | 251.7286 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 126 |  | 88290586 | 4431 | 106.344 | 4.431 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14074016 | 1167 | 263.3717 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 125 |  | 88294811 | 4225 | 101.4 | 4.225 | 2.3 | 2.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14075148 | 1132 | 267.929 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 126 |  | 88299293 | 4482 | 107.568 | 4.482 | 2.1 | 2.1 | 3B+1S | 1013 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14076333 | 1185 | 264.3909 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 137 |  | 88302645 | 3352 | 80.448 | 3.352 | 2.8 | 2.8 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14077387 | 1054 | 314.4391 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 133 |  | 88306485 | 3840 | 92.16 | 3.84 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14078527 | 1140 | 296.875 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 105460 | 2531.04 | 105.46 | [13 empty] | 27589 | 261.6063 | [7 empty] | 0 | 0 | 1.1083 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:25 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 15, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-16 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27638 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88306485 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14078527 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.4 | 131 |  | 88309985 | 3500 | 84 | 3.5 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14079575 | 1048 | 299.4286 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.2 | 130 |  | 88313480 | 3495 | 83.88 | 3.495 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14080671 | 1096 | 313.5908 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 142 |  | 88316844 | 3364 | 80.736 | 3.364 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14081775 | 1104 | 328.1807 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 5 | 83 | 58.4507 | 82 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 116 |  | 88320395 | 3551 | 85.224 | 3.551 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14082917 | 1142 | 321.5995 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 4 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 125 |  | 88324963 | 4568 | 109.632 | 4.568 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14083934 | 1017 | 222.6357 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 136 |  | 88330555 | 5592 | 134.208 | 5.592 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14085050 | 1116 | 199.5708 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 129 |  | 88336030 | 5475 | 131.4 | 5.475 | 9.1 | 9.1 | 3B+1S | 0 | 1048 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14086239 | 1189 | 217.1689 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 126 |  | 88340768 | 4738 | 113.712 | 4.738 | 8.2 | 8.2 | 3B+1S | 0 | 1119 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14087463 | 1224 | 258.3369 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 124 |  | 88345606 | 4838 | 116.112 | 4.838 | 7.4 | 7.4 | 3B+1S | 0 | 1147 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14088700 | 1237 | 255.6842 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 127 |  | 88350311 | 4705 | 112.92 | 4.705 | 6.5 | 6.5 | 3B+1S | 0 | 1108 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14089939 | 1239 | 263.3369 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.07 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 126 |  | 88355060 | 4749 | 113.976 | 4.749 | 5.7 | 5.7 | 3B+1S | 0 | 1108 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14091187 | 1248 | 262.7922 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 129 |  | 88359711 | 4651 | 111.624 | 4.651 | 4.9 | 4.9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14092369 | 1182 | 254.1389 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 129 |  | 88364249 | 4538 | 108.912 | 4.538 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14093539 | 1170 | 257.8228 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 128 |  | 88368627 | 4378 | 105.072 | 4.378 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14094708 | 1169 | 267.0169 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -2 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 127 |  | 88372880 | 4253 | 102.072 | 4.253 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14095840 | 1132 | 266.1651 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 132 |  | 88377355 | 4475 | 107.4 | 4.475 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14097030 | 1190 | 265.9218 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 88382100 | 4745 | 113.88 | 4.745 | 3.14 | 3.14 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14098199 | 1169 | 250.7903 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 88386725 | 4625 | 111 | 4.625 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14099376 | 1177 | 252.7568 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 88391340 | 4615 | 110.76 | 4.615 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14100535 | 1159 | 251.1376 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 88395504 | 4164 | 99.936 | 4.164 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14101677 | 1142 | 274.2555 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 88399865 | 4361 | 104.664 | 4.361 | 2 | 2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14102817 | 1140 | 261.4079 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 125 |  | 88404115 | 4250 | 102 | 4.25 | 1.8 | 1.8 | 3B+1S | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14103944 | 1127 | 265.1765 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 3 | 71 | 50 | 75 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 129 |  | 88407688 | 3573 | 85.752 | 3.573 | 2.4 | 2.4 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14105043 | 1099 | 307.5847 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 76 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 131 |  | 88411303 | 3615 | 86.76 | 3.615 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14106165 | 1122 | 310.3734 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 104818 | 2515.632 | 104.818 | [13 empty] | 27638 | 263.6761 | [7 empty] | 0 | 0 | 0.99667 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 16, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
[15 empty] | 10pm - 6am | PAUL G. LABIAN / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-17 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27521 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88411303 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14106165 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 78 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.4 | 133 |  | 88414686 | 3383 | 81.192 | 3.383 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14107247 | 1082 | 319.8345 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 78 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 133 |  | 88418184 | 3498 | 83.952 | 3.498 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14108370 | 1123 | 321.0406 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 0.86 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 79 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 130 |  | 88421483 | 3299 | 79.176 | 3.299 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14109462 | 1092 | 331.0094 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 134 |  | 88424817 | 3334 | 80.016 | 3.334 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14110574 | 1112 | 333.5333 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 |  | 88429503 | 4686 | 112.464 | 4.686 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14111615 | 1041 | 222.1511 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 133 |  | 88434931 | 5428 | 130.272 | 5.428 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14112691 | 1076 | 198.2314 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 130 |  | 88440568 | 5637 | 135.288 | 5.637 | 9.3 | 9.3 | 3B+1S | 1037 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14113812 | 1121 | 198.8646 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 125 |  | 88445699 | 5131 | 123.144 | 5.131 | 8.6 | 8.6 | 3B+1S | 1118 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14115053 | 1241 | 241.8632 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 124 |  | 88450422 | 4723 | 113.352 | 4.723 | 7.7 | 7.7 | 3B+1S | 1148 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14116288 | 1235 | 261.4863 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 125 |  | 88454998 | 4576 | 109.824 | 4.576 | 6.8 | 6.8 | 3B+1S | 1149 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14117528 | 1240 | 270.979 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.94 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 124 |  | 88459755 | 4757 | 114.168 | 4.757 | 5.8 | 5.8 | 3B+1S | 1179 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14118780 | 1252 | 263.1911 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 88464314 | 4559 | 109.416 | 4.559 | 4.9 | 4.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14119996 | 1216 | 266.7252 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 88468848 | 4534 | 108.816 | 4.534 | 4.5 | 4.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14121174 | 1178 | 259.8147 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 88473166 | 4318 | 103.632 | 4.318 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14122352 | 1178 | 272.8115 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 128 |  | 88477487 | 4321 | 103.704 | 4.321 | 3.5 | 3.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14123473 | 1121 | 259.4307 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88482157 | 4670 | 112.08 | 4.67 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14124684 | 1211 | 259.3148 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 88486480 | 4323 | 103.752 | 4.323 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14125825 | 1141 | 280.1295 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88490995 | 4515 | 108.36 | 4.515 | 2.5 | 2.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14126985 | 1160 | 252.7132 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 88495400 | 4405 | 105.72 | 4.405 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14128150 | 1165 | 264.4722 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -7 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 88499946 | 4546 | 109.104 | 4.546 | 2 | 2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14129275 | 1125 | 247.4703 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -7 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 88504404 | 4458 | 106.992 | 4.458 | 1.8 | 1.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14130422 | 1147 | 257.2903 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 127 |  | 88508226 | 3822 | 91.728 | 3.822 | 1.3 | 1.3 | 3B+1S | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14131454 | 1032 | 270.0157 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 136 |  | 88511938 | 3712 | 89.088 | 3.712 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14132622 | 1168 | 314.6552 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 135 |  | 88515502 | 3564 | 85.536 | 3.564 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14133686 | 1064 | 298.541 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 104199 | 2500.776 | 104.199 | [13 empty] | 27521 | 264.1196 | [7 empty] | 0 | 0 | 0.96833 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:00 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 17, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | A.RAYALA II/ D.E CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-18 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27466 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88515502 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14133686 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.4 | 131 |  | 88518906 | 3404 | 81.696 | 3.404 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14134740 | 1054 | 309.6357 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.2 | 131 |  | 88522496 | 3590 | 86.16 | 3.59 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14135854 | 1114 | 310.3064 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A.ONG | 11.2 | 132 |  | 88525882 | 3386 | 81.264 | 3.386 | 6.3 | 6.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14136900 | 1046 | 308.9191 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 12.8 | 132 |  | 88529128 | 3246 | 77.904 | 3.246 | 8.2 | 8.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14138000 | 1100 | 338.8786 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 118 |  | 88533328 | 4200 | 100.8 | 4.2 | 9.5 | 9.5 | 3B | 0 | 0 | 1156 | 0 | 1177 | 1185 | N/A | N/A | N/A | 14139206 | 1206 | 287.1429 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 78 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 |  | 88538751 | 5423 | 130.152 | 5.423 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14140215 | 1009 | 186.0594 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.09 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 138 |  | 88544228 | 5477 | 131.448 | 5.477 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14141297 | 1082 | 197.5534 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | A.RAYALA II/ D.E CAPIÑA
55:00 | 8:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 127 |  | 88550039 | 5811 | 139.464 | 5.811 | 9 | 9 | 3B+1S | 0 | 1088 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14142465 | 1168 | 200.9981 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 126 |  | 88554334 | 4295 | 103.08 | 4.295 | 8.2 | 8.2 | 3B+1S | 0 | 1089 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14143689 | 1224 | 284.9825 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 127 |  | 88558481 | 4147 | 99.528 | 4.147 | 7.3 | 7.3 | 3B+1S | 0 | 1088 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14144910 | 1221 | 294.4297 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 128 |  | 88562596 | 4115 | 98.76 | 4.115 | 6.6 | 6.6 | 3B+1S | 0 | 1088 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14146115 | 1205 | 292.8311 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 88566472 | 3876 | 93.024 | 3.876 | 5.8 | 5.8 | 3B+1S | 0 | 1087 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14147316 | 1201 | 309.8555 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 127 |  | 88570349 | 3877 | 93.048 | 3.877 | 5.1 | 5.1 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14148514 | 1198 | 309.0018 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 88574360 | 4011 | 96.264 | 4.011 | 4.5 | 4.5 | 3B+1S | 0 | 1045 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14149710 | 1196 | 298.18 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 130 |  | 88578200 | 3840 | 92.16 | 3.84 | 4.1 | 4.1 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14150862 | 1152 | 300 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 131 |  | 88582222 | 4022 | 96.528 | 4.022 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14152053 | 1191 | 296.1213 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 88586083 | 3861 | 92.664 | 3.861 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14153210 | 1157 | 308.4693 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88589900 | 3817 | 91.608 | 3.817 | 3 | 3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14154380 | 1170 | 303.1176 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 88593770 | 3870 | 92.88 | 3.87 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14155538 | 1158 | 299.2248 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88597655 | 3885 | 93.24 | 3.885 | 2.4 | 2.4 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14156691 | 1153 | 296.7825 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 88601360 | 3705 | 88.92 | 3.705 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14157822 | 1131 | 305.2632 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 132 |  | 88605532 | 4172 | 100.128 | 4.172 | 2 | 2 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14158992 | 1170 | 280.441 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189
70:00 | 23:00 | 4 | 2.8169 | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 129 |  | 88609766 | 4234 | 101.616 | 4.234 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14160110 | 1118 | 264.0529 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 126 |  | 88613822 | 4056 | 97.344 | 4.056 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14161152 | 1042 | 256.9034 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 98320 | 2359.68 | 98.32 | [13 empty] | 27466 | 279.3531 | [7 empty] | 0 | 0 | 1.0567 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
BP2 - STOPPED @ 4:30 AM DUE TO SHIFTING BP3 OPERATION.
BP3 - STARTED @ 4:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:05 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAINTENANCE TEAM LEAD BY SAMUEL EISMA ARRIVE @ 8AM FOR RE-FILLING OF GRAVEL AT PUMP BASE HOLE OF BP SLOT # 5 & # 6
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 18, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
MR. JIMMY DIOKNO AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 11:00 PM TO CONDUCT MONTHLY PREVENTIVE MAINTENANCE AND REGREASING AND CLEANING SP1 / SP2 / BP2

## MAR 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-19 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27504 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88613822 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14161152 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 131 |  | 88618376 | 4554 | 109.296 | 4.554 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14162348 | 1196 | 262.6263 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 133 |  | 88623104 | 4728 | 113.472 | 4.728 | 7 | 7 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14163588 | 1240 | 262.2673 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A.ONG | 11.2 | 128 |  | 88625986 | 2882 | 69.168 | 2.882 | 7.6 | 7.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14164416 | 828 | 287.3005 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 12.8 | 131 |  | 88629888 | 3902 | 93.648 | 3.902 | 8.8 | 8.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14165514 | 1098 | 281.3942 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 132 |  | 88632948 | 3060 | 73.44 | 3.06 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14166576 | 1062 | 347.0588 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 121 |  | 88638487 | 5539 | 132.936 | 5.539 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14167648 | 1072 | 193.5367 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 120 |  | 88644007 | 5520 | 132.48 | 5.52 | 9 | 9 | 3B+1S | 1037 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14168810 | 1162 | 210.5072 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | A.RAYALA II/ D.E CAPIÑA
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 129 |  | 88647960 | 3953 | 94.872 | 3.953 | 8.4 | 8.4 | 3B+1S | 1036 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14170000 | 1190 | 301.0372 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 105 |  | 88652143 | 4183 | 100.392 | 4.183 | 7.7 | 7.7 | 3B+1S | 1057 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14171207 | 1207 | 288.5489 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 112 |  | 88656078 | 3935 | 94.44 | 3.935 | 7 | 7 | 3B+1S | 1058 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14172412 | 1205 | 306.2262 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.19 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 128 |  | 88660109 | 4031 | 96.744 | 4.031 | 6.4 | 6.4 | 3B+1S | 1057 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 14173609 | 1197 | 296.9486 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 126 |  | 88664226 | 4117 | 98.808 | 4.117 | 5.7 | 5.7 | 3B+1S | 1057 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14174806 | 1197 | 290.7457 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 127 |  | 88668120 | 3894 | 93.456 | 3.894 | 5.1 | 5.1 | 3B+1S | 1046 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14176024 | 1218 | 312.7889 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 127 |  | 88672005 | 3885 | 93.24 | 3.885 | 4.6 | 4.6 | 3B+1S | 1045 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14177203 | 1179 | 303.4749 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 88675762 | 3757 | 90.168 | 3.757 | 4.3 | 4.3 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14178342 | 1139 | 303.1674 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 130 |  | 88679708 | 3946 | 94.704 | 3.946 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14179513 | 1171 | 296.7562 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 88683433 | 3725 | 89.4 | 3.725 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14180648 | 1135 | 314.3624 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 88687255 | 3822 | 91.728 | 3.822 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14181818 | 1170 | 296.9649 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 88690970 | 3715 | 89.16 | 3.715 | 3 | 3 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14182990 | 1172 | 315.4778 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 88694870 | 3900 | 93.6 | 3.9 | 2.7 | 2.7 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14184141 | 1151 | 295.1282 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 88698766 | 3896 | 93.504 | 3.896 | 2.4 | 2.4 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14185300 | 1159 | 297.4846 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 125 |  | 88702512 | 3746 | 89.904 | 3.746 | 2.2 | 2.2 | 3B+1S | 1014 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14186452 | 1152 | 307.528 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 141 |  | 88706444 | 3932 | 94.368 | 3.932 | 3 | 3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14187502 | 1050 | 267.0397 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 132 |  | 88710966 | 4522 | 108.528 | 4.522 | 4.4 | 4.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14188656 | 1154 | 255.1968 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 97144 | 2331.456 | 97.144 | [13 empty] | 27504 | 283.1261 | [7 empty] | 0 | 0 | 1.0083 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:22 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 19, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY PROVIDENCIA / PAUL G. LABIAN
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-20 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 25617 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88710966 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14188656 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 134 |  | 88715166 | 4200 | 100.8 | 4.2 | 5.5 | 5.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14189744 | 1088 | 259.0476 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 132 |  | 88719088 | 3922 | 94.128 | 3.922 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14190842 | 1098 | 279.9592 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A.ONG | 11.2 | 136 |  | 88722748 | 3660 | 87.84 | 3.66 | 7.9 | 7.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14191906 | 1064 | 290.7104 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 12.8 | 134 |  | 88726266 | 3518 | 84.432 | 3.518 | 9 | 9 | 3B | 0 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14192996 | 1090 | 309.8351 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 133 |  | 88730934 | 4668 | 112.032 | 4.668 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14194056 | 1060 | 227.078 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 128 |  | 88736030 | 5096 | 122.304 | 5.096 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14195175 | 1119 | 219.584 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.96 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 126 |  | 88740863 | 4833 | 115.992 | 4.833 | 8.8 | 8.8 | 3B+1S | 0 | 1087 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14196380 | 1205 | 249.3275 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | A.RAYALA II/ D.E CAPIÑA
55:00 | 8:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 130 |  | 88744775 | 3912 | 93.888 | 3.912 | 8.1 | 8.1 | 3B+1S | 0 | 1088 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14197604 | 1224 | 312.8834 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 126 |  | 88748679 | 3904 | 93.696 | 3.904 | 7.3 | 7.3 | 3B+1S | 0 | 1087 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14198814 | 1210 | 309.9385 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 128 |  | 88752613 | 3934 | 94.416 | 3.934 | 6.5 | 6.5 | 3B+1S | 0 | 1087 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14198814 | 0 | 0 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 128 |  | 88756550 | 3937 | 94.488 | 3.937 | 5.6 | 5.6 | 3B+1S | 0 | 1085 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14199284 | 470 | 119.3802 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 124 |  | 88760384 | 3834 | 92.016 | 3.834 | 4.9 | 4.9 | 3B+1S | 0 | 1088 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14200497 | 1213 | 316.3798 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 129 |  | 88764278 | 3894 | 93.456 | 3.894 | 4.3 | 4.3 | 3B+1S | 0 | 1017 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14201670 | 1173 | 301.2327 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 129 |  | 88767945 | 3667 | 88.008 | 3.667 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14202834 | 1164 | 317.4257 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 132 |  | 88771580 | 3635 | 87.24 | 3.635 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14203983 | 1149 | 316.0935 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 132 |  | 88775445 | 3865 | 92.76 | 3.865 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14205142 | 1159 | 299.8706 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88779175 | 3730 | 89.52 | 3.73 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14206315 | 1173 | 310.7239 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88782990 | 3815 | 91.56 | 3.815 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14207446 | 1131 | 307.4705 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88786785 | 3795 | 91.08 | 3.795 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14208596 | 1150 | 303.0303 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88790770 | 3985 | 95.64 | 3.985 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14209792 | 1196 | 300.1255 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 126 |  | 88794400 | 3630 | 87.12 | 3.63 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14210887 | 1095 | 301.6529 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 |  | 88798264 | 3864 | 92.736 | 3.864 | 1.7 | 1.7 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14212048 | 1161 | 300.4658 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.82 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -5 | 71 | 50 | 67 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 136 |  | 88802068 | 3804 | 91.296 | 3.804 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14213148 | 1100 | 289.1693 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | -5 | 71 | 50 | 67 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | 144 |  | 88806270 | 4202 | 100.848 | 4.202 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14214273 | 1125 | 267.7297 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 95304 | 2287.296 | 95.304 | [13 empty] | 25617 | 268.7925 | [7 empty] | 0 | 0 | 0.97 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
MR. MARIO MIRANDA OF SOUTH MAINTENANCE TEAM ARRIVE @ 8:23 AM TO CONDUCT GENSET 1/2 WARM-UP WITH LOAD (430 LITERS) AND REGREASE BP1, BP2. BP4.
GENSET 1/2 WARM-UP DONE @ 10:46 AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 20, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-21 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27291 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88806270 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14214273 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | -2 | 71 | 50 | 67 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | 148 |  | 88810180 | 3910 | 93.84 | 3.91 | 5.1 | 5.1 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14215355 | 1082 | 276.7263 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 0 | 71 | 50 | 67 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 147 |  | 88814165 | 3985 | 95.64 | 3.985 | 7 | 7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14216474 | 1119 | 280.803 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 148 |  | 88818052 | 3887 | 93.288 | 3.887 | 9 | 9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14217605 | 1131 | 290.9699 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 |  | 88822691 | 4639 | 111.336 | 4.639 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 0 | 1126 | 1185 | N/A | N/A | N/A | 14218562 | 957 | 206.2945 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 |  | 88827632 | 4941 | 118.584 | 4.941 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14219548 | 986 | 199.5547 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 134 |  | 88832158 | 4526 | 108.624 | 4.526 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14220630 | 1082 | 239.0632 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 128 |  | 88837190 | 5032 | 120.768 | 5.032 | 9 | 9 | 3B+1S | 1059 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14221810 | 1180 | 234.4992 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | A.RAYALA II/ D.E CAPIÑA
55:00 | 8:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 126 |  | 88841340 | 4150 | 99.6 | 4.15 | 8.2 | 8.2 | 3B+1S | 1097 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14223034 | 1224 | 294.9398 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 126 |  | 88845178 | 3838 | 92.112 | 3.838 | 7.4 | 7.4 | 3B+1S | 1098 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14224245 | 1211 | 315.5289 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 128 |  | 88849200 | 4022 | 96.528 | 4.022 | 6.6 | 6.6 | 3B+1S | 1097 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14225473 | 1228 | 305.3207 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.96 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 127 |  | 88853422 | 4222 | 101.328 | 4.222 | 5.8 | 5.8 | 3B+1S | 1097 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14226699 | 1226 | 290.3837 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 126 |  | 88857506 | 4084 | 98.016 | 4.084 | 5.1 | 5.1 | 3B+1S | 1046 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14227896 | 1197 | 293.095 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 128 |  | 88861240 | 3734 | 89.616 | 3.734 | 4.5 | 4.5 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14229078 | 1182 | 316.5506 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 130 |  | 88864914 | 3674 | 88.176 | 3.674 | 4.2 | 4.2 | 3B+1S | 1014 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14230225 | 1147 | 312.1938 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 129 |  | 88868599 | 3685 | 88.44 | 3.685 | 3.8 | 3.8 | 3B+1S | 1014 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14231405 | 1180 | 320.2171 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 130 |  | 88872365 | 3766 | 90.384 | 3.766 | 3.5 | 3.5 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14232549 | 1144 | 303.7706 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 88876195 | 3830 | 91.92 | 3.83 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14233739 | 1190 | 298.6945 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 88880062 | 3867 | 92.808 | 3.867 | 3 | 3 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14234897 | 1158 | 307.7321 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 88883864 | 3802 | 91.248 | 3.802 | 2.7 | 2.7 | 3B+1S | 1015 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 14236005 | 1108 | 291.4256 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 88887584 | 3720 | 89.28 | 3.72 | 2.4 | 2.4 | 3B+1S | 1013 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14237144 | 1139 | 306.1828 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 88891345 | 3761 | 90.264 | 3.761 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14238289 | 1145 | 304.4403 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 88895252 | 3907 | 93.768 | 3.907 | 1.9 | 1.9 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14239542 | 1253 | 320.7064 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A ONG | 11.9 | 144 |  | 88898502 | 3250 | 78 | 3.25 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14240560 | 1018 | 313.2308 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | 138 |  | 88901746 | 3244 | 77.856 | 3.244 | 4.4 | 4.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14241564 | 1004 | 309.4945 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 95476 | 2291.424 | 95.476 | [13 empty] | 27291 | 285.8415 | [7 empty] | 0 | 0 | 1.0817 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:05 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 21, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / PAUL G. LABIAN
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-22 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27468 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 88901746 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14241564 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 2 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 134 |  | 88904994 | 3248 | 77.952 | 3.248 | 6.2 | 6.2 | 3B | 0 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14242653 | 1089 | 335.2833 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 139 |  | 88910644 | 5650 | 135.6 | 5.65 | 7.2 | 7.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14243900 | 1247 | 220.708 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.2 | 137 |  | 88914876 | 4232 | 101.568 | 4.232 | 8.6 | 8.6 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14245006 | 1106 | 261.3422 | 0% | 0% | 100% | 0% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 113 |  | 88919278 | 4402 | 105.648 | 4.402 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1115 | 1185 | N/A | N/A | N/A | 14246046 | 1040 | 236.2562 | 0% | 0% | 0% | 100% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 127 |  | 88923898 | 4620 | 110.88 | 4.62 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1146 | 1185 | N/A | N/A | N/A | 14247000 | 954 | 206.4935 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 135 |  | 88929610 | 5712 | 137.088 | 5.712 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14248121 | 1121 | 196.2535 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.97 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 128 |  | 88935445 | 5835 | 140.04 | 5.835 | 9.4 | 9.4 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14249256 | 1135 | 194.5159 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | A.RAYALA II/ D.E CAPIÑA
55:00 | 8:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 127 |  | 88941586 | 6141 | 147.384 | 6.141 | 8.7 | 8.7 | 3B+1S | 0 | 1087 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14250469 | 1213 | 197.5248 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 130 |  | 88947750 | 6164 | 147.936 | 6.164 | 7.8 | 7.8 | 3B+1S | 0 | 1118 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14251704 | 1235 | 200.3569 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 126 |  | 88953782 | 6032 | 144.768 | 6.032 | 6.9 | 6.9 | 3B+1S | 0 | 1098 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14252927 | 1223 | 202.752 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.09 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 124 |  | 88959816 | 6034 | 144.816 | 6.034 | 6.2 | 6.2 | 3B+1S | 0 | 1098 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14254151 | 1224 | 202.8505 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 130 |  | 88965708 | 5892 | 141.408 | 5.892 | 5.6 | 5.6 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14255343 | 1192 | 202.3082 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 127 |  | 88971409 | 5701 | 136.824 | 5.701 | 5.1 | 5.1 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14256510 | 1167 | 204.7009 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 128 |  | 88977294 | 5885 | 141.24 | 5.885 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14257721 | 1211 | 205.7774 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 80 | 56.338 | 75 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.9 | 128 |  | 88982540 | 5246 | 125.904 | 5.246 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14258825 | 1104 | 210.4461 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.7 | 130 |  | 88987975 | 5435 | 130.44 | 5.435 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14259945 | 1120 | 206.0718 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 131 |  | 88993812 | 5837 | 140.088 | 5.837 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14261141 | 1196 | 191.8794 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 88999498 | 5686 | 136.464 | 5.686 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14262296 | 1155 | 210.3412 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 |  | 0 | -3 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 |  |  | 89005056 | 5558 | 133.392 | 5.558 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14263436 | 1140 | 205.1098 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 |  | 0 | -3 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 |  |  | 89010437 | 5381 | 129.144 | 5.381 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14264555 | 1119 | 207.9539 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 |  | 89016008 | 5571 | 133.704 | 5.571 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14265722 | 1167 | 209.4777 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 128 |  | 89021466 | 5458 | 130.992 | 5.458 | 2.6 | 2.6 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14266868 | 1146 | 209.967 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 4 | 71 | 50 | 72 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 126 |  | 89025138 | 3672 | 88.128 | 3.672 | 3.5 | 3.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14267906 | 1038 | 282.6797 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 132 |  | 89029896 | 4758 | 114.192 | 4.758 | 4.8 | 4.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14269032 | 1126 | 236.6541 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 128150 | 3075.6 | 128.15 | [13 empty] | 27468 | 214.3426 | [7 empty] | 0 | 0 | 1.0067 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:28 AM, WATER ELEVATION (9.5M)
BP1 - STOPPED @ 3:30 AM DUE TO SHIFTING BP2 OPERATION.
BP2 - STARTED @ 3:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 22, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. JAY-AR PAGNAS AND EMERSON CORPUZ OF TECHNICAL PARAÑAQUE BA ARRIVE @ 12:50 PM TO CONDUCT CLOSE OF VALVE 100 DUE TO VALVE REPLACEMENT AT PASAY SOUTH HIGH SCHOOL.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
FYI: SUCTION FLOWRATE METER CORRUPTED @ 6:20 PM
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-23 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27286 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89029896 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14269032 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.4 | 136 |  | 89034478 | 4582 | 109.968 | 4.582 | 6 | 6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14270122 | 1090 | 237.8874 | 0% | 0% | 0% | 100% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.2 | 139 |  | 89038972 | 4494 | 107.856 | 4.494 | 7.1 | 7.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14271194 | 1072 | 238.5403 | 0% | 0% | 0% | 100% | 100% | 100% | 70% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A.ONG | 11.2 | 138 |  | 89043378 | 4406 | 105.744 | 4.406 | 8.3 | 8.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14272302 | 1108 | 251.4753 | 0% | 0% | 0% | 100% | 100% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 130 |  | 89047798 | 4420 | 106.08 | 4.42 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14273322 | 1020 | 230.7692 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 82 | 57.7465 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 124 |  | 89052626 | 4828 | 115.872 | 4.828 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14274318 | 996 | 206.2966 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 126 |  | 89058023 | 5397 | 129.528 | 5.397 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14275442 | 1124 | 208.2639 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.11 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 127 |  | 89063279 | 5256 | 126.144 | 5.256 | 9.1 | 9.1 | 3B+1S | 0 | 1046 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14276588 | 1146 | 218.0365 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 126 |  | 89068201 | 4922 | 118.128 | 4.922 | 8.4 | 8.4 | 3B+1S | 0 | 1058 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14277806 | 1218 | 247.4604 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 125 |  | 89072966 | 4765 | 114.36 | 4.765 | 7.6 | 7.6 | 3B+1S | 0 | 1118 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14279012 | 1206 | 253.0955 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 126 |  | 89078232 | 5266 | 126.384 | 5.266 | 6.8 | 6.8 | 3B+1S | 0 | 1097 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14280276 | 1264 | 240.0304 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.07 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 129 |  | 89082832 | 4600 | 110.4 | 4.6 | 6 | 6 | 3B+1S | 0 | 1088 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14281443 | 1167 | 253.6957 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 89087390 | 4558 | 109.392 | 4.558 | 5.5 | 5.5 | 3B+1S | 0 | 1035 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14282632 | 1189 | 260.86 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 127 |  | 89091973 | 4583 | 109.992 | 4.583 | 5 | 5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14283830 | 1198 | 261.4008 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 128 |  | 89096445 | 4472 | 107.328 | 4.472 | 4.5 | 4.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14284999 | 1169 | 261.4043 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 129 |  | 89100810 | 4365 | 104.76 | 4.365 | 4.1 | 4.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14286163 | 1164 | 266.6667 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 |  | 89105277 | 4467 | 107.208 | 4.467 | 3.8 | 3.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14287318 | 1155 | 258.5628 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 89109836 | 4559 | 109.416 | 4.559 | 3.5 | 3.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14288482 | 1164 | 253.345 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 89114264 | 4428 | 106.272 | 4.428 | 3.2 | 3.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14289621 | 1139 | 262.8726 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 89118659 | 4395 | 105.48 | 4.395 | 2.8 | 2.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14290757 | 1136 | 258.4755 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 89123229 | 4570 | 109.68 | 4.57 | 2.6 | 2.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14291921 | 1164 | 254.7046 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -6 | 76 | 53.5211 | 68 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 127 |  | 89127708 | 4479 | 107.496 | 4.479 | 2.3 | 2.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14293079 | 1158 | 258.5399 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -2 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 128 |  | 89131824 | 4116 | 98.784 | 4.116 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14294216 | 1137 | 276.2391 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 137 |  | 89135334 | 3510 | 84.24 | 3.51 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14295257 | 1041 | 296.5812 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 138 |  | 89139159 | 3825 | 91.8 | 3.825 | 3.7 | 3.7 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14296318 | 1061 | 277.3856 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 109263 | 2622.312 | 109.263 | [13 empty] | 27286 | 249.7277 | [7 empty] | 0 | 0 | 1.085 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:26 AM,WATER ELEVATION (9.5M)
BP3 - STOPPED @ 3:30 AM DUE TO SHIFTING BP1 OPERATION.
BP1 - STARTED @ 3:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:15 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 23, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
ENGR. DOIKNO JIMMY AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 2:18 PM TO ASSIST ABB
MR. JOHN PAUL DELAS ALAS AND TEAM OF ABB INC. ARRIVE @ 2:24 PM TO CONDUCT PREVENTIVE MAINTENANCE OF ACS1001
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | PAUL G. LABIAN / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-24 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27695 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89139159 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14296318 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 6 | 68 | 47.8873 | 68 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 137 |  | 89142741 | 3582 | 85.968 | 3.582 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14297443 | 1125 | 314.0704 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 139 |  | 89146036 | 3295 | 79.08 | 3.295 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14298525 | 1082 | 328.3763 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 136 |  | 89149571 | 3535 | 84.84 | 3.535 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14299639 | 1114 | 315.1344 | 0% | 0% | 100% | 100% | 0% | 100% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 5 | 83 | 58.4507 | 81 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 |  | 89153945 | 4374 | 104.976 | 4.374 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1146 | 0 | N/A | N/A | N/A | 14300662 | 1023 | 233.882 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 4 | 82 | 57.7465 | 81 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 123 |  | 89158835 | 4890 | 117.36 | 4.89 | 9.5 | 9.5 | 3B | 0 | 0 | 1166 | 1185 | 1166 | 0 | N/A | N/A | N/A | 14301689 | 1027 | 210.0204 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | 135 |  | 89164256 | 5421 | 130.104 | 5.421 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14302774 | 1085 | 200.1476 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 142 |  | 89170041 | 5785 | 138.84 | 5.785 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14303881 | 1107 | 191.357 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 130 |  | 89175464 | 5423 | 130.152 | 5.423 | 9.1 | 9.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14305067 | 1186 | 218.6981 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 125 |  | 89179933 | 4469 | 107.256 | 4.469 | 8.3 | 8.3 | 3B+1S | 0 | 1118 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14306318 | 1251 | 279.9284 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 126 |  | 89184325 | 4392 | 105.408 | 4.392 | 7.4 | 7.4 | 3B+1S | 0 | 1138 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14307544 | 1226 | 279.1439 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.06 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 125 |  | 89188710 | 4385 | 105.24 | 4.385 | 6.5 | 6.5 | 3B+1S | 0 | 1138 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14308806 | 1262 | 287.7993 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 125 |  | 89193227 | 4517 | 108.408 | 4.517 | 5.7 | 5.7 | 3B+1S | 0 | 1087 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14310021 | 1215 | 268.9838 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 126 |  | 89197418 | 4191 | 100.584 | 4.191 | 5 | 5 | 3B+1S | 0 | 1068 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14311238 | 1217 | 290.3842 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 89201770 | 4352 | 104.448 | 4.352 | 4.4 | 4.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14312480 | 1242 | 285.386 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 126 |  | 89206033 | 4263 | 102.312 | 4.263 | 3.9 | 3.9 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14313625 | 1145 | 268.5902 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 123 |  | 89210489 | 4456 | 106.944 | 4.456 | 3.4 | 3.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14314792 | 1167 | 261.8941 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 89214951 | 4462 | 107.088 | 4.462 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14315995 | 1203 | 261.5419 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | DEF | #VALUE! | -3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 89218999 | 4048 | 97.152 | 4.048 | 2.7 | 2.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14317155 | 1160 | 297.1838 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | DEF | #VALUE! | -4 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 89223215 | 4216 | 101.184 | 4.216 | 2.3 | 2.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14318351 | 1196 | 283.6812 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 89227596 | 4381 | 105.144 | 4.381 | 2 | 2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14319537 | 1186 | 270.7144 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | DEF | #VALUE! | -6 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 89231772 | 4176 | 100.224 | 4.176 | 1.7 | 1.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14320685 | 1148 | 274.9042 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -2 | 78 | 54.9296 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 127 |  | 89235498 | 3726 | 89.424 | 3.726 | 1.4 | 1.4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14321801 | 1116 | 299.5169 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 75 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 129 |  | 89238831 | 3333 | 79.992 | 3.333 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14322903 | 1102 | 330.6331 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 131 |  | 89242493 | 3662 | 87.888 | 3.662 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14324013 | 1110 | 303.1131 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 103334 | 2480.016 | 103.334 | [13 empty] | 27695 | 268.0144 | [7 empty] | 0 | 0 | 1.08 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:15 AM,WATER ELEVATION (9.5M)
BP4 - STOPPED @ 3:25 AM DUE TO SHIFTING BP3 OPERATION.
BP3 - STARTED @ 3:26 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 FAILED TO OPERATE @ 7:10 AM DUE TO MOV FAILED TO OPEN.
SP2 - STARTED @ 7:12 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 23, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
FIXE CORP. LEAD BY JAYSON NIOUA ARRIVE @ 8:10PM FOR SPRING/ MISTING
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-25 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27789 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89242493 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14324013 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 75 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 134 |  | 89245840 | 3347 | 80.328 | 3.347 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14325134 | 1121 | 334.9268 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 71 | 50 | 77 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 132 |  | 89249228 | 3388 | 81.312 | 3.388 | 5.7 | 5.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14326249 | 1115 | 329.1027 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 78 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 130 |  | 89252693 | 3465 | 83.16 | 3.465 | 7.1 | 7.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14327344 | 1095 | 316.0173 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 79 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 12.8 | 133 |  | 89256135 | 3442 | 82.608 | 3.442 | 8.5 | 8.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14328457 | 1113 | 323.3585 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 89260338 | 4203 | 100.872 | 4.203 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14329547 | 1090 | 259.3386 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 7 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | DEF |  | 89265976 | 5638 | 135.312 | 5.638 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | 0 | N/A | N/A | N/A | 14330643 | 1096 | 194.3952 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.01 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 138 |  | 89271450 | 5474 | 131.376 | 5.474 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14331696 | 1053 | 192.3639 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 5 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 128 |  | 89277076 | 5626 | 135.024 | 5.626 | 9.1 | 9.1 | 3B+1S | 1067 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14332872 | 1176 | 209.0295 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 127 |  | 89281741 | 4665 | 111.96 | 4.665 | 8.4 | 8.4 | 3B+1S | 1087 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14334099 | 1227 | 263.0225 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 126 |  | 89286284 | 4543 | 109.032 | 4.543 | 7.4 | 7.4 | 3B+1S | 1138 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14335356 | 1257 | 276.6894 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.95 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 127 |  | 89290600 | 4316 | 103.584 | 4.316 | 6.7 | 6.7 | 3B+1S | 1087 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14336581 | 1225 | 283.8276 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 125 |  | 89294687 | 4087 | 98.088 | 4.087 | 6 | 6 | 3B+1S | 1067 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14337791 | 1210 | 296.0607 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 126 |  | 89298980 | 4293 | 103.032 | 4.293 | 5.4 | 5.4 | 3B+1S | 1047 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14338987 | 1196 | 278.5931 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 127 |  | 89303259 | 4279 | 102.696 | 4.279 | 4.8 | 4.8 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14340206 | 1219 | 284.8796 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 127 |  | 89307436 | 4177 | 100.248 | 4.177 | 4.3 | 4.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14341375 | 1169 | 279.8659 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 127 |  | 89311816 | 4380 | 105.12 | 4.38 | 2.7 | 2.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14342554 | 1179 | 269.1781 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 128 |  | 89316012 | 4196 | 100.704 | 4.196 | 3.3 | 3.3 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14343739 | 1185 | 280.9819 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 128 |  | 89320114 | 4102 | 98.448 | 4.102 | 2.9 | 2.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14344925 | 1186 | 288.8835 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 |  | 89324261 | 4147 | 99.528 | 4.147 | 2.5 | 2.5 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14346100 | 1175 | 283.3374 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 77 | 54.2254 | 69 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 127 |  | 89328314 | 4053 | 97.272 | 4.053 | 2.1 | 2.1 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14347315 | 1215 | 299.7779 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 68 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 126 |  | 89332183 | 3869 | 92.856 | 3.869 | 1.8 | 1.8 | 3B+1S | 1035 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14348438 | 1123 | 290.2559 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 126 |  | 89335925 | 3742 | 89.808 | 3.742 | 1.6 | 1.6 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14349590 | 1152 | 307.8568 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 139 |  | 89339349 | 3424 | 82.176 | 3.424 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 14350678 | 1088 | 317.757 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 132 |  | 89342918 | 3569 | 85.656 | 3.569 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14351802 | 1124 | 314.9342 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 100425 | 2410.2 | 100.425 | [13 empty] | 27789 | 276.714 | [7 empty] | 0 | 0 | 0.985 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 7:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MELCHOR O. GIRON AND TEAM OF MAINTENANCE ARRIVE @ 9:55 AM FOR REPLACEMENT OF BALL VALVE 1/2".
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 25, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-26 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27891 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89342918 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14351802 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 6 | 68 | 47.8873 | 67 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 135 |  | 89346422 | 3504 | 84.096 | 3.504 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14352911 | 1109 | 316.4954 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 134 |  | 89349657 | 3235 | 77.64 | 3.235 | 6.4 | 6.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14354052 | 1141 | 352.7048 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 130 |  | 89353138 | 3481 | 83.544 | 3.481 | 8.3 | 8.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14355187 | 1135 | 326.0557 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 4 | 83 | 58.4507 | 81 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 89357406 | 4268 | 102.432 | 4.268 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1167 | 0 | N/A | N/A | N/A | 14356276 | 1089 | 255.1546 | 0% | 0% | 100% | 100% | 100% | 0% | 70% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 3 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | DEF |  | 89362319 | 4913 | 117.912 | 4.913 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | 0 | N/A | N/A | N/A | 14357278 | 1002 | 203.9487 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 134 |  | 89367918 | 5599 | 134.376 | 5.599 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14358413 | 1135 | 202.7148 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.05 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | DEF |  | 89373848 | 5930 | 142.32 | 5.93 | 9 | 9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14359606 | 1193 | 201.1804 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | DEF |  | 89378425 | 4577 | 109.848 | 4.577 | 8.4 | 8.4 | 3B+1S | 0 | 1077 | 1186 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14360843 | 1237 | 270.2644 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | DEF |  | 89382734 | 4309 | 103.416 | 4.309 | 7.7 | 7.7 | 3B+1S | 0 | 1097 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14362045 | 1202 | 278.951 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 2 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 128 |  | 89387148 | 4414 | 105.936 | 4.414 | 6.8 | 6.8 | 3B+1S | 0 | 1097 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14363295 | 1250 | 283.1899 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.97 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 127 |  | 89391461 | 4313 | 103.512 | 4.313 | 6 | 6 | 3B+1S | 0 | 1097 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14364517 | 1222 | 283.3295 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 89395831 | 4370 | 104.88 | 4.37 | 5.4 | 5.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14365706 | 1189 | 272.0824 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 128 |  | 89400149 | 4318 | 103.632 | 4.318 | 4.8 | 4.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14366914 | 1208 | 279.7591 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 129 |  | 89404533 | 4384 | 105.216 | 4.384 | 4.2 | 4.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14368141 | 1227 | 279.8814 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 130 |  | 89408521 | 3988 | 95.712 | 3.988 | 3.8 | 3.8 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14369304 | 1163 | 291.6249 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 131 |  | 89412807 | 4286 | 102.864 | 4.286 | 3.4 | 3.4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14370482 | 1178 | 274.8483 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 89417197 | 4390 | 105.36 | 4.39 | 3 | 3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14371663 | 1181 | 268.3371 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 89421385 | 4188 | 100.512 | 4.188 | 2.7 | 2.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14372853 | 1190 | 281.9962 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -6 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 89425641 | 4256 | 102.144 | 4.256 | 2.3 | 2.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14374034 | 1181 | 277.4906 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -7 | 75 | 52.8169 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 89429925 | 4284 | 102.816 | 4.284 | 2 | 2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14375197 | 1163 | 271.4753 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -8 | 76 | 53.5211 | 68 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 128 |  | 89433911 | 3986 | 95.664 | 3.986 | 1.7 | 1.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14376365 | 1168 | 293.0256 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -9 | 78 | 54.9296 | 67 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 129 |  | 89437812 | 3901 | 93.624 | 3.901 | 1.5 | 1.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14377482 | 1117 | 286.3368 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -5 | 80 | 56.338 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 11.9 | 127 |  | 89441497 | 3685 | 88.44 | 3.685 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14378594 | 1112 | 301.7639 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
71:00 | 24:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | 133 |  | 89444982 | 3485 | 83.64 | 3.485 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14379693 | 1099 | 315.3515 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 102064 | 2449.536 | 102.064 | [13 empty] | 27891 | 273.2697 | [7 empty] | 0 | 0 | 1 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 25, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / REY PROVIDENCIA
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-27 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27787 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89444982 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14379693 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 9 | 76 | 53.5211 | 80 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.4 | 130 |  | 89448330 | 3348 | 80.352 | 3.348 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14380794 | 1101 | 328.853 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 9 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.2 | DEF |  | 89451593 | 3263 | 78.312 | 3.263 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14381871 | 1077 | 330.0644 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 9 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 130 |  | 89455057 | 3464 | 83.136 | 3.464 | 4.7 | 4.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14382946 | 1075 | 310.3349 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 70 | 49.2958 | 80 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 127 |  | 89458451 | 3394 | 81.456 | 3.394 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14384053 | 1107 | 326.1638 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 |  | 89462636 | 4185 | 100.44 | 4.185 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14385183 | 1130 | 270.0119 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 135 |  | 89467843 | 5207 | 124.968 | 5.207 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14386271 | 1088 | 208.9495 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 130 |  | 89473118 | 5275 | 126.6 | 5.275 | 9.2 | 9.2 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14387441 | 1170 | 221.8009 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 89477520 | 4402 | 105.648 | 4.402 | 8.5 | 8.5 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14388656 | 1215 | 276.0109 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 89481914 | 4394 | 105.456 | 4.394 | 7.8 | 7.8 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14389865 | 1209 | 275.1479 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 128 |  | 89486300 | 4386 | 105.264 | 4.386 | 7.1 | 7.1 | 3B+1S | 1077 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14391079 | 1214 | 276.7898 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.19 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 127 |  | 89490718 | 4418 | 106.032 | 4.418 | 6.4 | 6.4 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14392296 | 1217 | 275.464 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 89495044 | 4326 | 103.824 | 4.326 | 5.8 | 5.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14393502 | 1206 | 278.7795 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 126 |  | 89499127 | 4083 | 97.992 | 4.083 | 5.2 | 5.2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14394696 | 1194 | 292.432 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 127 |  | 89503236 | 4109 | 98.616 | 4.109 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14395920 | 1224 | 297.8827 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 126 |  | 89507041 | 3805 | 91.32 | 3.805 | 4.2 | 4.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14397062 | 1142 | 300.1314 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 128 |  | 89511199 | 4158 | 99.792 | 4.158 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14398225 | 1163 | 279.7018 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 89515249 | 4050 | 97.2 | 4.05 | 3.3 | 3.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14399437 | 1212 | 287.1605 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 89519450 | 4201 | 100.824 | 4.201 | 2.9 | 2.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14400623 | 1186 | 288.5027 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 89523568 | 4118 | 98.832 | 4.118 | 2.5 | 2.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14401760 | 1137 | 276.1049 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 89527928 | 4360 | 104.64 | 4.36 | 2.1 | 2.1 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14402954 | 1194 | 273.8532 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 89531808 | 3880 | 93.12 | 3.88 | 1.8 | 1.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14404121 | 1167 | 300.7732 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | -1 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 89535471 | 3663 | 87.912 | 3.663 | 1.5 | 1.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14405265 | 1144 | 312.3123 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | DEF | #VALUE! | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 89538907 | 3436 | 82.464 | 3.436 | 2.1 | 2.1 | 3B | 0 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14406355 | 1090 | 317.2293 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
71:00 | 24:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 89542410 | 3503 | 84.072 | 3.503 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14407480 | 1125 | 321.1533 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 97428 | 2338.272 | 97.428 | [13 empty] | 27787 | 285.2055 | [7 empty] | 0 | 0 | 1.0467 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:18 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
SP1 STOPPED @ 10:40 AM DUE TO SEMI ANNUAL PREVENTIVE MAINTENANCE
SP2 STARTED @ 10:41 AM DUE TO SEMI ANNUAL PREVENTIVE MAINTENANCE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 27, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / REY PROVIDENCIA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-28 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27479 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89542410 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14407480 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 6 | 69 | 48.5915 | 65 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 137 |  | 89545850 | 3440 | 82.56 | 3.44 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14408609 | 1129 | 328.1977 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 5 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 89549215 | 3365 | 80.76 | 3.365 | 5.7 | 5.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14409730 | 1121 | 333.1352 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 5 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 89552603 | 3388 | 81.312 | 3.388 | 7.1 | 7.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14410828 | 1098 | 324.085 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 12.8 | 124 |  | 89555855 | 3252 | 78.048 | 3.252 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14411920 | 1092 | 335.7934 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 3 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | DEF |  | 89560140 | 4285 | 102.84 | 4.285 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14412966 | 1046 | 244.1074 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | DEF |  | 89565283 | 5143 | 123.432 | 5.143 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14414072 | 1106 | 215.0496 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 131 |  | 89570890 | 5607 | 134.568 | 5.607 | 9 | 9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14415249 | 1177 | 209.9162 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 128 |  | 89575620 | 4730 | 113.52 | 4.73 | 8.3 | 8.3 | 3B+1S | 0 | 1067 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14416445 | 1196 | 252.8541 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 129 |  | 89580184 | 4564 | 109.536 | 4.564 | 7.6 | 7.6 | 3B+1S | 0 | 1067 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14417666 | 1221 | 267.5285 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 129 |  | 89584841 | 4657 | 111.768 | 4.657 | 6.8 | 6.8 | 3B+1S | 0 | 1067 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14418890 | 1224 | 262.8301 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.2 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 129 |  | 89589537 | 4696 | 112.704 | 4.696 | 6.1 | 6.1 | 3B+1S | 0 | 1068 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14420097 | 1207 | 257.0273 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 89594208 | 4671 | 112.104 | 4.671 | 5.5 | 5.5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14421280 | 1183 | 253.2648 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 89598962 | 4754 | 114.096 | 4.754 | 4.9 | 4.9 | 3B+1S | 0 | 1036 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14422464 | 1184 | 249.0534 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 126 |  | 89603513 | 4551 | 109.224 | 4.551 | 4.4 | 4.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14423650 | 1186 | 260.6021 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 130 |  | 89607988 | 4475 | 107.4 | 4.475 | 3.8 | 3.8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14424828 | 1178 | 263.2402 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 125 |  | 89612289 | 4301 | 103.224 | 4.301 | 3.3 | 3.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14426022 | 1194 | 277.6099 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 123 |  | 89616280 | 3991 | 95.784 | 3.991 | 2.8 | 2.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14427159 | 1137 | 299.1731 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 123 |  | 89620285 | 4005 | 96.12 | 4.005 | 2.4 | 2.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14428303 | 1144 | 283.8951 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 124 |  | 89624494 | 4209 | 101.016 | 4.209 | 2 | 2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14429466 | 1163 | 276.3127 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 124 |  | 89628635 | 4141 | 99.384 | 4.141 | 1.6 | 1.6 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14430617 | 1151 | 277.9522 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.1 | 129 |  | 89632790 | 4155 | 99.72 | 4.155 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14431738 | 1121 | 269.7954 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 128 |  | 89636884 | 4094 | 98.256 | 4.094 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14432814 | 1076 | 262.8236 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 2 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 141 |  | 89640360 | 3476 | 83.424 | 3.476 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14433866 | 1052 | 302.6467 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
71:00 | 24:00 | 4 | 2.8169 | 2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 139 |  | 89643884 | 3524 | 84.576 | 3.524 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14434959 | 1093 | 310.1589 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 101474 | 2435.376 | 101.474 | [13 empty] | 27479 | 270.7984 | [7 empty] | 0 | 0 | 1.1217 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:20 AM,WATER ELEVATION (9.5M)
BP3 - STOPPED @ 4:30 AM DUE TO SHIFTING BP4 OPERATION.
BP4 - STARTED @ 4:31 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 28, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MAINTENANCE TEAM LEAD BY NOEL NERPIO ARRIVE @ 3:00PM FOR CRANE ELOAD TEST/AND WARM UP GENSET 1 AND 2. NORMAL CONDITION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 8:20 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA/J. LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-29 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27150 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89643884 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14434959 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 7 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | 138 |  | 89647465 | 3581 | 85.944 | 3.581 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14436042 | 1083 | 302.4295 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 137 |  | 89651280 | 3815 | 91.56 | 3.815 | 5.8 | 5.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14437170 | 1128 | 295.675 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 127 |  | 89654940 | 3660 | 87.84 | 3.66 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14438280 | 1110 | 303.2787 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 6 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 145 |  | 89658008 | 3068 | 73.632 | 3.068 | 8.4 | 8.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14439330 | 1050 | 342.2425 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 5 | 83 | 58.4507 | 82 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 |  | 89662302 | 4294 | 103.056 | 4.294 | 9.5 | 9.5 | 3B | 0 | 0 | 1098 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14440406 | 1076 | 250.5822 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 82 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 127 |  | 89667580 | 5278 | 126.672 | 5.278 | 9.5 | 9.5 | 3B | 0 | 0 | 1076 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14441439 | 1033 | 195.7181 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 4 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 139 |  | 89672976 | 5396 | 129.504 | 5.396 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14442434 | 995 | 184.3958 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 143 |  | 89678693 | 5717 | 137.208 | 5.717 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14443517 | 1083 | 189.435 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 3 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 18.4 | 134 |  | 89684639 | 5946 | 142.704 | 5.946 | 9.3 | 9.3 | 3B+1S | 1036 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14444661 | 1144 | 192.3983 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 134 |  | 89690959 | 6320 | 151.68 | 6.32 | 8.7 | 8.7 | 3B+1S | 1046 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14445904 | 1243 | 196.6772 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 128 |  | 89696996 | 6037 | 144.888 | 6.037 | 8 | 8 | 3B+1S | 1068 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14447102 | 1198 | 198.4429 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 124 |  | 89700475 | 3479 | 83.496 | 3.479 | 7.3 | 7.3 | 3B+1S | 1087 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14448303 | 1201 | 345.2141 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 123 |  | 89703870 | 3395 | 81.48 | 3.395 | 6.5 | 6.5 | 3B+1S | 1086 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14449522 | 1219 | 359.0574 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 123 |  | 89709551 | 5681 | 136.344 | 5.681 | 5.7 | 5.7 | 3B+1S | 1067 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14450725 | 1203 | 211.7585 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 16.9 | 127 |  | 89713952 | 4401 | 105.624 | 4.401 | 5.1 | 5.1 | 3B+1S | 1066 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14451896 | 1171 | 266.0759 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 133 |  | 89718606 | 4654 | 111.696 | 4.654 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14453034 | 1138 | 244.5208 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 131 |  | 89723134 | 4528 | 108.672 | 4.528 | 4.3 | 4.3 | 3B+1S | 1017 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14454201 | 1167 | 251.3251 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 89727611 | 4477 | 107.448 | 4.477 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14455361 | 1160 | 260.6656 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 129 |  | 89731957 | 4346 | 104.304 | 4.346 | 3.6 | 3.6 | 3B+1S | 1014 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14456525 | 1164 | 267.8325 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 128 |  | 89736324 | 4367 | 104.808 | 4.367 | 3.3 | 3.3 | 3B+1S | 1014 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14457678 | 1153 | 264.0256 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -2 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.1 | 127 |  | 89740740 | 4416 | 105.984 | 4.416 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14458821 | 1143 | 258.8315 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 1 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A ONG | 12.6 | 128 |  | 89745138 | 4398 | 105.552 | 4.398 | 3 | 3 | 3B | 1014 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14459958 | 1137 | 258.5266 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 11.9 | 133 |  | 89749968 | 4830 | 115.92 | 4.83 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14461022 | 1064 | 220.2899 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
71:00 | 24:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 11.5 | 134 |  | 89754247 | 4279 | 102.696 | 4.279 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14462109 | 1087 | 254.0313 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
[12 empty] | TOTAL | [5 empty] | 110363 | 2648.712 | 110.363 | [13 empty] | 27150 | 246.0064 | [7 empty] | 0 | 0 | 1.0317 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 8:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 29, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. GERRY BUNDA AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 2:35PM FOR PULL OUT OF A-FRAME AND ASSORTED SCRAP.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / GEORGE O. HERNANDEZ
[15 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-30 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26836 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89754247 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14462109 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.4 | 131 |  | 89757964 | 3717 | 89.208 | 3.717 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14463196 | 1087 | 292.4401 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A.ONG | 11.2 | 133 |  | 89761591 | 3627 | 87.048 | 3.627 | 5.8 | 5.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14464295 | 1099 | 303.0052 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.2 | 135 |  | 89765364 | 3773 | 90.552 | 3.773 | 7 | 7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14465425 | 1130 | 299.4964 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 12.8 | 135 |  | 89769335 | 3971 | 95.304 | 3.971 | 8.1 | 8.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14466497 | 1072 | 269.9572 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 3 | 83 | 58.4507 | 82 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 117 |  | 89773197 | 3862 | 92.688 | 3.862 | 9.5 | 9.5 | 3B | 0 | 0 | 1056 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14467566 | 1069 | 276.7996 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 124 |  | 89778384 | 5187 | 124.488 | 5.187 | 9.5 | 9.5 | 3B | 0 | 0 | 996 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14468566 | 1000 | 192.7897 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 135 |  | 89783889 | 5505 | 132.12 | 5.505 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14469577 | 1011 | 183.6512 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 7 | 82 | 57.7465 | 79 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 17.3 | 142 |  | 89789390 | 5501 | 132.024 | 5.501 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14470606 | 1029 | 187.0569 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 142 |  | 89795130 | 5740 | 137.76 | 5.74 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14471716 | 1110 | 193.3798 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 143 |  | 89800837 | 5707 | 136.968 | 5.707 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14472841 | 1125 | 197.1263 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.95 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 134 |  | 89806349 | 5512 | 132.288 | 5.512 | 9 | 9 | 3B+1S | 0 | 1016 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14474039 | 1198 | 217.344 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 89811657 | 5308 | 127.392 | 5.308 | 8.5 | 8.5 | 3B+1S | 0 | 1016 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14475212 | 1173 | 220.9872 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 128 |  | 89816327 | 4670 | 112.08 | 4.67 | 8 | 8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14476399 | 1187 | 254.1756 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 2 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 17.3 | 127 |  | 89820844 | 4517 | 108.408 | 4.517 | 7.5 | 7.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14477592 | 1193 | 264.1133 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 60.5634 | 18 | A ONG | 16.9 | 127 |  | 89826207 | 5363 | 128.712 | 5.363 | 7.1 | 7.1 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14478743 | 1151 | 214.6187 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.7 | 129 |  | 89831780 | 5573 | 133.752 | 5.573 | 6.7 | 6.7 | 3B+1S | 0 | 1026 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14479898 | 1155 | 207.2492 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.7 | 128 |  | 89836511 | 4731 | 113.544 | 4.731 | 6.3 | 6.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14481051 | 1153 | 244.1344 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 |  | 89840948 | 4437 | 106.488 | 4.437 | 6 | 6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14482209 | 1158 | 259.8603 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 0 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.6 | 128 |  | 89845499 | 4551 | 109.224 | 4.551 | 5.6 | 5.6 | 3B+1S | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14483373 | 1164 | 255.768 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -1 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.6 | 126 |  | 89849843 | 4344 | 104.256 | 4.344 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14484527 | 1154 | 265.6538 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -2 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.1 | 125 |  | 89854068 | 4225 | 101.4 | 4.225 | 5 | 5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14485663 | 1136 | 268.8757 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -1 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 14 | A ONG | 12.6 | 126 |  | 89859157 | 5089 | 122.136 | 5.089 | 4.8 | 4.8 | 3B | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14486805 | 1142 | 224.4056 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 11.9 | 134 |  | 89863611 | 4454 | 106.896 | 4.454 | 5.1 | 5.1 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14487868 | 1063 | 238.6619 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
71:00 | 24:00 | DEF | #VALUE! | 1 | 79 | 55.6338 |  | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 11.5 | DEF |  | 89867882 | 4271 | 102.504 | 4.271 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14488945 | 1077 | 252.1658 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
[12 empty] | TOTAL | [5 empty] | 113635 | 2727.24 | 113.635 | [13 empty] | 26836 | 236.1596 | [7 empty] | 0 | 0 | 1.035 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 4:34 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 10:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 30, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAR 31
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / GEORGE O. HERNANDEZ
[15 empty] | 10pm - 6am | PAUL G. LABIAN / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-03-31 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26676 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89867882 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14488945 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A.ONG | 11.4 | 129 |  | 89872533 | 4651 | 111.624 | 4.651 | 6.8 | 6.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14490041 | 1096 | 235.6482 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 6 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A.ONG | 11.2 | 131 |  | 89876954 | 4421 | 106.104 | 4.421 | 7.6 | 7.6 | 3B | 0 | 0 | 1126 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14491078 | 1037 | 234.5623 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A.ONG | 11.2 | 135 |  | 89881145 | 4191 | 100.584 | 4.191 | 8.9 | 8.9 | 3B | 0 | 0 | 1128 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14492108 | 1030 | 245.7647 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 5 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | DEF |  | 89885690 | 4545 | 109.08 | 4.545 | 9.5 | 9.5 | 3B | 0 | 0 | 1044 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14493090 | 982 | 216.0616 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 4 | 83 | 58.4507 | 81 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 119 |  | 89890350 | 4660 | 111.84 | 4.66 | 9.5 | 9.5 | 3B | 0 | 0 | 1046 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14494071 | 981 | 210.515 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | DEF |  | 89895475 | 5125 | 123 | 5.125 | 9.5 | 9.5 | 3B | 0 | 0 | 1015 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14495061 | 990 | 193.1707 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 137 |  | 89900988 | 5513 | 132.312 | 5.513 | 9.5 | 9.5 | 3B | 0 | 0 | 1086 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14496058 | 997 | 180.8453 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN RAYALA II / GEORGE HERNANDEZ
55:00 | 8:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 143 |  | 89906603 | 5615 | 134.76 | 5.615 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14497108 | 1050 | 186.9991 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 132 |  | 89912470 | 5867 | 140.808 | 5.867 | 9.2 | 9.2 | 3B+1S | 1037 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14498244 | 1136 | 193.6254 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | GEORGE O. HERNANDEZ / JONEL V. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 134 |  | 89918625 | 6155 | 147.72 | 6.155 | 8.6 | 8.6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14499466 | 1222 | 198.5378 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.93 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 6 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 132 |  | 89924473 | 5848 | 140.352 | 5.848 | 8 | 8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14500664 | 1198 | 204.8564 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 89929339 | 4866 | 116.784 | 4.866 | 7.4 | 7.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14501839 | 1175 | 241.4714 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 128 |  | 89934086 | 4747 | 113.928 | 4.747 | 6.8 | 6.8 | 3B+1S | 1036 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14503012 | 1173 | 247.1034 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 128 |  | 89938785 | 4699 | 112.776 | 4.699 | 6.3 | 6.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14504233 | 1221 | 259.8425 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 128 |  | 89943061 | 4276 | 102.624 | 4.276 | 5.9 | 5.9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14505350 | 1117 | 261.2254 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 129 |  | 89947550 | 4489 | 107.736 | 4.489 | 5.4 | 5.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14506528 | 1178 | 262.4192 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 128 |  | 89951980 | 4430 | 106.32 | 4.43 | 5.1 | 5.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14507668 | 1140 | 265.9142 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 129 |  | 89956465 | 4485 | 107.64 | 4.485 | 4.7 | 4.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14508831 | 1163 | 254.1806 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 129 |  | 89960881 | 4416 | 105.984 | 4.416 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14509987 | 1156 | 261.7754 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 127 |  | 89965331 | 4450 | 106.8 | 4.45 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14511149 | 1162 | 261.1236 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.1 | 126 |  | 89969676 | 4345 | 104.28 | 4.345 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14512285 | 1136 | 261.4499 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -1 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A ONG | 12.6 | 128 |  | 89974087 | 4411 | 105.864 | 4.411 | 3.5 | 3.5 | 3B+1S | 1014 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14513427 | 1142 | 258.8982 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | 130 |  | 89978147 | 4060 | 97.44 | 4.06 | 4.1 | 4.1 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14514522 | 1095 | 269.7044 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | ARMAN RAYALA II / DYAN ELVIN CAPIÑA
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 130 |  | 89981919 | 3772 | 90.528 | 3.772 | 5 | 5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14515621 | 1099 | 291.3574 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
[12 empty] | TOTAL | [5 empty] | 114037 | 2736.888 | 114.037 | [13 empty] | 26676 | 233.9241 | [7 empty] | 0 | 0 | 1.0283 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (70%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:10 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 8:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( MARCH 31, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)