## APR 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / GEORGE O. HERNANDEZ
WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / PAUL G. LABIAN
[15 empty] | 10pm - 6am | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-01 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27236 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 89981919 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14515621 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.4 | 131 |  | 89985423 | 3504 | 84.096 | 3.504 | 5.8 | 5.8 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14516701 | 1080 | 308.2192 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 78 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 133 |  | 89988758 | 3335 | 80.04 | 3.335 | 7.1 | 7.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14517802 | 1101 | 330.1349 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 79 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 139 |  | 89992023 | 3265 | 78.36 | 3.265 | 8.5 | 8.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14518892 | 1090 | 333.8438 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 114 |  | 89995992 | 3969 | 95.256 | 3.969 | 9.5 | 9.5 | 3B | 0 | 0 | 1116 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14519943 | 1051 | 264.8022 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 119 |  | 90000830 | 4838 | 116.112 | 4.838 | 9.5 | 9.5 | 3b | 0 | 0 | 1115 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14520934 | 991 | 204.8367 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 125 |  | 90006052 | 5222 | 125.328 | 5.222 | 9.5 | 9.5 | 3B | 0 | 0 | 1045 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14521936 | 1002 | 191.8805 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.93 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 79 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 137 |  | 90011369 | 5317 | 127.608 | 5.317 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14522953 | 1017 | 191.2733 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 81 | 57.0423 | 79 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 17.3 | 134 |  | 90017131 | 5762 | 138.288 | 5.762 | 9.4 | 9.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14524086 | 1133 | 196.6331 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 131 |  | 90022920 | 5789 | 138.936 | 5.789 | 8.9 | 8.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14525239 | 1153 | 199.1708 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 131 |  | 90029074 | 6154 | 147.696 | 6.154 | 8.2 | 8.2 | 3B+1S | 0 | 1067 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14526495 | 1256 | 204.0949 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.15 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 131 |  | 90034889 | 5815 | 139.56 | 5.815 | 7.5 | 7.5 | 3B+1S | 0 | 1067 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14527718 | 1223 | 210.3181 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 131 |  | 90040486 | 5597 | 134.328 | 5.597 | 6.9 | 6.9 | 3B+1S | 0 | 1057 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14528936 | 1218 | 217.6166 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 128 |  | 90045396 | 4910 | 117.84 | 4.91 | 6.2 | 6.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14530153 | 1217 | 247.8615 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 3 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 17.3 | 127 |  | 90049940 | 4544 | 109.056 | 4.544 | 5.6 | 5.6 | 3B+1S | 0 | 1055 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14531348 | 1195 | 262.9842 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 131 |  | 90054322 | 4382 | 105.168 | 4.382 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14532513 | 1165 | 265.8603 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.7 | 134 |  | 90058937 | 4615 | 110.76 | 4.615 | 4.9 | 4.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14533683 | 1170 | 253.5211 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 90063458 | 4521 | 108.504 | 4.521 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14534850 | 1167 | 258.7923 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 90067879 | 4421 | 106.104 | 4.421 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14536023 | 1173 | 263.9674 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 130 |  | 90072368 | 4489 | 107.736 | 4.489 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14537187 | 1164 | 259.3005 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 128 |  | 90076594 | 4226 | 101.424 | 4.226 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14538337 | 1150 | 272.1249 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.1 | 127 |  | 90081042 | 4448 | 106.752 | 4.448 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14539497 | 1160 | 260.7914 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -3 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A ONG | 12.6 | 129 |  | 90085365 | 4323 | 103.752 | 4.323 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14540660 | 1163 | 269.0261 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.9 | 137 |  | 90089230 | 3865 | 92.76 | 3.865 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14541776 | 1116 | 288.7451 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM)
71:00 | 24:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 11.5 | 134 |  | 90092885 | 3655 | 87.72 | 3.655 | 4.8 | 4.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14542857 | 1081 | 295.7592 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 110966 | 2663.184 | 110.966 | [13 empty] | 27236 | 245.4446 | [7 empty] | 0 | 0 | 0.97833 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2- CLOSED @ 3:30 AM,WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2- STOPPED @9;00 AM DUE TO PREVENTIVE MAINTENANCE
SP1- STARTED @9;01 AM DUE TO PREVENTIVE MAINTENANCE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 1, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 3.1 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
MR. ERIC CAMUA OF SOUTH MAINTENANCE AND TEAM ARRIVE @ 10:45 PM TO CONDUCT PREVENTIVE MAINETNANCE OF PUMPS.

## APR 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE HERNANDEZ / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / PAUL G. LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-02 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27245 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90092885 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14542857 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 69 | 48.5915 | 67 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 150 |  | 90096248 | 3363 | 80.712 | 3.363 | 6.6 | 6.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14543980 | 1123 | 333.928 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 7 | 69 | 48.5915 | 67 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.2 | 148 |  | 90099300 | 3052 | 73.248 | 3.052 | 8.5 | 8.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14545097 | 1117 | 365.9895 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 108 |  | 90103208 | 3908 | 93.792 | 3.908 | 9.5 | 9.5 | 3B | 0 | 0 | 1045 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14546117 | 1020 | 261.0031 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 110 |  | 90107900 | 4692 | 112.608 | 4.692 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14547100 | 983 | 209.5055 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 |  | 90112601 | 4701 | 112.824 | 4.701 | 9.5 | 9.5 | 3B | 0 | 0 | 1097 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14548080 | 980 | 208.4663 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 |  | 90118103 | 5502 | 132.048 | 5.502 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14549019 | 939 | 170.6652 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 141 |  | 90123894 | 5791 | 138.984 | 5.791 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14550222 | 1203 | 207.7361 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 129 |  | 90130044 | 6150 | 147.6 | 6.15 | 9.1 | 9.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14551456 | 1234 | 200.6504 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 129 |  | 90134650 | 4606 | 110.544 | 4.606 | 8.4 | 8.4 | 3B+1S | 1046 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14552637 | 1181 | 256.4047 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 130 |  | 90139538 | 4888 | 117.312 | 4.888 | 7.8 | 7.8 | 3B+1S | 1046 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14553832 | 1195 | 244.4763 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.87 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 131 |  | 90144275 | 4737 | 113.688 | 4.737 | 7.2 | 7.2 | 3B+1S | 1046 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14555058 | 1226 | 258.8136 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 90148855 | 4580 | 109.92 | 4.58 | 6.6 | 6.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14556254 | 1196 | 261.1354 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 128 |  | 90153228 | 4373 | 104.952 | 4.373 | 6.1 | 6.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14557414 | 1160 | 265.2641 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 128 |  | 90157022 | 3794 | 91.056 | 3.794 | 5.6 | 5.6 | 3b+1s | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14558562 | 1148 | 302.583 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 128 |  | 90161717 | 4695 | 112.68 | 4.695 | 5.3 | 5.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14559729 | 1167 | 248.5623 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 131 |  | 90166135 | 4418 | 106.032 | 4.418 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14560892 | 1163 | 263.2413 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 90170477 | 4342 | 104.208 | 4.342 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14562049 | 1157 | 267.8489 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 90174892 | 4415 | 105.96 | 4.415 | 4.5 | 4.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14563219 | 1170 | 262.0612 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 |  | 90179302 | 4410 | 105.84 | 4.41 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14564385 | 1166 | 264.3991 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 90183632 | 4330 | 103.92 | 4.33 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14565560 | 1175 | 271.3626 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 127 |  | 90187867 | 4235 | 101.64 | 4.235 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14566707 | 1147 | 270.8383 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 129 |  | 90192357 | 4490 | 107.76 | 4.49 | 2.9 | 2.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14567866 | 1159 | 258.1292 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 60 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 140 |  | 90195970 | 3613 | 86.712 | 3.613 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14568959 | 1093 | 302.5187 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 65 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 142 |  | 90199255 | 3285 | 78.84 | 3.285 | 5.7 | 5.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14570102 | 1143 | 347.9452 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 106370 | 2552.88 | 106.37 | [13 empty] | 27245 | 256.1342 | [7 empty] | 0 | 0 | 1.0167 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
XCV2 - CLOSED @ 2:20 AM, WATER ELEVATION (9.5M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 2, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / PAUL G. LABIAN
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / PAUL G. LABIAN
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-03 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 37354 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90199255 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14570102 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 6 | 70 | 49.2958 | 66 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 140 |  | 90202470 | 3215 | 77.16 | 3.215 | 7.8 | 7.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14571246 | 1144 | 355.832 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 81 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 117 |  | 90205975 | 3505 | 84.12 | 3.505 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14577235 | 5989 | 1708.7019 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 81 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 114 |  | 90210855 | 4880 | 117.12 | 4.88 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1098 | 1185 | N/A | N/A | N/A | 14583346 | 6111 | 1252.2541 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 118 |  | 90215625 | 4770 | 114.48 | 4.77 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 14584338 | 992 | 207.9665 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 81 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 |  | 90221290 | 5665 | 135.96 | 5.665 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1146 | 1185 | N/A | N/A | N/A | 14585405 | 1067 | 188.3495 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 132 |  | 90226348 | 5058 | 121.392 | 5.058 | 9.5 | 9.5 | 3b | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14586405 | 1000 | 197.7066 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 134 |  | 90232184 | 5836 | 140.064 | 5.836 | 9.2 | 9.2 | 3B+1S | 0 | 1006 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14587573 | 1168 | 200.1371 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 90238323 | 6139 | 147.336 | 6.139 | 8.6 | 8.6 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14588770 | 1197 | 194.9829 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 129 |  | 90243435 | 5112 | 122.688 | 5.112 | 8 | 8 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14589962 | 1192 | 233.1768 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 128 |  | 90247857 | 4422 | 106.128 | 4.422 | 7.3 | 7.3 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14591179 | 1217 | 275.2148 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.15 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 129 |  | 90252090 | 4233 | 101.592 | 4.233 | 6.6 | 6.6 | 3B+1S | 0 | 1078 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14592366 | 1187 | 280.4158 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 90256838 | 4748 | 113.952 | 4.748 | 5.9 | 5.9 | 3B+1S | 0 | 1056 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14593598 | 1232 | 259.4777 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 127 |  | 90261909 | 5071 | 121.704 | 5.071 | 5.3 | 5.3 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14594787 | 1189 | 234.4705 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 128 |  | 90267771 | 5862 | 140.688 | 5.862 | 4.7 | 4.7 | 3B+1S | 0 | 1035 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14595995 | 1208 | 206.073 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 131 |  | 90273489 | 5718 | 137.232 | 5.718 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14597160 | 1165 | 203.7426 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 135 |  | 90279175 | 5686 | 136.464 | 5.686 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14598344 | 1184 | 208.2307 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 90284860 | 5685 | 136.44 | 5.685 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14599488 | 1144 | 208.2674 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 90290607 | 5747 | 137.928 | 5.747 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14600656 | 1168 | 199.0604 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 90296380 | 5773 | 138.552 | 5.773 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14601828 | 1172 | 203.014 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 132 |  | 90302069 | 5689 | 136.536 | 5.689 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14602990 | 1162 | 204.2538 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 90307618 | 5549 | 133.176 | 5.549 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14604134 | 1144 | 206.1633 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 132 |  | 90313320 | 5702 | 136.848 | 5.702 | 2 | 2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14605321 | 1187 | 208.1726 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -4 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 140 |  | 90318487 | 5167 | 124.008 | 5.167 | 2.2 | 2.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14606393 | 1072 | 207.4705 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 140 |  | 90323052 | 4565 | 109.56 | 4.565 | 3.2 | 3.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14607456 | 1063 | 232.8587 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 123797 | 2971.128 | 123.797 | [13 empty] | 37354 | 301.7359 | [7 empty] | 0 | 0 | 1.0133 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
XCV2 - CLOSED @ 1:45 AM, WATER ELEVATION (9.5M)
BP1 STOPPED @ 2:00 AM DUE TO SHIFT OPERATION BP3
BP3 STARTED @ 2:02 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 3, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-03 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27730 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90323052 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14607456 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | -2 | 70 | 49.2958 | 65 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 145 |  | 90326247 | 3195 | 76.68 | 3.195 | 4.7 | 4.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14608625 | 1169 | 365.8842 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 0 | 71 | 50 | 65 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 145 |  | 90330418 | 4171 | 100.104 | 4.171 | 6.2 | 6.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14609777 | 1152 | 276.1928 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 72 | 50.7042 | 65 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 144 |  | 90335125 | 4707 | 112.968 | 4.707 | 7.9 | 7.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14610950 | 1173 | 249.2033 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 72 | 50.7042 | 65 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | 144 |  | 90339688 | 4563 | 109.512 | 4.563 | 9.2 | 9.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14612056 | 1106 | 242.3844 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 |  | 90344470 | 4782 | 114.768 | 4.782 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14613063 | 1007 | 210.5813 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 137 |  | 90349773 | 5303 | 127.272 | 5.303 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14614122 | 1059 | 199.6983 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 130 |  | 90355713 | 5940 | 142.56 | 5.94 | 9.2 | 9.2 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14615294 | 1172 | 197.3064 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 128 |  | 90361703 | 5990 | 143.76 | 5.99 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14616498 | 1204 | 201.0017 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 128 |  | 90366879 | 5176 | 124.224 | 5.176 | 7.8 | 7.8 | 3B+1S | 1067 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14617691 | 1193 | 230.4869 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 129 |  | 90371513 | 4634 | 111.216 | 4.634 | 7.1 | 7.1 | 3B+1S | 1068 | 0 | 0 | 1185 | 11887 | 1185 | N/A | N/A | N/A | 14618899 | 1208 | 260.6819 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 129 |  | 90377117 | 5604 | 134.496 | 5.604 | 6.4 | 6.4 | 3B+1S | 1067 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14620110 | 1211 | 216.0956 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 90383003 | 5886 | 141.264 | 5.886 | 5.7 | 5.7 | 3B+1S | 1056 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14621307 | 1197 | 203.3639 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 126 |  | 90385992 | 2989 | 71.736 | 2.989 | 5.1 | 5.1 | 3B+1S | 1056 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14622460 | 1153 | 385.7477 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 127 |  | 90385992 | 0 | 0 | 0 | 4.5 | 4.5 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14623696 | 1236 | #DIV/0! | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.22 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 128 |  | 90389778 | 3786 | 90.864 | 3.786 | 4 | 4 | 3B+1S | 1036 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14624867 | 1171 | 309.2974 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 136 |  | 90395366 | 5588 | 134.112 | 5.588 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14626024 | 1157 | 207.0508 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 131 |  | 90400985 | 5619 | 134.856 | 5.619 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14627185 | 1161 | 205.9085 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 90406651 | 5666 | 135.984 | 5.666 | 3 | 3 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14628346 | 1161 | 204.9065 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 90412432 | 5781 | 138.744 | 5.781 | 2.7 | 2.7 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14629521 | 1175 | 203.252 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 90417883 | 5451 | 130.824 | 5.451 | 2.4 | 2.4 | 3B+1S | 1014 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14630660 | 1139 | 208.9525 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | FIDEL RAMOS / REY PROVIDENCIA
68:00 | 21:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 90423375 | 5492 | 131.808 | 5.492 | 2.1 | 2.1 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14631817 | 1157 | 210.6701 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 |  | 90428905 | 5530 | 132.72 | 5.53 | 2 | 2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14632965 | 1148 | 207.5949 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.85 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 130 |  | 90433370 | 4465 | 107.16 | 4.465 | 2.6 | 2.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14634023 | 1058 | 236.9541 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 0 | 70 | 49.2958 | 67 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 142 |  | 90438040 | 4670 | 112.08 | 4.67 | 3.8 | 3.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14635186 | 1163 | 249.0364 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 114988 | 2759.712 | 114.988 | [13 empty] | 27730 | 241.1556 | [7 empty] | 0 | 0 | 1.0767 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:10 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 4, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
ICI SYSTEMS INC. LEAD BY RALPH BONTO ARRIVE @ 10:40PM FOR INSTALLATION OF TRANSMITTER
MARC DAVID KE AND VANESSA ILAGAN ARRIVE @ 2:10 TO BORROW ASSET DOCUMENTS FOR SCANNING.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-05 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27397 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90438040 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14635186 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 0 | 70 | 49.2958 | 67 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 143 |  | 90441583 | 3543 | 85.032 | 3.543 | 5.4 | 5.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14636219 | 1033 | 291.5608 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 142 |  | 90446066 | 4483 | 107.592 | 4.483 | 7 | 7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14637394 | 1175 | 262.1013 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 140 |  | 90450414 | 4348 | 104.352 | 4.348 | 8.4 | 8.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14638510 | 1116 | 256.6697 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 |  | 90454915 | 4501 | 108.024 | 4.501 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1050 | 1185 | N/A | N/A | N/A | 14639562 | 1052 | 233.7258 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 132 |  | 90459715 | 4800 | 115.2 | 4.8 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1097 | 1185 | N/A | N/A | N/A | 14640566 | 1004 | 209.1667 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 135 |  | 90464871 | 5156 | 123.744 | 5.156 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14641600 | 1034 | 200.5431 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.92 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 131 |  | 90470757 | 5886 | 141.264 | 5.886 | 9.3 | 9.3 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14642744 | 1144 | 194.3595 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 90476840 | 6083 | 145.992 | 6.083 | 8.7 | 8.7 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14643955 | 1211 | 199.0794 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 128 |  | 90482630 | 5790 | 138.96 | 5.79 | 8 | 8 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14645157 | 1202 | 207.5993 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 130 |  | 90487260 | 4630 | 111.12 | 4.63 | 7.3 | 7.3 | 3B+1S | 0 | 1048 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14646347 | 1190 | 257.0194 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / REY L. PROVIDENCIA
58:00 | 11:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 130 |  | 90492346 | 5086 | 122.064 | 5.086 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14647551 | 1204 | 236.7283 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 126 |  | 90498098 | 5752 | 138.048 | 5.752 | 6.1 | 6.1 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14648737 | 1186 | 206.1892 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 127 |  | 90503798 | 5700 | 136.8 | 5.7 | 5.5 | 5.5 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14649917 | 1180 | 207.0175 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 130 |  | 90509692 | 5894 | 141.456 | 5.894 | 5 | 5 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14651112 | 1195 | 202.7486 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 128 |  | 90515252 | 5560 | 133.44 | 5.56 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14652278 | 1166 | 209.7122 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.7 | 133 |  | 90520885 | 5633 | 135.192 | 5.633 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14653436 | 1158 | 205.5743 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 128 |  | 90526484 | 5599 | 134.376 | 5.599 | 4 | 4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14654587 | 1151 | 206.8226 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 90532157 | 5673 | 136.152 | 5.673 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14655755 | 1168 | 202.8909 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 |  | 90537863 | 5706 | 136.944 | 5.706 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14656927 | 1172 | 205.3978 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 |  | 90543441 | 5578 | 133.872 | 5.578 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14658069 | 1142 | 204.7329 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.1 | 128 |  | 90548987 | 5546 | 133.104 | 5.546 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14659230 | 1161 | 209.3401 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 130 |  | 90554505 | 5518 | 132.432 | 5.518 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14660375 | 1145 | 207.5027 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 0 | 70 | 49.2958 | 67 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 150 |  | 90559340 | 4835 | 116.04 | 4.835 | 3.2 | 3.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14661474 | 1099 | 227.3009 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 2 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 143 |  | 90563770 | 4430 | 106.32 | 4.43 | 4.8 | 4.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14662583 | 1109 | 250.3386 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 125730 | 3017.52 | 125.73 | [13 empty] | 27397 | 217.9034 | [7 empty] | 0 | 0 | 1.015 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:30 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 5, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.5 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-06 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27288 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90563770 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14662583 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 140 |  | 90567670 | 3900 | 93.6 | 3.9 | 6.5 | 6.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14663683 | 1100 | 282.0513 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 7 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 143 |  | 90572080 | 4410 | 105.84 | 4.41 | 8 | 8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14664827 | 1144 | 259.4104 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 140 |  | 90576320 | 4240 | 101.76 | 4.24 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1095 | 1185 | N/A | N/A | N/A | 14665861 | 1034 | 243.8679 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 125 |  | 90580994 | 4674 | 112.176 | 4.674 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1097 | 1185 | N/A | N/A | N/A | 14666848 | 987 | 211.1682 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 |  | 90585815 | 4821 | 115.704 | 4.821 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1098 | 1185 | N/A | N/A | N/A | 14667845 | 997 | 206.8036 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 136 |  | 90591073 | 5258 | 126.192 | 5.258 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14668890 | 1045 | 198.7448 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 133 |  | 90596899 | 5826 | 139.824 | 5.826 | 9.2 | 9.2 | 3B+1S | 1016 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 14670055 | 1165 | 199.9657 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 129 |  | 90602875 | 5976 | 143.424 | 5.976 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14671244 | 1189 | 198.9625 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 128 |  | 90608449 | 5574 | 133.776 | 5.574 | 7.8 | 7.8 | 3B+1S | 1077 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14672446 | 1202 | 215.6441 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 127 |  | 90612780 | 4331 | 103.944 | 4.331 | 7.1 | 7.1 | 3B+1S | 1077 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14673671 | 1225 | 282.8446 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.09 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 129 |  | 90617062 | 4282 | 102.768 | 4.282 | 6.3 | 6.3 | 3B+1S | 1077 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14674870 | 1199 | 280.0093 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 90621782 | 4720 | 113.28 | 4.72 | 5.6 | 5.6 | 3B+1S | 1057 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14676097 | 1227 | 259.9576 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 19 | A ONG | 17.5 | 126 |  | 90627032 | 5250 | 126 | 5.25 | 5 | 5 | 3B+1S | 1056 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14677244 | 1147 | 218.4762 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 129 |  | 90632914 | 5882 | 141.168 | 5.882 | 4.5 | 4.5 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14678439 | 1195 | 203.1622 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 131 |  | 90638496 | 5582 | 133.968 | 5.582 | 4.2 | 4.2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14679592 | 1153 | 206.5568 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 134 |  | 90644237 | 5741 | 137.784 | 5.741 | 3.8 | 3.8 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14680756 | 1164 | 202.7521 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 90649880 | 5643 | 135.432 | 5.643 | 3.5 | 3.5 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14681920 | 1164 | 206.2733 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 90655349 | 5469 | 131.256 | 5.469 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14683020 | 1100 | 212.836 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 90661074 | 5725 | 137.4 | 5.725 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14684193 | 1173 | 204.8908 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 90666637 | 5563 | 133.512 | 5.563 | 2.5 | 2.5 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14685348 | 1155 | 207.6218 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 127 |  | 90672289 | 5652 | 135.648 | 5.652 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14686501 | 1153 | 203.9986 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 129 |  | 90677797 | 5508 | 132.192 | 5.508 | 2 | 2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14687671 | 1170 | 212.4183 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -2 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 139 |  | 90681555 | 3758 | 90.192 | 3.758 | 2.8 | 2.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14688751 | 1080 | 287.3869 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 144 |  | 90685790 | 4235 | 101.64 | 4.235 | 3.9 | 3.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14689871 | 1120 | 264.4628 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 122020 | 2928.48 | 122.02 | [13 empty] | 27288 | 223.6355 | [7 empty] | 0 | 0 | 0.97333 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 2:50 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 6, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. ERNESTO MONZON AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 3:00 PM TO CONDUCT SEMI ANNUAL PREVENTIVE MAINTENANCE.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
POWER FLUCTUATION @ 5:40 PM. BP2 STOPPED @5:40PM. BP4 STOPPED @ 5:40 PM
PR @ 5:40 PM
RNO 5:46 PM. BP2 RESET @ 5:44 PM. BP4 RESET @ 5:46 PM
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | FIDEL RAMOS / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-07 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27401 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90685790 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14689871 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 139 |  | 90689270 | 3480 | 83.52 | 3.48 | 5.6 | 5.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14690972 | 1101 | 316.3793 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 139 |  | 90693570 | 4300 | 103.2 | 4.3 | 6.8 | 6.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14692072 | 1100 | 255.814 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 8 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 140 |  | 90697918 | 4348 | 104.352 | 4.348 | 8.2 | 8.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14693174 | 1102 | 253.4499 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 113 |  | 90702525 | 4607 | 110.568 | 4.607 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1096 | 1185 | N/A | N/A | N/A | 14694265 | 1091 | 236.8135 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 |  | 90707200 | 4675 | 112.2 | 4.675 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 14695246 | 981 | 209.8396 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 134 |  | 90712240 | 5040 | 120.96 | 5.04 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14696271 | 1025 | 203.373 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.89 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 136 |  | 90717977 | 5737 | 137.688 | 5.737 | 9.4 | 9.4 | 3B+1S | 0 | 1006 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14697394 | 1123 | 195.7469 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 130 |  | 90723954 | 5977 | 143.448 | 5.977 | 8.5 | 8.5 | 3B+1S | 0 | 1046 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 14698578 | 1184 | 198.0927 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 130 |  | 90729601 | 5647 | 135.528 | 5.647 | 8.2 | 8.2 | 3B+1S | 0 | 1068 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14699797 | 1219 | 215.8668 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 90733844 | 4243 | 101.832 | 4.243 | 7.4 | 7.4 | 3B+1S | 0 | 1067 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14701005 | 1208 | 284.7042 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 128 |  | 90738361 | 4517 | 108.408 | 4.517 | 6.7 | 6.7 | 3B+1S | 0 | 1066 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14702228 | 1223 | 270.7549 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 90742883 | 4522 | 108.528 | 4.522 | 6 | 6 | 3B+1S | 0 | 1067 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14703421 | 1193 | 263.8213 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 126 |  | 90747664 | 4781 | 114.744 | 4.781 | 5.2 | 5.2 | 3B+1S | 0 | 1067 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14704641 | 1220 | 255.1767 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 90752765 | 5101 | 122.424 | 5.101 | 4.5 | 4.5 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14705847 | 1206 | 236.4242 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 90758043 | 5278 | 126.672 | 5.278 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14707004 | 1157 | 219.2118 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 90763567 | 5524 | 132.576 | 5.524 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14708176 | 1172 | 212.1651 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 90769129 | 5562 | 133.488 | 5.562 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14709335 | 1159 | 210.7156 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 90774767 | 5638 | 135.312 | 5.638 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14710497 | 1162 | 205.5694 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 |  | 90780378 | 5611 | 134.664 | 5.611 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14711655 | 1158 | 206.3803 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 127 |  | 90785849 | 5471 | 131.304 | 5.471 | 2.3 | 2.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14712804 | 1149 | 210.0165 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 127 |  | 90791332 | 5483 | 131.592 | 5.483 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14713949 | 1145 | 208.8273 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 128 |  | 90797328 | 5996 | 143.904 | 5.996 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14715228 | 1279 | 213.3089 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 130 |  | 90801564 | 4236 | 101.664 | 4.236 | 2.1 | 2.1 | 3B | 0 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 14716196 | 968 | 228.5175 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 2 | 67 | 47.1831 | 73 | Automatic - Pressure Setting | 42.2535 | 43.662 | 47.8873 | 14 | A ONG | 11.5 | 147 |  | 90804508 | 2944 | 70.656 | 2.944 | 3.5 | 3.5 | 3B | 0 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 14717272 | 1076 | 365.4891 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 118718 | 2849.232 | 118.718 | [13 empty] | 27401 | 230.8075 | [7 empty] | 0 | 0 | 1.0217 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:40 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 7, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. ERNESTO MONZON AND SOUTH MAINTENANCE TEAM ARRIVE @ 2:51 PM TO CONDUCT GENSET WARM-UP 1&2 FOR 5MINS.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | REY PROVIDENCIA / FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-08 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27169 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90804508 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14717272 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 68 | 47.8873 | 70 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 145 |  | 90807666 | 3158 | 75.792 | 3.158 | 5.4 | 5.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14718480 | 1208 | 382.5206 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 144 |  | 90810902 | 3236 | 77.664 | 3.236 | 6.8 | 6.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14719518 | 1038 | 320.7664 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 74 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 143 |  | 90815098 | 4196 | 100.704 | 4.196 | 8.5 | 8.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14720610 | 1092 | 260.2479 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 |  | 90819662 | 4564 | 109.536 | 4.564 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1177 | 1185 | N/A | N/A | N/A | 14721654 | 1044 | 228.7467 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 |  | 90824384 | 4722 | 113.328 | 4.722 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1177 | 1185 | N/A | N/A | N/A | 14722650 | 996 | 210.9276 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 81 | 57.0423 | 77 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 126 |  | 90829417 | 5033 | 120.792 | 5.033 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1096 | 1185 | N/A | N/A | N/A | 14723655 | 1005 | 199.6821 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 137 |  | 90834877 | 5460 | 131.04 | 5.46 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1126 | 1185 | N/A | N/A | N/A | 14724670 | 1015 | 185.8974 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 133 |  | 90840866 | 5989 | 143.736 | 5.989 | 9.2 | 9.2 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14725838 | 1168 | 195.0242 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 129 |  | 90846627 | 5761 | 138.264 | 5.761 | 8.6 | 8.6 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14726984 | 1146 | 198.9238 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 131 |  | 90852538 | 5911 | 141.864 | 5.911 | 8 | 8 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14728172 | 1188 | 200.9812 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 129 |  | 90858407 | 5869 | 140.856 | 5.869 | 7.4 | 7.4 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14729369 | 1197 | 203.953 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 90864205 | 5798 | 139.152 | 5.798 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14730551 | 1182 | 203.8634 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 126 |  | 90869955 | 5750 | 138 | 5.75 | 6.1 | 6.1 | 3B+1S | 1047 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 14731751 | 1200 | 208.6957 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 127 |  | 90875927 | 5972 | 143.328 | 5.972 | 5.5 | 5.5 | 3B+1S | 1047 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 14732985 | 1234 | 206.6309 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 128 |  | 90881504 | 5577 | 133.848 | 5.577 | 5 | 5 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14734144 | 1159 | 207.8178 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 127 |  | 90887163 | 5659 | 135.816 | 5.659 | 4.5 | 4.5 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14735301 | 1157 | 204.4531 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 90892814 | 5651 | 135.624 | 5.651 | 4 | 4 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14736464 | 1163 | 204.7425 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 90898478 | 5664 | 135.936 | 5.664 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14737630 | 1166 | 205.3319 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 |  | 90904088 | 5610 | 134.64 | 5.61 | 3.3 | 3.3 | 3B+1S | 1016 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 14738781 | 1151 | 205.1693 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 127 |  | 90909652 | 5564 | 133.536 | 5.564 | 3 | 3 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14739942 | 1161 | 208.6628 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.1 | 128 |  | 90915072 | 5420 | 130.08 | 5.42 | 2.7 | 2.7 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14741078 | 1136 | 209.5941 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 130 |  | 90920854 | 5782 | 138.768 | 5.782 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14742256 | 1178 | 203.7357 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | 139 |  | 90925711 | 4857 | 116.568 | 4.857 | 3.2 | 3.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14743349 | 1093 | 225.036 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 137 |  | 90930461 | 4750 | 114 | 4.75 | 4.3 | 4.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14744441 | 1092 | 229.8947 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD
[12 empty] | TOTAL | [5 empty] | 125953 | 3022.872 | 125.953 | [13 empty] | 27169 | 215.7074 | [7 empty] | 0 | 0 | 1.005 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 7:35 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 8, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE

## APR 9
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-09 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27222 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 90930461 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14744441 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 143 |  | 90934333 | 3872 | 92.928 | 3.872 | 5.4 | 5.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14745548 | 1107 | 285.8988 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 141 |  | 90938484 | 4151 | 99.624 | 4.151 | 6.9 | 6.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14746658 | 1110 | 267.4054 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 140 |  | 90942725 | 4241 | 101.784 | 4.241 | 8.5 | 8.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14747764 | 1106 | 260.7876 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 |  | 90947167 | 4442 | 106.608 | 4.442 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1117 | 1185 | N/A | N/A | N/A | 14748819 | 1055 | 237.5056 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 |  | 90952142 | 4975 | 119.4 | 4.975 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 14749837 | 1018 | 204.6231 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | 129 |  | 90957078 | 4936 | 118.464 | 4.936 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1086 | 1185 | N/A | N/A | N/A | 14750818 | 981 | 198.7439 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | DEF |  | 90962639 | 5561 | 133.464 | 5.561 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 14751854 | 1036 | 186.2974 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 133 |  | 90968615 | 5976 | 143.424 | 5.976 | 9.2 | 9.2 | 3B+1S | 0 | 1025 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14753011 | 1157 | 193.6078 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 132 |  | 90974615 | 6000 | 144 | 6 | 8.7 | 8.7 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14754195 | 1184 | 197.3333 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 134 |  | 90980630 | 6015 | 144.36 | 6.015 | 8.1 | 8.1 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14755385 | 1190 | 197.8387 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 134 |  | 90986523 | 5893 | 141.432 | 5.893 | 7.5 | 7.5 | 3B+1S | 0 | 1027 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 14756585 | 1200 | 203.6314 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 90992517 | 5994 | 143.856 | 5.994 | 7 | 7 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14757774 | 1189 | 198.365 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 19 | A ONG | 17.5 | 127 |  | 90998479 | 5962 | 143.088 | 5.962 | 6.3 | 6.3 | 3B+1S | 0 | 1048 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14758985 | 1211 | 203.1198 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 127 |  | 91004290 | 5811 | 139.464 | 5.811 | 5.6 | 5.6 | 3B+1S | 0 | 1046 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14760187 | 1202 | 206.8491 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 129 |  | 91009976 | 5686 | 136.464 | 5.686 | 5.2 | 5.2 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14761356 | 1169 | 205.5927 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 91015608 | 5632 | 135.168 | 5.632 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14762506 | 1150 | 204.1903 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 91021323 | 5715 | 137.16 | 5.715 | 4.4 | 4.4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14763679 | 1173 | 201.2248 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 91027021 | 5698 | 136.752 | 5.698 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14764837 | 1158 | 205.8617 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 91032684 | 5663 | 135.912 | 5.663 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14765999 | 1162 | 205.1916 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 91038343 | 5659 | 135.816 | 5.659 | 3.1 | 3.1 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14767156 | 1157 | 204.4531 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | DEF | #VALUE! | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 91043917 | 5574 | 133.776 | 5.574 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14768316 | 1160 | 208.1091 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 91049537 | 5620 | 134.88 | 5.62 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14769496 | 1180 | 209.9644 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 134 |  | 91054684 | 5147 | 123.528 | 5.147 | 2.9 | 2.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14770593 | 1097 | 213.1339 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 79 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 136 |  | 91059425 | 4741 | 113.784 | 4.741 | 3.5 | 3.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14771663 | 1070 | 225.6908 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 128964 | 3095.136 | 128.964 | [13 empty] | 27222 | 211.0822 | [7 empty] | 0 | 0 | 1.0283 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:30 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 9, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 10
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / FIDEL A. RAMOS
WATER NETWORK | [14 empty] | 2pm - 10pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-10 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27768 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91059425 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14771663 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 2 | 71 | 50 | 79 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 91062865 | 3440 | 82.56 | 3.44 | 5 | 5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14772765 | 1102 | 320.3488 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 4 | 73 | 51.4085 | 80 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 91067277 | 4412 | 105.888 | 4.412 | 6.4 | 6.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14773868 | 1103 | 250 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 5 | 74 | 52.1127 | 80 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 91071647 | 4370 | 104.88 | 4.37 | 7.8 | 7.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14774974 | 1106 | 253.0892 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 8 | 74 | 52.1127 | 80 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 12.8 | DEF |  | 91076271 | 4624 | 110.976 | 4.624 | 9.2 | 9.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 14776070 | 1096 | 237.0242 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 91080911 | 4640 | 111.36 | 4.64 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14777118 | 1048 | 225.8621 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 136 |  | 91086334 | 5423 | 130.152 | 5.423 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 14778262 | 1144 | 210.9533 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.06 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 124 |  | 91091934 | 5600 | 134.4 | 5.6 | 9 | 9 | 3B+1S | 1188 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14779484 | 1222 | 218.2143 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 91096074 | 4140 | 99.36 | 4.14 | 8.3 | 8.3 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14780618 | 1134 | 273.913 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 128 |  | 91100314 | 4240 | 101.76 | 4.24 | 7.6 | 7.6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14781830 | 1212 | 285.8491 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 91104452 | 4138 | 99.312 | 4.138 | 7 | 7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14783030 | 1200 | 289.9952 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.12 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 91108744 | 4292 | 103.008 | 4.292 | 6.5 | 6.5 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14784252 | 1222 | 284.7158 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 91112562 | 3818 | 91.632 | 3.818 | 6.1 | 6.1 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14785422 | 1170 | 306.4432 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 126 |  | 91116694 | 4132 | 99.168 | 4.132 | 5.6 | 5.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14786616 | 1194 | 288.9642 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 91120933 | 4239 | 101.736 | 4.239 | 5.1 | 5.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14787842 | 1226 | 289.2192 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 123 |  | 91124924 | 3991 | 95.784 | 3.991 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14789044 | 1202 | 301.1776 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 130 |  | 91128854 | 3930 | 94.32 | 3.93 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14790193 | 1149 | 292.3664 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 91132840 | 3986 | 95.664 | 3.986 | 4 | 4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14791395 | 1202 | 288.2589 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 91136875 | 4035 | 96.84 | 4.035 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 14792541 | 1146 | 297.8934 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 91141000 | 4125 | 99 | 4.125 | 3.2 | 3.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14793769 | 1228 | 297.697 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | DEF | #VALUE! | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 91144863 | 3863 | 92.712 | 3.863 | 2.8 | 2.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14794910 | 1141 | 295.3663 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 126 |  | 91148784 | 3921 | 94.104 | 3.921 | 2.5 | 2.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14796063 | 1153 | 294.0576 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 |  | 91152724 | 3940 | 94.56 | 3.94 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14797233 | 1170 | 296.9543 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | DEF | #VALUE! | 2 | 71 | 50 | 76 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 91156405 | 3681 | 88.344 | 3.681 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14798356 | 1123 | 305.0801 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 77 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 91159795 | 3390 | 81.36 | 3.39 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14799431 | 1075 | 317.1091 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 100370 | 2408.88 | 100.37 | [13 empty] | 27768 | 276.6564 | [7 empty] | 0 | 0 | 1.0483 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:05 AM WATER ELEVATION (9.5 M)
BP4 STOP @4:15AM SHIFT OPERATION
BP1 START @ 4:16AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 10, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 11
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-11 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27804 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91159795 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14799431 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 4 | 70 | 49.2958 | 78 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 91163220 | 3425 | 82.2 | 3.425 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14800573 | 1142 | 333.4307 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 5 | 70 | 49.2958 | 79 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 91166901 | 3681 | 88.344 | 3.681 | 6.6 | 6.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14801728 | 1155 | 313.7734 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 6 | 72 | 50.7042 | 79 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 91170876 | 3975 | 95.4 | 3.975 | 8 | 8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14802835 | 1107 | 278.4906 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 120 |  | 91174533 | 3657 | 87.768 | 3.657 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14803965 | 1130 | 308.9964 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 9 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 124 |  | 91178104 | 3571 | 85.704 | 3.571 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14805025 | 1060 | 296.8356 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 77 | 54.2254 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 137 |  | 91183415 | 5311 | 127.464 | 5.311 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14806156 | 1131 | 212.9542 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 91189225 | 5810 | 139.44 | 5.81 | 9.1 | 9.1 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14807350 | 1194 | 205.5077 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 91194523 | 5298 | 127.152 | 5.298 | 8.4 | 8.4 | 3B+1S | 0 | 1058 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14808533 | 1183 | 223.2918 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 127 |  | 91199871 | 5348 | 128.352 | 5.348 | 7.7 | 7.7 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14809766 | 1233 | 230.5535 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | DEEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 91203103 | 3232 | 77.568 | 3.232 | 6.9 | 6.9 | 3B+1S | 0 | 1048 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14810939 | 1173 | 362.9332 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 91206539 | 3436 | 82.464 | 3.436 | 6.2 | 6.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14812166 | 1227 | 357.1013 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 91210670 | 4131 | 99.144 | 4.131 | 5.6 | 5.6 | 3B+1S | 0 | 1046 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14813363 | 1197 | 289.7603 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 91214954 | 4284 | 102.816 | 4.284 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14814555 | 1192 | 278.2446 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 91219277 | 4323 | 103.752 | 4.323 | 4.5 | 4.5 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14815769 | 1214 | 280.8235 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 91223306 | 4029 | 96.696 | 4.029 | 4 | 4 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14816944 | 1175 | 291.6356 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 128 |  | 91227271 | 3965 | 95.16 | 3.965 | 3.6 | 3.6 | 3B +1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14818092 | 1148 | 289.5334 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 91231233 | 3962 | 95.088 | 3.962 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1186 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14819237 | 1145 | 289.7527 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 128 |  | 91235466 | 4233 | 101.592 | 4.233 | 2.8 | 2.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14820421 | 1184 | 270.4937 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 91239388 | 3922 | 94.128 | 3.922 | 2.5 | 2.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14821577 | 1156 | 294.7476 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | DEF |  | 91243291 | 3903 | 93.672 | 3.903 | 2.1 | 2.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14822733 | 1156 | 296.1824 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 91247144 | 3853 | 92.472 | 3.853 | 1.8 | 1.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14823879 | 1146 | 297.4306 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 91251093 | 3949 | 94.776 | 3.949 | 1.5 | 1.5 | 3B+1S | 0 | 1014 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14825038 | 1159 | 293.492 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | DEF |  | 91254797 | 3704 | 88.896 | 3.704 | 1.8 | 1.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14826154 | 1116 | 301.2959 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 91258244 | 3447 | 82.728 | 3.447 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14827235 | 1081 | 313.606 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 98449 | 2362.776 | 98.449 | [13 empty] | 27804 | 282.4203 | [7 empty] | 0 | 0 | 1.0217 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:00 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 11, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. WILLIAM A. PROVIDO OF ENGINEERIMG DEPARTMENT AND TEAM ARRIVE @ 1:50 PM FOR SITE INSPECTION.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 12
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-12 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 28182 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91258244 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14827235 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 3 | 69 | 48.5915 | 75 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | DEF |  | 91261547 | 3303 | 79.272 | 3.303 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14828364 | 1129 | 341.8105 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 4 | 71 | 50 | 78 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 91264902 | 3355 | 80.52 | 3.355 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14829551 | 1187 | 353.8003 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 5 | 73 | 51.4085 | 79 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 91268172 | 3270 | 78.48 | 3.27 | 7.1 | 7.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14830684 | 1133 | 346.4832 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 6 | 65 | 45.7746 | 80 | Automatic - Pressure Setting | 40.8451 | 42.2535 | 46.4789 | 14 | A.ONG | 12.8 | DEF |  | 91271471 | 3299 | 79.176 | 3.299 | 8.4 | 8.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14831776 | 1092 | 331.0094 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 91275238 | 3767 | 90.408 | 3.767 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14832877 | 1101 | 292.275 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 137 |  | 91280561 | 5323 | 127.752 | 5.323 | 9.5 | 9.5 | 3B+1S | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14833991 | 1114 | 209.2805 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 91286215 | 5654 | 135.696 | 5.654 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14835209 | 1218 | 215.4227 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 130 |  | 91291464 | 5249 | 125.976 | 5.249 | 8.5 | 8.5 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14836422 | 1213 | 231.0916 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 91295790 | 4326 | 103.824 | 4.326 | 7.8 | 7.8 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14837636 | 1214 | 280.6288 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 91299305 | 3515 | 84.36 | 3.515 | 7.1 | 7.1 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14838852 | 1216 | 345.9459 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 91303615 | 4310 | 103.44 | 4.31 | 6.5 | 6.5 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14840063 | 1211 | 280.9745 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 91308122 | 4507 | 108.168 | 4.507 | 5.9 | 5.9 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14841305 | 1242 | 275.5713 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 91312230 | 4108 | 98.592 | 4.108 | 5.3 | 5.3 | 3B+1S | 1037 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14842489 | 1184 | 288.2181 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 91316514 | 4284 | 102.816 | 4.284 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 14843670 | 1181 | 275.6769 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 91320606 | 4092 | 98.208 | 4.092 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14844844 | 1174 | 286.9013 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 91324584 | 3978 | 95.472 | 3.978 | 3.9 | 3.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14846028 | 1184 | 297.637 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 91328584 | 4000 | 96 | 4 | 3.5 | 3.5 | 3B+1S | 1057 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14847198 | 1170 | 296 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 126 |  | 91333042 | 4458 | 106.992 | 4.458 | 3 | 3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14848450 | 1252 | 262.4495 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 91337016 | 3974 | 95.376 | 3.974 | 2.7 | 2.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14849578 | 1128 | 283.845 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 91341180 | 4164 | 99.936 | 4.164 | 2.3 | 2.3 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14850762 | 1184 | 284.342 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 130 |  | 91345716 | 4536 | 108.864 | 4.536 | 2 | 2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14851970 | 1208 | 266.3139 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | -4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | DEF |  | 91349730 | 4014 | 96.336 | 4.014 | 1.8 | 1.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14853154 | 1184 | 294.9676 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -4 | 68 | 47.8873 | 65 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 148 |  | 91353258 | 3528 | 84.672 | 3.528 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14854268 | 1114 | 315.7596 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 0 | 68 | 47.8873 | 65 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.5 | 154 |  | 91356530 | 3272 | 78.528 | 3.272 | 4 | 4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14855417 | 1149 | 351.1614 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 98286 | 2358.864 | 98.286 | [13 empty] | 28182 | 286.7346 | [7 empty] | 0 | 0 | 1.0083 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 12, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. RICHARD DE LEON OF A&I ARRIVE @ 4:10 PM FOR RECTIFICATION OF SCADA.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 13
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / ARMAN R. RAYALA II
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-13 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27573 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91356530 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14855417 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 65 | 45.7746 | 60 | Automatic - Pressure Setting | 40.8451 | 42.2535 | 46.4789 | 14 | A.ONG | 11.4 | 153 |  | 91359948 | 3418 | 82.032 | 3.418 | 6 | 6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 14856594 | 1177 | 344.3534 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 6 | 68 | 47.8873 | 65 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | DEF |  | 91363860 | 3912 | 93.888 | 3.912 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14857658 | 1064 | 271.9836 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | DEF |  | 91366760 | 2900 | 69.6 | 2.9 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14858723 | 1065 | 367.2414 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 115 |  | 91371720 | 4960 | 119.04 | 4.96 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14859782 | 1059 | 213.5081 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 123 |  | 91376200 | 4480 | 107.52 | 4.48 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14860815 | 1033 | 230.5804 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 126 |  | 91380789 | 4589 | 110.136 | 4.589 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14861903 | 1088 | 237.0887 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 128 |  | 91385633 | 4844 | 116.256 | 4.844 | 9.2 | 9.2 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14863102 | 1199 | 247.5227 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 91389523 | 3890 | 93.36 | 3.89 | 8.4 | 8.4 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14864327 | 1225 | 314.91 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 127 |  | 91393529 | 4006 | 96.144 | 4.006 | 7.7 | 7.7 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14865534 | 1207 | 301.2981 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 128 |  | 91397266 | 3737 | 89.688 | 3.737 | 7 | 7 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14866733 | 1199 | 320.8456 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 127 |  | 91401020 | 3754 | 90.096 | 3.754 | 6.4 | 6.4 | 3B+1S | 0 | 1037 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14867923 | 1190 | 316.9952 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 91404663 | 3643 | 87.432 | 3.643 | 5.7 | 5.7 | 3B+1S | 0 | 1037 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14869142 | 1219 | 334.6143 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 91408444 | 3781 | 90.744 | 3.781 | 5.1 | 5.1 | 3B+1S | 0 | 1037 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14870310 | 1168 | 308.913 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 91412604 | 4160 | 99.84 | 4.16 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14871516 | 1206 | 289.9038 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 128 |  | 91416103 | 3499 | 83.976 | 3.499 | 4.2 | 4.2 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14872663 | 1147 | 327.8079 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 126 |  | 91419920 | 3817 | 91.608 | 3.817 | 3.7 | 3.7 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14873827 | 1164 | 304.9515 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 126 |  | 91423685 | 3765 | 90.36 | 3.765 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14875009 | 1182 | 309.1633 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 124 |  | 91427270 | 3585 | 86.04 | 3.585 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14876171 | 1162 | 329.7071 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 71 | 50 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.6 | 124 |  | 91429825 | 2555 | 61.32 | 2.555 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14877331 | 1160 | 454.0117 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | DEF | #VALUE! | -3 | 71 | 50 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.6 | DEF |  | 91433219 | 3394 | 81.456 | 3.394 | 2 | 2 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14878486 | 1155 | 340.3064 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -4 | 69 | 48.5915 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 18 | A ONG | 16.1 | DEF |  | 91436825 | 3606 | 86.544 | 3.606 | 1.5 | 1.5 | 3B+1S | 0 | 1015 | 1185 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14879657 | 1171 | 324.7366 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 12.6 | 129 |  | 91440402 | 3577 | 85.848 | 3.577 | 1.4 | 1.4 | 3B | 0 | 0 | 1186 | 0 | 1186 | 1185 | N/A | N/A | N/A | 14880756 | 1099 | 307.2407 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | 133 |  | 91443348 | 2946 | 70.704 | 2.946 | 1.6 | 1.6 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14881800 | 1044 | 354.3788 | 0% | 0% | 100% | 0% | 100% | 100% | 20% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 130 |  | 91447004 | 3656 | 87.744 | 3.656 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14882990 | 1190 | 325.4923 | 0% | 0% | 100% | 0% | 100% | 100% | 20% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 90474 | 2171.376 | 90.474 | [13 empty] | 27573 | 304.7616 | [7 empty] | 0 | 0 | 1.025 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
BP2 -STOPPED OPERATION @ 1:50 AM DUE TO SHIFTING OPERATION TO BP4
BP4 - STARTED @ 1:52 AM
XCV2 - CLOSED @ 2:50 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 13, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:10 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 14
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | FIDEL RAMOS / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-14 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27773 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91447004 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14882990 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 141 |  | 91450262 | 3258 | 78.192 | 3.258 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14884080 | 1090 | 334.5611 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 138 |  | 91453486 | 3224 | 77.376 | 3.224 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14885164 | 1084 | 336.2283 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 138 |  | 91457154 | 3668 | 88.032 | 3.668 | 6.4 | 6.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14886330 | 1166 | 317.8844 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 140 |  | 91460582 | 3428 | 82.272 | 3.428 | 7.9 | 7.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14887472 | 1142 | 333.1389 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 126 |  | 91463864 | 3282 | 78.768 | 3.282 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14888586 | 1114 | 339.4272 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 135 |  | 91467980 | 4116 | 98.784 | 4.116 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14889738 | 1152 | 279.8834 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 130 |  | 91474244 | 6264 | 150.336 | 6.264 | 9 | 9 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14890840 | 1102 | 175.9259 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 131 |  | 91478364 | 4120 | 98.88 | 4.12 | 8.5 | 8.5 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14892077 | 1237 | 300.2427 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 18.4 | 130 |  | 91482324 | 3960 | 95.04 | 3.96 | 7.8 | 7.8 | 3B+1S | 1027 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14893219 | 1142 | 288.3838 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 130 |  | 91485947 | 3623 | 86.952 | 3.623 | 7.2 | 7.2 | 3B+1S | 1027 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14894431 | 1212 | 334.5294 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 128 |  | 91489791 | 3844 | 92.256 | 3.844 | 6.6 | 6.6 | 3B+1S | 1046 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14895694 | 1263 | 328.564 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.3 | DEF |  | 91493368 | 3577 | 85.848 | 3.577 | 5.9 | 5.9 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14896813 | 1119 | 312.832 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 91497261 | 3893 | 93.432 | 3.893 | 5.2 | 5.2 | 3B+1S | 1047 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14898019 | 1206 | 309.7868 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 91501298 | 4037 | 96.888 | 4.037 | 4.6 | 4.6 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14899202 | 1183 | 293.0394 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 127 |  | 91505398 | 4100 | 98.4 | 4.1 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14900355 | 1153 | 281.2195 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 134 |  | 91510027 | 4629 | 111.096 | 4.629 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14901535 | 1180 | 254.9147 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 91514639 | 4612 | 110.688 | 4.612 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14902733 | 1198 | 255.8543 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 91518939 | 4300 | 103.2 | 4.3 | 3 | 3 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14903880 | 1147 | 278.6047 | 100% | 0% | 100% | 0% | 100% | 1100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 132 |  | 91523308 | 4369 | 104.856 | 4.369 | 2.7 | 2.7 | 3B+1S | 1015 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14905071 | 1191 | 272.6024 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 |  | 91528081 | 4773 | 114.552 | 4.773 | 2.5 | 2.5 | 3B+1S | 1015 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14906246 | 1175 | 246.1764 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 131 |  | 91532501 | 4420 | 106.08 | 4.42 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14907393 | 1147 | 259.5023 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | 0 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | DEF |  | 91537405 | 4904 | 117.696 | 4.904 | 2.1 | 2.1 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14908613 | 1220 | 248.7765 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 11.9 | 134 |  | 91541733 | 4328 | 103.872 | 4.328 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14909699 | 1086 | 250.9242 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 138 |  | 91545513 | 3780 | 90.72 | 3.78 | 3 | 3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14910763 | 1064 | 281.4815 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 98509 | 2364.216 | 98.509 | [13 empty] | 27773 | 281.9336 | [7 empty] | 0 | 0 | 1.04 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:44 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:10 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MR CHARLES PORQUEZ AND TEAM OF ITS, A&I INTRUMENTATION ARRIVE @ 10:15 AM TO ASSIST CONTRACTOR WITH THE TROBLE SHOOTING OF DISCHARGE F.M.
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 14, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. ROBERT RAEVIN ROXAS AND EARL FERNAN BOSI OF ITS, A&I INSTRUMENTATION ARRIVE @ 1:30PM TO TROUBLESHOOT BY CHECKING THE PARAMETERS OF THE TRANSMITTER LINE TRACING IN THE SENSOR SIDE.
MAINTENANCE TEAM LEAD BY ERNESTO MONZON ARRIVE @ 3:41 PM TO CONDUCT WARM UP GENSET 1 AND 2 FOR 5 MINS.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 15
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / REY PROVIDENCIA
[15 empty] | 10pm - 6am | REY L. PROVIDENCIA / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-15 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27631 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91545513 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14910763 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 3 | 71 | 50 | 78 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 91549273 | 3760 | 90.24 | 3.76 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14911911 | 1148 | 305.3191 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 79 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 144 |  | 91553170 | 3897 | 93.528 | 3.897 | 6.1 | 6.1 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14913030 | 1119 | 287.144 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 5 | 74 | 52.1127 | 80 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 91557301 | 4131 | 99.144 | 4.131 | 7.7 | 7.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14914166 | 1136 | 274.9939 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 8 | 73 | 51.4085 | 80 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 12.8 | DEF |  | 91561051 | 3750 | 90 | 3.75 | 9.2 | 9.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14915215 | 1049 | 279.7333 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 121 |  | 91564597 | 3546 | 85.104 | 3.546 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 14916332 | 1117 | 315.0028 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 132 |  | 91568466 | 3869 | 92.856 | 3.869 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14917468 | 1136 | 293.6159 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 139 |  | 91573195 | 4729 | 113.496 | 4.729 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14918534 | 1066 | 225.4176 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 91577866 | 4671 | 112.104 | 4.671 | 9.1 | 9.1 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14919706 | 1172 | 250.9099 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 131 |  | 91581984 | 4118 | 98.832 | 4.118 | 8.4 | 8.4 | 3B+1S | 0 | 1027 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14920925 | 1219 | 296.0175 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 91587281 | 5297 | 127.128 | 5.297 | 7.8 | 7.8 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14922104 | 1179 | 222.5788 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 130 |  | 91592213 | 4932 | 118.368 | 4.932 | 7.2 | 7.2 | 3B+1S | 0 | 1027 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14923298 | 1194 | 242.0925 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 91596521 | 4308 | 103.392 | 4.308 | 6.6 | 6.6 | 3B+1S | 0 | 1027 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14924483 | 1185 | 275.0696 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 126 |  | 91600740 | 4219 | 101.256 | 4.219 | 6 | 6 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14925670 | 1187 | 281.3463 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 126 |  | 91605290 | 4550 | 109.2 | 4.55 | 5.4 | 5.4 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14926864 | 1194 | 262.4176 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 127 |  | 91609704 | 4414 | 105.936 | 4.414 | 4.9 | 4.9 | 3B+1S | 0 | 1026 | 1186 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14928023 | 1159 | 262.5736 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 91614250 | 4546 | 109.104 | 4.546 | 4.5 | 4.5 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14929196 | 1173 | 258.029 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 91618860 | 4610 | 110.64 | 4.61 | 3.9 | 3.9 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14930369 | 1173 | 254.4469 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 91623393 | 4533 | 108.792 | 4.533 | 3.4 | 3.4 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14931548 | 1179 | 258.769 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 91628422 | 5029 | 120.696 | 5.029 | 3 | 3 | 3B+1S | 0 | 1025 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14932729 | 1181 | 234.8379 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 128 |  | 91633314 | 4892 | 117.408 | 4.892 | 2.6 | 2.6 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14933896 | 1167 | 238.5527 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.1 | 127 |  | 91638232 | 4918 | 118.032 | 4.918 | 2.3 | 2.3 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14935043 | 1147 | 233.2249 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | 128 |  | 91643189 | 4957 | 118.968 | 4.957 | 2 | 2 | 3B+1S | 0 | 1026 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14936215 | 1172 | 236.4333 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 134 |  | 91648104 | 4915 | 117.96 | 4.915 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14937324 | 1109 | 225.6358 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 145 |  | 91652453 | 4349 | 104.376 | 4.349 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 0 | 1185 | 1185 | N/A | N/A | N/A | 14938394 | 1070 | 246.0336 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 106940 | 2566.56 | 106.94 | [13 empty] | 27631 | 258.3785 | [7 empty] | 0 | 0 | 1.0317 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
BP3 STOP @5:00AM SHIFT OPERATION
BP2 START @ 5:01AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:05 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 15, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:10 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 16
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-16 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27809 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91652453 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14938394 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 2 | 72 | 50.7042 | 78 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 142 |  | 91656671 | 4218 | 101.232 | 4.218 | 4.4 | 4.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14939524 | 1130 | 267.8995 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 78 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 141 |  | 91660887 | 4216 | 101.184 | 4.216 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14940658 | 1134 | 268.9753 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 79 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 |  | 91665032 | 4145 | 99.48 | 4.145 | 7.3 | 7.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14941787 | 1129 | 272.3764 | 0% | 0% | 100% | 100% | 0% | 1000% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 7 | 73 | 51.4085 | 80 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 12.8 | 141 |  | 91669124 | 4092 | 98.208 | 4.092 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14942881 | 1094 | 267.3509 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 |  | 91673097 | 3973 | 95.352 | 3.973 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14943960 | 1079 | 271.5832 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 137 |  | 91677312 | 4215 | 101.16 | 4.215 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14945054 | 1094 | 259.5492 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.06 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 137 |  | 91682698 | 5386 | 129.264 | 5.386 | 8.9 | 8.9 | 3B+1S | 1028 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14946344 | 1290 | 239.5098 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 91687612 | 4914 | 117.936 | 4.914 | 8.4 | 8.4 | 3B+1S | 1027 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14947446 | 1102 | 224.2572 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 129 |  | 91692436 | 4824 | 115.776 | 4.824 | 7.8 | 7.8 | 3B+1S | 1036 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14948646 | 1200 | 248.7562 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 131 |  | 91697214 | 4778 | 114.672 | 4.778 | 7.1 | 7.1 | 3B+1S | 1037 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14949870 | 1224 | 256.1741 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 91701928 | 4714 | 113.136 | 4.714 | 6.8 | 6.8 | 3B+1S | 1036 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14951068 | 1198 | 254.1366 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 91706256 | 4328 | 103.872 | 4.328 | 5.9 | 5.9 | 3B+1S | 1037 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14952222 | 1154 | 266.6359 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 129 |  | 91710488 | 4232 | 101.568 | 4.232 | 5.4 | 5.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14953354 | 1132 | 267.4858 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 130 |  | 91715645 | 5157 | 123.768 | 5.157 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14954639 | 1285 | 249.1759 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 131 |  | 91720305 | 4660 | 111.84 | 4.66 | 4.5 | 4.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14955807 | 1168 | 250.6438 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 91725234 | 4929 | 118.296 | 4.929 | 4.1 | 4.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14956977 | 1170 | 237.3707 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 91730166 | 4932 | 118.368 | 4.932 | 3.6 | 3.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14958166 | 1189 | 237.2263 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 91735018 | 4852 | 116.448 | 4.852 | 3.2 | 3.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14959323 | 1157 | 245.0536 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 91739915 | 4897 | 117.528 | 4.897 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14960502 | 1179 | 240.7596 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 126 |  | 91744494 | 4579 | 109.896 | 4.579 | 2.5 | 2.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14961649 | 1147 | 250.4914 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 125 |  | 91748802 | 4308 | 103.392 | 4.308 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14962799 | 1150 | 266.9452 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 126 |  | 91753751 | 4949 | 118.776 | 4.949 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14963981 | 1182 | 238.8361 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 75 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 139 |  | 91758369 | 4618 | 110.832 | 4.618 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14965069 | 1088 | 235.5998 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 136 |  | 91763134 | 4765 | 114.36 | 4.765 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14966203 | 1134 | 237.9853 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 110681 | 2656.344 | 110.681 | [13 empty] | 27809 | 251.2536 | [7 empty] | 0 | 0 | 1.04 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:23 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 16, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 17
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-17 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27726 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91763134 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14966203 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 2 | 72 | 50.7042 | 76 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | DEF |  | 91767415 | 4281 | 102.744 | 4.281 | 4.4 | 4.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14967305 | 1102 | 257.4165 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 4 | 73 | 51.4085 | 77 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 91771767 | 4352 | 104.448 | 4.352 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14968410 | 1105 | 253.9062 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 6 | 73 | 51.4085 | 79 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 91775888 | 4121 | 98.904 | 4.121 | 7.3 | 7.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14969478 | 1068 | 259.1604 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 8 | 73 | 51.4085 | 80 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 12.8 | DEF |  | 91780197 | 4309 | 103.416 | 4.309 | 8.8 | 8.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14970588 | 1110 | 257.6004 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 91784356 | 4159 | 99.816 | 4.159 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14971698 | 1110 | 266.8911 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 136 |  | 91788785 | 4429 | 106.296 | 4.429 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14972817 | 1119 | 252.653 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 142 |  | 91793950 | 5165 | 123.96 | 5.165 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14973939 | 1122 | 217.2314 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 91799122 | 5172 | 124.128 | 5.172 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14975136 | 1197 | 231.4385 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 124 |  | 91804050 | 4928 | 118.272 | 4.928 | 8.2 | 8.2 | 3B+1S | 0 | 1117 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14976368 | 1232 | 250 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 126 |  | 91808713 | 4663 | 111.912 | 4.663 | 7.3 | 7.3 | 3B+1S | 0 | 1099 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14977596 | 1228 | 263.3498 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.96 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 126 |  | 91813246 | 4533 | 108.792 | 4.533 | 6.5 | 6.5 | 3B+1S | 0 | 1098 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14978827 | 1231 | 271.5641 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 91817610 | 4364 | 104.736 | 4.364 | 5.8 | 5.8 | 3B+1S | 0 | 1045 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14980008 | 1181 | 270.6233 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 127 |  | 91822280 | 4670 | 112.08 | 4.67 | 5.2 | 5.2 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14981244 | 1236 | 264.6681 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 127 |  | 91826712 | 4432 | 106.368 | 4.432 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14982398 | 1154 | 260.3791 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 130 |  | 91831635 | 4923 | 118.152 | 4.923 | 4.2 | 4.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14983589 | 1191 | 241.9257 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 91836508 | 4873 | 116.952 | 4.873 | 3.7 | 3.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14984760 | 1171 | 240.3037 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 127 |  | 91841386 | 4878 | 117.072 | 4.878 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14985921 | 1161 | 240.0574 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 128 |  | 91846045 | 4659 | 111.816 | 4.659 | 3 | 3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14987086 | 1165 | 249.1951 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 127 |  | 91850676 | 4631 | 111.144 | 4.631 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14988250 | 1164 | 251.3496 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 126 |  | 91855152 | 4476 | 107.424 | 4.476 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14989410 | 1160 | 259.16 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 91859763 | 4611 | 110.664 | 4.611 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14990562 | 1152 | 249.8373 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -5 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 132 |  | 91864807 | 5044 | 121.056 | 5.044 | 1.7 | 1.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14991735 | 1173 | 232.5535 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 140 |  | 91869500 | 4693 | 112.632 | 4.693 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14992818 | 1083 | 230.7692 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | 137 |  | 91874070 | 4570 | 109.68 | 4.57 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14993929 | 1111 | 243.1072 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 110936 | 2662.464 | 110.936 | [13 empty] | 27726 | 249.9279 | [7 empty] | 0 | 0 | 1.0033 |  | MLD | 1
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 17, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 18
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | A.RAYALA II /J. LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-18 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27733 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91874070 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 14993929 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.4 | 144 |  | 91878175 | 4105 | 98.52 | 4.105 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14995028 | 1099 | 267.7223 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 143 |  | 91882555 | 4380 | 105.12 | 4.38 | 6.3 | 6.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14996163 | 1135 | 259.1324 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 143 |  | 91886845 | 4290 | 102.96 | 4.29 | 7.8 | 7.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14997320 | 1157 | 269.697 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 143 |  | 91890845 | 4000 | 96 | 4 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14998376 | 1056 | 264 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 |  | 91894675 | 3830 | 91.92 | 3.83 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 0 | 1185 | N/A | N/A | N/A | 14999440 | 1064 | 277.8068 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 129 |  | 91898798 | 4123 | 98.952 | 4.123 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15000527 | 1087 | 263.643 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 9 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 129 |  | 91903839 | 5041 | 120.984 | 5.041 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15001741 | 1214 | 240.8252 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 91909261 | 5422 | 130.128 | 5.422 | 8.2 | 8.2 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15002968 | 1227 | 226.3003 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 128 |  | 91913905 | 4644 | 111.456 | 4.644 | 7.6 | 7.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15004155 | 1187 | 255.5986 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 91918827 | 4922 | 118.128 | 4.922 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15005363 | 1208 | 245.4287 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 91923588 | 4761 | 114.264 | 4.761 | 6.3 | 6.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15006495 | 1132 | 237.7652 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 128 |  | 91928292 | 4704 | 112.896 | 4.704 | 5.7 | 5.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15007784 | 1289 | 274.0221 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 91932683 | 4391 | 105.384 | 4.391 | 5.2 | 5.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15008947 | 1163 | 264.8599 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 91937368 | 4685 | 112.44 | 4.685 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15010082 | 1135 | 242.2625 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 131 |  | 91941854 | 4486 | 107.664 | 4.486 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15011206 | 1124 | 250.5573 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 91946268 | 4414 | 105.936 | 4.414 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15012338 | 1132 | 256.4567 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 91951594 | 5326 | 127.824 | 5.326 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15013586 | 1248 | 212.5422 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 91955998 | 4404 | 105.696 | 4.404 | 3 | 3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15014788 | 1202 | 283.3787 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.16 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 91960976 | 4978 | 119.472 | 4.978 | 2.6 | 2.6 | 3B+1S | 0 | 1016 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15015888 | 1100 | 220.9723 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 91965610 | 4634 | 111.216 | 4.634 | 2.3 | 2.3 | 3B+1S | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15017014 | 1126 | 242.9866 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 91970602 | 4992 | 119.808 | 4.992 | 2 | 2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15018178 | 1164 | 233.1731 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 151 |  | 91975777 | 5175 | 124.2 | 5.175 | 1.8 | 1.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15019381 | 1203 | 232.4638 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 163 |  | 91979690 | 3913 | 93.912 | 3.913 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15020478 | 1097 | 280.3476 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | 163 |  | 91983480 | 3790 | 90.96 | 3.79 | 5 | 5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15021662 | 1184 | 312.4011 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 109410 | 2625.84 | 109.41 | [13 empty] | 27733 | 253.4777 | [7 empty] | 0 | 0 | 1.0583 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:45 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 18, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 19
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | A.RAYALA II /J. LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-19 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26656 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 91983480 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15021662 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | DEF |  | 91986997 | 3517 | 84.408 | 3.517 | 7 | 7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15022830 | 1168 | 332.1012 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | 169 |  | 91990450 | 3453 | 82.872 | 3.453 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15023995 | 1165 | 337.3878 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 11.2 | DEF |  | 91994210 | 3760 | 90.24 | 3.76 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15024870 | 875 | 232.7128 | 0% | 0% | 0% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 91997840 | 3630 | 87.12 | 3.63 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15025678 | 808 | 222.5895 | 0% | 0% | 0% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 92001464 | 3624 | 86.976 | 3.624 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15026498 | 820 | 226.2693 | 0% | 0% | 0% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 143 |  | 92005475 | 4011 | 96.264 | 4.011 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1016 | 1185 | N/A | N/A | N/A | 15027387 | 889 | 221.6405 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 153 |  | 92009617 | 4142 | 99.408 | 4.142 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1127 | 1185 | N/A | N/A | N/A | 15028415 | 1028 | 248.1893 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 17.3 | 140 |  | 92013672 | 4055 | 97.32 | 4.055 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15029569 | 1154 | 284.5869 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 132 |  | 92017624 | 3952 | 94.848 | 3.952 | 9.3 | 9.3 | 3B+1S | 1028 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15030743 | 1174 | 297.0648 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | 136 |  | 92021771 | 4147 | 99.528 | 4.147 | 8.7 | 8.7 | 3B+1S | 1028 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15031966 | 1223 | 294.912 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 125 |  | 92025685 | 3914 | 93.936 | 3.914 | 8.1 | 8.1 | 3B+1S | 1149 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15033159 | 1193 | 304.8033 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 124 |  | 92029860 | 4175 | 100.2 | 4.175 | 7.1 | 7.1 | 3B+1S | 1148 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15034411 | 1252 | 299.8802 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 129 |  | 92033643 | 3783 | 90.792 | 3.783 | 6.4 | 6.4 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15035598 | 1187 | 313.7721 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 17.3 | 129 |  | 92037652 | 4009 | 96.216 | 4.009 | 5.9 | 5.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15036797 | 1199 | 299.0771 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 129 |  | 92041171 | 3519 | 84.456 | 3.519 | 5.6 | 5.6 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15037942 | 1145 | 325.3765 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 128 |  | 92044861 | 3690 | 88.56 | 3.69 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15039117 | 1175 | 318.4282 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 92048443 | 3582 | 85.968 | 3.582 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15040279 | 1162 | 328.029 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 92052109 | 3666 | 87.984 | 3.666 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15041456 | 1177 | 316.9667 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 92055850 | 3741 | 89.784 | 3.741 | 3.9 | 3.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15042650 | 1194 | 319.166 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 92059559 | 3709 | 89.016 | 3.709 | 3.4 | 3.4 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15043792 | 1142 | 307.8997 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 92062975 | 3416 | 81.984 | 3.416 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15044945 | 1153 | 337.5293 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | 0 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A ONG | 12.6 | DEF |  | 92066522 | 3547 | 85.128 | 3.547 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15046111 | 1166 | 328.7285 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 142 |  | 92069616 | 3094 | 74.256 | 3.094 | 3.6 | 3.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15047204 | 1093 | 353.2644 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 138 |  | 92072642 | 3026 | 72.624 | 3.026 | 4.7 | 4.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15048318 | 1114 | 368.1428 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 89162 | 2139.888 | 89.162 | [13 empty] | 26656 | 298.9614 | [7 empty] | 0 | 0 | 1 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
XCV2 - CLOSED @ 1:55 AM WATER ELEVATION (9.5 M)
BP1 STOPPED @ 2:15 AM DUE TO HIGH DISCHARGE PRESSURE.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
BP3 - STARTED @ 5:30 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 8:25 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 17, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 20
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | A.RAYALA II /J. LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-20 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27507 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92072642 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15048318 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 4 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | DEF |  | 92075673 | 3031 | 72.744 | 3.031 | 6.1 | 6.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15049400 | 1082 | 356.9779 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 7 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 92078490 | 2817 | 67.608 | 2.817 | 7.6 | 7.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15050525 | 1125 | 399.361 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 8 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | DEF |  | 92081290 | 2800 | 67.2 | 2.8 | 8.9 | 8.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15051626 | 1101 | 393.2143 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 92084775 | 3485 | 83.64 | 3.485 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1096 | 1185 | N/A | N/A | N/A | 15052655 | 1029 | 295.2654 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 92088260 | 3485 | 83.64 | 3.485 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 15053639 | 984 | 282.3529 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | DEF | #VALUE! | 9 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | DEF |  | 92091787 | 3527 | 84.648 | 3.527 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15054749 | 1110 | 314.7151 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | DEF | #VALUE! | 9 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | DEF |  | 92095551 | 3764 | 90.336 | 3.764 | 9.3 | 9.3 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15055859 | 1110 | 294.899 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | DEF |  | 92099550 | 3999 | 95.976 | 3.999 | 8.7 | 8.7 | 3B+1S | 0 | 1087 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15057112 | 1253 | 313.3283 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | 127 |  | 92103516 | 3966 | 95.184 | 3.966 | 7.9 | 7.9 | 3B+1S | 0 | 1108 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15058330 | 1218 | 307.1104 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 128 |  | 92107615 | 4099 | 98.376 | 4.099 | 7 | 7 | 3B+1S | 0 | 1108 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15059565 | 1235 | 301.293 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.7 | 132 |  | 92111562 | 3947 | 94.728 | 3.947 | 6.1 | 6.1 | 3B+1S | 0 | 1127 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15060805 | 1240 | 314.1627 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 128 |  | 92115430 | 3868 | 92.832 | 3.868 | 5.5 | 5.5 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15062002 | 1197 | 309.4623 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 128 |  | 92119312 | 3882 | 93.168 | 3.882 | 4.9 | 4.9 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15063192 | 1190 | 306.543 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 92123018 | 3706 | 88.944 | 3.706 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15064395 | 1203 | 324.6087 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 130 |  | 92126462 | 3444 | 82.656 | 3.444 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15065516 | 1121 | 325.4936 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 92130199 | 3737 | 89.688 | 3.737 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15066676 | 1160 | 310.4094 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 92133775 | 3576 | 85.824 | 3.576 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15067856 | 1180 | 324.3848 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 92137557 | 3782 | 90.768 | 3.782 | 2.9 | 2.9 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15069048 | 1192 | 312.0042 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 92140959 | 3402 | 81.648 | 3.402 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15070173 | 1125 | 330.6878 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 92144473 | 3514 | 84.336 | 3.514 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15071330 | 1157 | 329.2544 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 92147890 | 3417 | 82.008 | 3.417 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15072484 | 1154 | 337.7231 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 130 |  | 92151293 | 3403 | 81.672 | 3.403 | 1.7 | 1.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15073653 | 1169 | 343.5204 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.74 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 134 |  | 92154405 | 3112 | 74.688 | 3.112 | 2.1 | 2.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15074721 | 1068 | 343.1877 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 92157460 | 3055 | 73.32 | 3.055 | 3 | 3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15075825 | 1104 | 361.3748 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 84818 | 2035.632 | 84.818 | [13 empty] | 27507 | 324.3062 | [7 empty] | 0 | 0 | 0.93667 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:15 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 20, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 21
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | FIDEL RAMOS / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-21 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27589 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92157460 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15075825 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 2 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | DEF |  | 92160632 | 3172 | 76.128 | 3.172 | 4.4 | 4.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15076946 | 1121 | 353.4048 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 141 |  | 92163430 | 2798 | 67.152 | 2.798 | 5.8 | 5.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15078062 | 1116 | 398.8563 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 7 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 92166007 | 2577 | 61.848 | 2.577 | 7.5 | 7.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15079159 | 1097 | 425.6888 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 8 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | DEF |  | 92168695 | 2688 | 64.512 | 2.688 | 9.3 | 9.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15080283 | 1124 | 418.1548 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 92171840 | 3145 | 75.48 | 3.145 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 15081313 | 1030 | 327.504 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 136 |  | 92175174 | 3334 | 80.016 | 3.334 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15082404 | 1091 | 327.2346 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 136 |  | 92179076 | 3902 | 93.648 | 3.902 | 9.4 | 9.4 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15083586 | 1182 | 302.9216 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 132 |  | 92183192 | 4116 | 98.784 | 4.116 | 8.8 | 8.8 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15084804 | 1218 | 295.9184 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 130 |  | 92187264 | 4072 | 97.728 | 4.072 | 8.1 | 8.1 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15085992 | 1188 | 291.7485 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 131 |  | 92191476 | 4212 | 101.088 | 4.212 | 7.4 | 7.4 | 3B+1S | 1048 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15087238 | 1246 | 295.8215 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.16 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 92195338 | 3862 | 92.688 | 3.862 | 6.7 | 6.7 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15088406 | 1168 | 302.434 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 92199036 | 3698 | 88.752 | 3.698 | 6 | 6 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15089586 | 1180 | 319.0914 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 92202924 | 3888 | 93.312 | 3.888 | 5.3 | 5.3 | 3B+1S | 1036 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15090820 | 1234 | 317.3868 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 129 |  | 92206670 | 3746 | 89.904 | 3.746 | 4.8 | 4.8 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15091973 | 1153 | 307.795 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 92210344 | 3674 | 88.176 | 3.674 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15093140 | 1167 | 317.6375 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 92214018 | 3674 | 88.176 | 3.674 | 3.8 | 3.8 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15094304 | 1164 | 316.8209 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 127 |  | 92217790 | 3772 | 90.528 | 3.772 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15095498 | 1194 | 308.5896 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 92221231 | 3441 | 82.584 | 3.441 | 3 | 3 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15096629 | 1131 | 346.9922 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 92224889 | 3658 | 87.792 | 3.658 | 2.7 | 2.7 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15097794 | 1165 | 318.48 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 92228475 | 3586 | 86.064 | 3.586 | 2.4 | 2.4 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15098939 | 1145 | 319.2973 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 126 |  | 92232003 | 3528 | 84.672 | 3.528 | 2.1 | 2.1 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15100091 | 1152 | 326.5306 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 127 |  | 92235092 | 3089 | 74.136 | 3.089 | 1.8 | 1.8 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15101168 | 1077 | 348.6565 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 71 | 50 | 72 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 128 |  | 92239164 | 4072 | 97.728 | 4.072 | 2.5 | 2.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15102324 | 1156 | 283.89 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 72 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 130 |  | 92242686 | 3522 | 84.528 | 3.522 | 3.5 | 3.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15103414 | 1090 | 309.4832 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 85226 | 2045.424 | 85.226 | [13 empty] | 27589 | 323.7158 | [7 empty] | 0 | 0 | 1.045 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:10 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 21, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 22
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
[15 empty] | 10pm - 6am | GEORGE HERNANDEZ / JONEL LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-22 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27530 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92242686 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15103414 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 134 |  | 92245866 | 3180 | 76.32 | 3.18 | 4.5 | 4.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15104546 | 1132 | 355.9748 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 130 |  | 92248994 | 3128 | 75.072 | 3.128 | 5.5 | 5.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15105664 | 1118 | 357.4169 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A.ONG | 11.2 | 130 |  | 92251698 | 2704 | 64.896 | 2.704 | 6.4 | 6.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15106770 | 1106 | 409.0237 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 70 | 49.2958 | 74 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 128 |  | 92254096 | 2398 | 57.552 | 2.398 | 8 | 8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15107822 | 1052 | 438.6989 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 |  | 92257264 | 3168 | 76.032 | 3.168 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15109034 | 1212 | 382.5758 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 78 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 126 |  | 92261000 | 3736 | 89.664 | 3.736 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1126 | 1185 | N/A | N/A | N/A | 15110170 | 1136 | 304.0685 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 141 |  | 92264586 | 3586 | 86.064 | 3.586 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15111192 | 1022 | 284.9972 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 131 |  | 92268940 | 4354 | 104.496 | 4.354 | 8.9 | 8.9 | 3B+1S | 0 | 1056 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15112466 | 1274 | 292.6045 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 131 |  | 92272292 | 3352 | 80.448 | 3.352 | 8.3 | 8.3 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15113506 | 1040 | 310.2625 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 92276104 | 3812 | 91.488 | 3.812 | 7.6 | 7.6 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15114692 | 1186 | 311.1228 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.14 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 128 |  | 92279688 | 3584 | 86.016 | 3.584 | 6.9 | 6.9 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15115848 | 1156 | 322.5446 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 92283888 | 4200 | 100.8 | 4.2 | 6.2 | 6.2 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15117118 | 1270 | 302.381 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 128 |  | 92287446 | 3558 | 85.392 | 3.558 | 5.6 | 5.6 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15118252 | 1134 | 318.7184 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 130 |  | 92291238 | 3792 | 91.008 | 3.792 | 5.1 | 5.1 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15119468 | 1216 | 320.6751 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | 129 |  | 92294753 | 3515 | 84.36 | 3.515 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15120636 | 1168 | 332.2902 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 92298263 | 3510 | 84.24 | 3.51 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15121794 | 1158 | 329.9145 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 92301762 | 3499 | 83.976 | 3.499 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15122952 | 1158 | 330.9517 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 92305471 | 3709 | 89.016 | 3.709 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15124119 | 1167 | 312.2135 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 92309030 | 3559 | 85.416 | 3.559 | 3 | 3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15125277 | 1158 | 325.3723 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 92312475 | 3445 | 82.68 | 3.445 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15126430 | 1153 | 334.688 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 92316027 | 3552 | 85.248 | 3.552 | 2.3 | 2.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15127586 | 1156 | 325.4505 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 128 |  | 92319430 | 3403 | 81.672 | 3.403 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15128741 | 1155 | 339.4064 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 128 |  | 92322692 | 3262 | 78.288 | 3.262 | 2.9 | 2.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15129835 | 1094 | 335.3771 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | DEF | #VALUE! |  | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 92325695 | 3003 | 72.072 | 3.003 | 3.8 | 3.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15130944 | 1109 | 369.2974 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 83009 | 1992.216 | 83.009 | [13 empty] | 27530 | 331.6508 | [7 empty] | 0 | 0 | 1.01 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:36 AM WATER ELEVATION (9.5 M)
VILLAMOR DAILY DATA & HOURLY MONITORING REPORT UPDATE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 22, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.1 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 23
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-23 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27833 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92325695 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15130944 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | DEF |  | 92328462 | 2767 | 66.408 | 2.767 | 5.7 | 5.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15132097 | 1153 | 416.6968 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | DEF |  | 92331246 | 2784 | 66.816 | 2.784 | 7.3 | 7.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15133180 | 1083 | 389.0086 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 145 |  | 92333951 | 2705 | 64.92 | 2.705 | 8.1 | 8.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15134300 | 1120 | 414.0481 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 |  | 92337090 | 3139 | 75.336 | 3.139 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15135391 | 1091 | 347.5629 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 122 |  | 92340568 | 3478 | 83.472 | 3.478 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 1146 | 0 | N/A | N/A | N/A | 15136417 | 1026 | 294.9971 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 138 |  | 92344262 | 3694 | 88.656 | 3.694 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15137458 | 1041 | 281.8083 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 134 |  | 92348650 | 4388 | 105.312 | 4.388 | 9.5 | 9.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15138642 | 1184 | 269.8268 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 92353471 | 4821 | 115.704 | 4.821 | 8.9 | 8.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15139867 | 1225 | 254.0967 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 92358428 | 4957 | 118.968 | 4.957 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15141108 | 1241 | 250.353 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 92362515 | 4087 | 98.088 | 4.087 | 7.5 | 7.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15142306 | 1198 | 293.1245 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 92366504 | 3989 | 95.736 | 3.989 | 6.9 | 6.9 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15143542 | 1236 | 309.8521 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 92370815 | 4311 | 103.464 | 4.311 | 6.2 | 6.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15144737 | 1195 | 277.1979 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 127 |  | 92375050 | 4235 | 101.64 | 4.235 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15145998 | 1261 | 297.7568 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 92379149 | 4099 | 98.376 | 4.099 | 5 | 5 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15147162 | 1164 | 283.9717 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 128 |  | 92383465 | 4316 | 103.584 | 4.316 | 4.4 | 4.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15148332 | 1170 | 271.0843 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 130 |  | 92388343 | 4878 | 117.072 | 4.878 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15149586 | 1254 | 257.0726 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 92392643 | 4300 | 103.2 | 4.3 | 3.5 | 3.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15150700 | 1114 | 291.6279 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 92397223 | 4580 | 109.92 | 4.58 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15151875 | 1175 | 243.2314 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | DEF | #VALUE! | -2 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 92401699 | 4476 | 107.424 | 4.476 | 2.9 | 2.9 | 3B+1S | 1014 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15153039 | 1164 | 260.0536 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | DEF | #VALUE! | -3 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 92406275 | 4576 | 109.824 | 4.576 | 2.5 | 2.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15154221 | 1182 | 258.3042 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 92410996 | 4721 | 113.304 | 4.721 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15155377 | 1156 | 244.8634 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 127 |  | 92415974 | 4978 | 119.472 | 4.978 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15156579 | 1202 | 241.4624 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | DEF | #VALUE! | 6 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | DEF |  | 92420773 | 4799 | 115.176 | 4.799 | 2.1 | 2.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15157722 | 1143 | 238.1746 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | DEF | #VALUE! | 6 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 92425511 | 4738 | 113.712 | 4.738 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15158777 | 1055 | 222.6678 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 99816 | 2395.584 | 99.816 | [13 empty] | 27833 | 278.8431 | [7 empty] | 0 | 0 | 0.97833 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:20 AM WATER ELEVATION (9.5 M)
BP4 - STOPPED @ 3:30 AM DUE TO SHIFTING OPERATION @ BP1
BP1 - STARTED @ 3:32 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:15 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MR.OTHONIEL PETALLO NETWORK ADMINISTRATOR OF INDRA ARRIVE @ 11:28 AM TO INSPECTION NETWORK CABINET.
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 23, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. ERNESTO MONZON AND SOUTH MAINTENANCE TEAM ARRIVE @ 3:48 PM TO CONDUCT REGREASING OF DRIVE COUPLING OF BP4 AND SP2.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 24
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / ARMAN R. RAYALA II
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-24 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27624 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92425511 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15158777 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 6 | 70 | 49.2958 | 73 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 143 |  | 92429887 | 4376 | 105.024 | 4.376 | 3.7 | 3.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15159895 | 1118 | 255.4845 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 7 | 70 | 49.2958 | 74 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 92434115 | 4228 | 101.472 | 4.228 | 5.5 | 5.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15161021 | 1126 | 266.3198 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 7 | 70 | 49.2958 | 75 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 92438374 | 4259 | 102.216 | 4.259 | 6.9 | 6.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15162124 | 1103 | 258.981 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 8 | 68 | 47.8873 | 79 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | DEF |  | 92442802 | 4428 | 106.272 | 4.428 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15163241 | 1117 | 252.2584 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 92446244 | 3442 | 82.608 | 3.442 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15164318 | 1077 | 312.8995 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 76 | 53.5211 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 13.1 | 134 |  | 92450076 | 3832 | 91.968 | 3.832 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 |  | 1187 | 1185 | N/A | N/A | N/A | 15165392 | 1074 | 280.2714 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 130 |  | 92454812 | 4736 | 113.664 | 4.736 | 8.9 | 8.9 | 3B+1S | 0 | 1047 | 1187 |  | 1187 | 1185 | N/A | N/A | N/A | 15166676 | 1284 | 271.1149 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 132 |  | 92459666 | 4854 | 116.496 | 4.854 | 8.2 | 8.2 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15167806 | 1130 | 232.7977 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 129 |  | 92463684 | 4018 | 96.432 | 4.018 | 7.5 | 7.5 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15169014 | 1208 | 300.6471 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 92467278 | 3594 | 86.256 | 3.594 | 6.8 | 6.8 | 3B+1S | 0 | 1046 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15170202 | 1188 | 330.5509 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 92470768 | 3490 | 83.76 | 3.49 | 6.2 | 6.2 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15171412 | 1210 | 346.7049 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 92474294 | 3526 | 84.624 | 3.526 | 5.5 | 5.5 | 3B+1S | 0 | 1037 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15172604 | 1192 | 338.0601 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 92477942 | 3648 | 87.552 | 3.648 | 5 | 5 | 3B+1S | 0 | 1036 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15173796 | 1192 | 326.7544 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 126 |  | 92482533 | 4591 | 110.184 | 4.591 | 4.4 | 4.4 | 3B+1S | 0 | 1037 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15175038 | 1242 | 270.5293 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 92486581 | 4048 | 97.152 | 4.048 | 3.8 | 3.8 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15176160 | 1122 | 277.1739 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 92490931 | 4350 | 104.4 | 4.35 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15177344 | 1184 | 272.1839 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 124 |  | 92495175 | 4244 | 101.856 | 4.244 | 3 | 3 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15178486 | 1142 | 278.9821 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.7 | 125 |  | 92499483 | 4308 | 103.392 | 4.308 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15179636 | 1150 | 265.0882 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 69 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 126 |  | 92504186 | 4703 | 112.872 | 4.703 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15180828 | 1192 | 253.4552 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.6 | 124 |  | 92508627 | 4441 | 106.584 | 4.441 | 1.8 | 1.8 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15181992 | 1164 | 262.1031 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 73 | 51.4085 | 69 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | DEF |  | 92513046 | 4419 | 106.056 | 4.419 | 1.4 | 1.4 | 3B+1S | 0 | 1014 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15183116 | 1124 | 254.3562 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | -2 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 12.6 | DEF |  | 92517461 | 4415 | 105.96 | 4.415 | 1.3 | 1.3 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15184228 | 1112 | 251.8686 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | 131 |  | 92522071 | 4610 | 110.64 | 4.61 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15185303 | 1075 | 233.1887 | 0% | 0% | 100% | 0% | 100% | 100% | 20% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | DEF | #VALUE! | 1 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | DEF |  | 92525866 | 3795 | 91.08 | 3.795 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 0 | 1188 | 1185 | N/A | N/A | N/A | 15186401 | 1098 | 289.3281 | 0% | 0% | 100% | 0% | 100% | 100% | 20% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 100355 | 2408.52 | 100.355 | [13 empty] | 27624 | 275.2628 | [7 empty] | 0 | 0 | 1.0267 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
BP2 - STOPPED @ 5:00 AM DUE TO SHIFTING OPERATION
BP4 - STARTED @ 5:01 AM
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
MR MARVIN CALMONA AND TEAM OF A&I ARRIVE @ 10:18 AM FOR PREVENTIVE AND CHEKING OF ACTUAL SPOT PRESSURE SUCTION AND DISCHARGE
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 24, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 25
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-25 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27764 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92525866 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15186401 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 2 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 138 |  | 92529805 | 3939 | 94.536 | 3.939 | 3.7 | 3.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15187526 | 1125 | 285.6055 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 4 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 139 |  | 92533726 | 3921 | 94.104 | 3.921 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15188624 | 1098 | 280.0306 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 5 | 68 | 47.8873 | 68 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | DEF |  | 92537458 | 3732 | 89.568 | 3.732 | 6.8 | 6.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15189716 | 1092 | 292.6045 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 6 | 68 | 47.8873 | 69 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | 149 |  | 92541232 | 3774 | 90.576 | 3.774 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15190887 | 1171 | 310.2809 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 8 | 79 | 55.6338 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A.ONG | 13.1 | 124 |  | 92544926 | 3694 | 88.656 | 3.694 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15191971 | 1084 | 293.4488 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 126 |  | 92549402 | 4476 | 107.424 | 4.476 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15193119 | 1148 | 256.479 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 128 |  | 92554186 | 4784 | 114.816 | 4.784 | 8.8 | 8.8 | 3B+1S | 1046 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15194296 | 1177 | 246.0284 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 92559686 | 5500 | 132 | 5.5 | 8.1 | 8.1 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15195560 | 1264 | 229.8182 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 128 |  | 92564118 | 4432 | 106.368 | 4.432 | 7.5 | 7.5 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15196668 | 1108 | 250 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 92568304 | 4186 | 100.464 | 4.186 | 6.9 | 6.9 | 3B+1S | 1036 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15197770 | 1102 | 263.2585 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 129 |  | 92572534 | 4230 | 101.52 | 4.23 | 6.2 | 6.2 | 3B+1S | 1027 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 15199020 | 1250 | 295.5083 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 92576228 | 3694 | 88.656 | 3.694 | 5.6 | 5.6 | 3B+1S | 1028 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15200218 | 1198 | 324.3097 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 129 |  | 92580234 | 4006 | 96.144 | 4.006 | 5.1 | 5.1 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15201440 | 1222 | 305.0424 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 92583996 | 3762 | 90.288 | 3.762 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15202611 | 1171 | 311.2706 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 127 |  | 92588338 | 4342 | 104.208 | 4.342 | 4 | 4 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15203838 | 1227 | 282.5887 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 92592731 | 4393 | 105.432 | 4.393 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15204987 | 1149 | 261.5525 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 92597500 | 4769 | 114.456 | 4.769 | 3.1 | 3.1 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15206189 | 1202 | 240.931 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 92601916 | 4416 | 105.984 | 4.416 | 2.7 | 2.7 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15207333 | 1144 | 272.192 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 128 |  | 92606447 | 4531 | 108.744 | 4.531 | 2.3 | 2.3 | 3B+1S | 1021 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15208490 | 1157 | 255.352 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 69 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 92611046 | 4599 | 110.376 | 4.599 | 1.9 | 1.9 | 3B+1S | 1020 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15209655 | 1165 | 253.3159 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 69 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 92615622 | 4576 | 109.824 | 4.576 | 1.6 | 1.6 | 3B+1S | 1020 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15210817 | 1162 | 253.9336 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 132 |  | 92620238 | 4616 | 110.784 | 4.616 | 1.3 | 1.3 | 3B+1S | 1020 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15211956 | 1139 | 246.7504 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.9 | 129 |  | 92624643 | 4405 | 105.72 | 4.405 | 1.5 | 1.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15213039 | 1083 | 245.857 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | DEF | #VALUE! | 3 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | DEF |  | 92628659 | 4016 | 96.384 | 4.016 | 2 | 2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15214165 | 1126 | 280.3785 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 102793 | 2467.032 | 102.793 | [13 empty] | 27764 | 270.0962 | [7 empty] | 0 | 0 | 1.0383 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
VILLAMOR DAILY DATA & HOURLY MONITORING REPORT
SP1 - STARTED @ 5:50 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MR.JOSEPHUS DELA ROSA AND TEAM ARRIVE AT 8:20AM FOR INTERNAL AUDIT TO BUSINESS CONTINUITY PLAN
Additional 3 psi to target discharge pressure from 12:01 PM to 5PM ( APRIL 25, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 26
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE HERNANDEZ / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-26 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27532 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92628659 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15214165 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 4 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 92632352 | 3693 | 88.632 | 3.693 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15215290 | 1125 | 304.6304 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 72 | 50.7042 | 74 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 140 |  | 92635972 | 3620 | 86.88 | 3.62 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15216395 | 1105 | 305.2486 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 7 | 73 | 51.4085 | 76 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 140 |  | 92639418 | 3446 | 82.704 | 3.446 | 7.2 | 7.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15217537 | 1142 | 331.3987 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 9 | 65 | 45.7746 | 78 | Automatic - Pressure Setting | 40.8451 | 42.2535 | 46.4789 | 14 | A.ONG | 12.8 | 135 |  | 92642851 | 3433 | 82.392 | 3.433 | 9.2 | 9.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15218700 | 1163 | 338.7708 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 126 |  | 92646233 | 3382 | 81.168 | 3.382 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 15219717 | 1017 | 300.7096 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 129 |  | 92649721 | 3488 | 83.712 | 3.488 | 9.5 | 9.5 | 3B | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15220796 | 1079 | 309.3463 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.78 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 129 |  | 92653538 | 3817 | 91.608 | 3.817 | 8.8 | 8.8 | 3B+1S | 0 | 1048 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15221980 | 1184 | 310.1912 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 92657692 | 4154 | 99.696 | 4.154 | 8.2 | 8.2 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15223232 | 1252 | 301.3962 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 128 |  | 92661325 | 3633 | 87.192 | 3.633 | 7.5 | 7.5 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15224375 | 1143 | 314.616 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 132 |  | 92665228 | 3903 | 93.672 | 3.903 | 6.9 | 6.9 | 3B+1S | 0 | 1048 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15225575 | 1200 | 307.4558 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 92669388 | 4160 | 99.84 | 4.16 | 6.3 | 6.3 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15226810 | 1235 | 296.875 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 131 |  | 92673070 | 3682 | 88.368 | 3.682 | 5.7 | 5.7 | 3B+1S | 0 | 1046 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15227947 | 1137 | 308.7996 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 92676826 | 3756 | 90.144 | 3.756 | 5.1 | 5.1 | 3B+1S | 0 | 1017 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15229126 | 1179 | 313.8978 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 92680894 | 4068 | 97.632 | 4.068 | 4.7 | 4.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15230400 | 1274 | 313.176 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 92683912 | 3018 | 72.432 | 3.018 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15231400 | 1000 | 331.3453 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 92687626 | 3714 | 89.136 | 3.714 | 3.8 | 3.8 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15232616 | 1216 | 327.4098 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 92691092 | 3466 | 83.184 | 3.466 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15233744 | 1128 | 350.8367 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 92694756 | 3664 | 87.936 | 3.664 | 3 | 3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15234918 | 1174 | 307.8603 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 92698222 | 3466 | 83.184 | 3.466 | 2.7 | 2.7 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15236036 | 1118 | 322.562 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 126 |  | 92702520 | 4298 | 103.152 | 4.298 | 2.2 | 2.2 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15237270 | 1234 | 287.1103 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 92706966 | 4446 | 106.704 | 4.446 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15238434 | 1164 | 261.8084 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 69 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 129 |  | 92710706 | 3740 | 89.76 | 3.74 | 1.7 | 1.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15239560 | 1126 | 301.0695 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 134 |  | 92713798 | 3092 | 74.208 | 3.092 | 1.9 | 1.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15240602 | 1042 | 336.9987 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 3 | 69 | 48.5915 | 71 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A ONG | 11.5 | 145 |  | 92717806 | 4008 | 96.192 | 4.008 | 3.2 | 3.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15241697 | 1095 | 273.2036 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 89147 | 2139.528 | 89.147 | [13 empty] | 27532 | 308.8382 | [7 empty] | 0 | 0 | 0.99 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:10 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
BP1 - STOPPED @ 5:00 AM DUE TO SHIFTING OPERATION
BP2 - STARTED @ 5:01 AM
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( APRIL 26, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 27
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | A.RAYALA II /J. LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-27 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27543 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92717806 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15241697 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 143 |  | 92721537 | 3731 | 89.544 | 3.731 | 4.8 | 4.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15242881 | 1184 | 317.3412 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 142 |  | 92724637 | 3100 | 74.4 | 3.1 | 6.1 | 6.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15243930 | 1049 | 338.3871 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 76 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 140 |  | 92727459 | 2822 | 67.728 | 2.822 | 7.6 | 7.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15245056 | 1126 | 399.0078 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 7 | 71 | 50 | 78 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 141 |  | 92729991 | 2532 | 60.768 | 2.532 | 8.9 | 8.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15246151 | 1095 | 432.4645 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 9 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 124 |  | 92733191 | 3200 | 76.8 | 3.2 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15247220 | 1069 | 334.0625 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 124 |  | 92736694 | 3503 | 84.072 | 3.503 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15248305 | 1085 | 309.7345 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 132 |  | 92740583 | 3889 | 93.336 | 3.889 | 8.9 | 8.9 | 3B+1S | 1017 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15249504 | 1199 | 308.3055 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 127 |  | 92744424 | 3841 | 92.184 | 3.841 | 8.1 | 8.1 | 3B+1S | 1088 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15250714 | 1210 | 315.0221 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 127 |  | 92748259 | 3835 | 92.04 | 3.835 | 7.3 | 7.3 | 3B+1S | 1088 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15251923 | 1209 | 315.2542 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 128 |  | 92752410 | 4151 | 99.624 | 4.151 | 6.5 | 6.5 | 3B+1S | 1087 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15253137 | 1214 | 292.4596 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 128 |  | 92756315 | 3905 | 93.72 | 3.905 | 5.7 | 5.7 | 3B+1S | 1057 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15254251 | 1114 | 285.2753 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 92760040 | 3725 | 89.4 | 3.725 | 5.1 | 5.1 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15255545 | 1294 | 347.3826 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 19 | A ONG | 17.5 | 129 |  | 92763766 | 3726 | 89.424 | 3.726 | 4.5 | 4.5 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15256730 | 1185 | 318.0354 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 92767438 | 3672 | 88.128 | 3.672 | 4 | 4 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15257849 | 1119 | 304.7386 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 92770868 | 3430 | 82.32 | 3.43 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15259000 | 1151 | 335.5685 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 92774503 | 3635 | 87.24 | 3.635 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15260183 | 1183 | 325.447 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 92778017 | 3514 | 84.336 | 3.514 | 2.9 | 2.9 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15261329 | 1146 | 336.6534 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | 0 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 129 |  | 92781824 | 3807 | 91.368 | 3.807 | 2.5 | 2.5 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15262482 | 1153 | 301.0244 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 92785509 | 3685 | 88.44 | 3.685 | 2.1 | 2.1 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15263652 | 1170 | 317.5034 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 92789533 | 4024 | 96.576 | 4.024 | 1.8 | 1.8 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15264815 | 1163 | 289.0159 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 126 |  | 92793425 | 3892 | 93.408 | 3.892 | 1.5 | 1.5 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15265954 | 1139 | 292.6516 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 129 |  | 92797462 | 4037 | 96.888 | 4.037 | 1.3 | 1.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15267158 | 1204 | 298.2413 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 74 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 136 |  | 92801178 | 3716 | 89.184 | 3.716 | 1.9 | 1.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15268264 | 1106 | 297.6319 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 74 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 134 |  | 92804864 | 3686 | 88.464 | 3.686 | 2.6 | 2.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15269240 | 976 | 264.7857 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 87058 | 2089.392 | 87.058 | [13 empty] | 27543 | 316.3753 | [7 empty] | 0 | 0 | 1.0117 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( APRIL 27, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:40 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 28
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | REY PROVIDENCIA / FIDEL RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-28 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27561 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92804864 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15269240 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 133 |  | 92808312 | 3448 | 82.752 | 3.448 | 3.3 | 3.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15270378 | 1138 | 330.0464 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 146 |  | 92811924 | 3612 | 86.688 | 3.612 | 4.9 | 4.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15271472 | 1094 | 302.8793 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 142 |  | 92815524 | 3600 | 86.4 | 3.6 | 6.5 | 6.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15272542 | 1070 | 297.2222 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 4 | 2.8169 | 7 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 138 |  | 92818988 | 3464 | 83.136 | 3.464 | 8.2 | 8.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15273618 | 1076 | 310.6236 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 125 |  | 92821874 | 2886 | 69.264 | 2.886 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15274680 | 1062 | 367.9834 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 75 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 131 |  | 92824195 | 2321 | 55.704 | 2.321 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15275898 | 1218 | 524.7738 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 129 |  | 92827981 | 3786 | 90.864 | 3.786 | 9.1 | 9.1 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15277072 | 1174 | 310.0898 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 92831778 | 3797 | 91.128 | 3.797 | 8.5 | 8.5 | 3B+1S | 0 | 1027 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15278233 | 1161 | 305.7677 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 130 |  | 92835575 | 3797 | 91.128 | 3.797 | 7.8 | 7.8 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15279415 | 1182 | 311.2984 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 92839692 | 4117 | 98.808 | 4.117 | 7.2 | 7.2 | 3B+1S | 0 | 1056 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15280619 | 1204 | 292.446 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 126 |  | 92843479 | 3787 | 90.888 | 3.787 | 6.4 | 6.4 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15281818 | 1199 | 316.6095 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 125 |  | 92847149 | 3670 | 88.08 | 3.67 | 5.7 | 5.7 | 3B+1S | 0 | 1057 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15282987 | 1169 | 318.5286 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 126 |  | 92851026 | 3877 | 93.048 | 3.877 | 5.1 | 5.1 | 3B+1S | 0 | 1057 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15284170 | 1183 | 305.1328 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 92854733 | 3707 | 88.968 | 3.707 | 4.4 | 4.4 | 3B+1S | 0 | 1016 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15285377 | 1207 | 325.6002 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | 129 |  | 92858454 | 3721 | 89.304 | 3.721 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15286531 | 1154 | 310.1317 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 92861964 | 3510 | 84.24 | 3.51 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15287711 | 1180 | 336.1823 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 128 |  | 92865585 | 3621 | 86.904 | 3.621 | 3 | 3 | 3B+1S | 0 | 1016 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15288861 | 1150 | 325.8768 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 92869325 | 3740 | 89.76 | 3.74 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15290020 | 1159 | 307.4866 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 92872908 | 3583 | 85.992 | 3.583 | 2.3 | 2.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15291156 | 1136 | 317.0527 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 92876639 | 3731 | 89.544 | 3.731 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15292334 | 1178 | 315.733 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 92880142 | 3503 | 84.072 | 3.503 | 1.6 | 1.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15293470 | 1136 | 324.2935 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 4 | 2.8169 | -4 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 126 |  | 92883684 | 3542 | 85.008 | 3.542 | 1.4 | 1.4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15294621 | 1151 | 324.9577 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | 0.5 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 132 |  | 92887601 | 3917 | 94.008 | 3.917 | 1.8 | 1.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15295710 | 1089 | 278.0189 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 0.5 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 134 |  | 92891345 | 3744 | 89.856 | 3.744 | 2.7 | 2.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15296801 | 1091 | 291.3996 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 86481 | 2075.544 | 86.481 | [13 empty] | 27561 | 318.6943 | [7 empty] | 0 | 0 | 1.0083 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:36 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:16 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( APRIL 28, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
ENGR. MARK JOSEPH PASCUAL AND SOUTH MAINTENANCE TEAM ARRIVE @11:47 PM TO CONDUCT GENSET 1&2 WARM-UP WITHOUT LOAD FOR 5MINS.

## APR 29
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-29 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27553 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92891345 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15296801 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | -4 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 135 |  | 92894530 | 3185 | 76.44 | 3.185 | 3.1 | 3.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15297884 | 1083 | 340.0314 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | -2 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 129 |  | 92897661 | 3131 | 75.144 | 3.131 | 4.9 | 4.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15298999 | 1115 | 356.1163 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 132 |  | 92900779 | 3118 | 74.832 | 3.118 | 6.1 | 6.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15300106 | 1107 | 355.0353 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 136 |  | 92903883 | 3104 | 74.496 | 3.104 | 7.3 | 7.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15301205 | 1099 | 354.0593 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 7 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 128 |  | 92906866 | 2983 | 71.592 | 2.983 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15302322 | 1117 | 374.4552 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 134 |  | 92910250 | 3384 | 81.216 | 3.384 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15303424 | 1102 | 325.6501 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 130 |  | 92914001 | 3751 | 90.024 | 3.751 | 9.4 | 9.4 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15304543 | 1119 | 298.3204 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 131 |  | 92917850 | 3849 | 92.376 | 3.849 | 8.8 | 8.8 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15305716 | 1173 | 304.7545 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 129 |  | 92921847 | 3997 | 95.928 | 3.997 | 8.2 | 8.2 | 3B+1S | 1048 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15306913 | 1197 | 299.4746 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 92926090 | 4243 | 101.832 | 4.243 | 7.5 | 7.5 | 3B+1S | 1048 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15308132 | 1219 | 287.2967 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 129 |  | 92929805 | 3715 | 89.16 | 3.715 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15309285 | 1153 | 310.3634 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 92933605 | 3800 | 91.2 | 3.8 | 6.2 | 6.2 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15310505 | 1220 | 321.0526 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 92937444 | 3839 | 92.136 | 3.839 | 5.5 | 5.5 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15311704 | 1199 | 312.3209 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 92941183 | 3739 | 89.736 | 3.739 | 4.9 | 4.9 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15312872 | 1168 | 312.383 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 130 |  | 92944776 | 3593 | 86.232 | 3.593 | 4.5 | 4.5 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15314044 | 1172 | 326.1898 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 92948334 | 3558 | 85.392 | 3.558 | 3.9 | 3.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15315192 | 1148 | 322.6532 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 92951890 | 3556 | 85.344 | 3.556 | 3.5 | 3.5 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15316362 | 1170 | 322.8346 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 92955535 | 3645 | 87.48 | 3.645 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15317535 | 1173 | 320.9877 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 131 |  | 92959094 | 3559 | 85.416 | 3.559 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15318868 | 1333 | 374.5434 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 92962618 | 3524 | 84.576 | 3.524 | 2.5 | 2.5 | 3B+1S | 1016 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15319843 | 975 | 276.6742 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 92966102 | 3484 | 83.616 | 3.484 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15320971 | 1128 | 323.7658 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 92969919 | 3817 | 91.608 | 3.817 | 1.8 | 1.8 | 3B+1S | 1014 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15322190 | 1219 | 319.3608 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 133 |  | 92973568 | 3649 | 87.576 | 3.649 | 2.2 | 2.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15323259 | 1069 | 292.957 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 3 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 135 |  | 92976602 | 3034 | 72.816 | 3.034 | 2.9 | 2.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15324354 | 1095 | 360.9097 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 85257 | 2046.168 | 85.257 | [13 empty] | 27553 | 323.1758 | [7 empty] | 0 | 0 | 1.0117 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:58 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:36 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( APRIL 29, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:40 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## APR 30
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[15 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-04-30 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27452 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 92976602 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15324354 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 74 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 143 |  | 92980659 | 4057 | 97.368 | 4.057 | 4.7 | 4.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15325449 | 1095 | 269.9039 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 6 | 70 | 49.2958 | 76 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 142 |  | 92983851 | 3192 | 76.608 | 3.192 | 5.7 | 5.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15326452 | 1003 | 314.2231 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 7 | 72 | 50.7042 | 77 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 142 |  | 92986800 | 2949 | 70.776 | 2.949 | 7.1 | 7.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15327562 | 1110 | 376.3988 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 8 | 72 | 50.7042 | 79 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | 142 |  | 92989768 | 2968 | 71.232 | 2.968 | 8.5 | 8.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15328745 | 1183 | 398.5849 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 126 |  | 92992690 | 2922 | 70.128 | 2.922 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15329810 | 1065 | 364.4764 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 126 |  | 92996295 | 3605 | 86.52 | 3.605 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15330972 | 1162 | 322.3301 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 130 |  | 92999823 | 3528 | 84.672 | 3.528 | 8.9 | 8.9 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15332071 | 1099 | 311.5079 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 93003715 | 3892 | 93.408 | 3.892 | 8.3 | 8.3 | 3B+1S | 0 | 1027 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15333267 | 1196 | 307.297 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 127 |  | 93007483 | 3768 | 90.432 | 3.768 | 7.7 | 7.7 | 3B+1S | 0 | 1048 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15334470 | 1203 | 319.2675 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 93011238 | 3755 | 90.12 | 3.755 | 7 | 7 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15335636 | 1166 | 310.5193 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 130 |  | 93015093 | 3855 | 92.52 | 3.855 | 6.4 | 6.4 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15336820 | 1184 | 307.1336 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 134 |  | 93018744 | 3651 | 87.624 | 3.651 | 5.9 | 5.9 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15337958 | 1138 | 311.6954 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 93022506 | 3762 | 90.288 | 3.762 | 5.3 | 5.3 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15339171 | 1213 | 322.4349 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 93026070 | 3564 | 85.536 | 3.564 | 4.8 | 4.8 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15340298 | 1127 | 316.2177 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 130 |  | 93029716 | 3646 | 87.504 | 3.646 | 4.4 | 4.4 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15341484 | 1186 | 325.288 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 2 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 126 |  | 93033682 | 3966 | 95.184 | 3.966 | 3.8 | 3.8 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15342756 | 1272 | 320.7262 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 93036834 | 3152 | 75.648 | 3.152 | 3.4 | 3.4 | 3B+1S | 0 | 1026 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15343798 | 1042 | 403.5533 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 93040284 | 3450 | 82.8 | 3.45 | 3 | 3 | 3B+1S | 0 | 1025 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15344914 | 1116 | 302.029 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 93044068 | 3784 | 90.816 | 3.784 | 2.6 | 2.6 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15346118 | 1204 | 318.1818 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 93047568 | 3500 | 84 | 3.5 | 2.2 | 2.2 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15347266 | 1148 | 328 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 93051080 | 3512 | 84.288 | 3.512 | 1.9 | 1.9 | 3B+1S | 0 | 1024 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15348416 | 1150 | 327.4487 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | 0 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 129 |  | 93054689 | 3609 | 86.616 | 3.609 | 1.6 | 1.6 | 3B+1S | 0 | 1023 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15349638 | 1222 | 338.5979 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | DEF | #VALUE! | 2 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.9 | DEF |  | 93057798 | 3109 | 74.616 | 3.109 | 1.8 | 1.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15350654 | 1016 | 326.7932 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | 142 |  | 93060983 | 3185 | 76.44 | 3.185 | 2.7 | 2.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15351806 | 1152 | 361.6954 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 84381 | 2025.144 | 84.381 | [13 empty] | 27452 | 325.3339 | [7 empty] | 0 | 0 | 1.0333 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:30 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( APRIL 30, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)