## MAY 1
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[15 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-01 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27846 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93060983 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15351806 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.4 | 135 |  | 93064415 | 3432 | 82.368 | 3.432 | 3.9 | 3.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15353000 | 1194 | 347.9021 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 135 |  | 93067051 | 2636 | 63.264 | 2.636 | 6.5 | 6.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15354102 | 1102 | 418.0577 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 7 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 139 |  | 93069812 | 2761 | 66.264 | 2.761 | 7 | 7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15355112 | 1010 | 365.8095 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 8 | 74 | 52.1127 | 79 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 12.8 | 141 |  | 93072570 | 2758 | 66.192 | 2.758 | 8.5 | 8.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15356207 | 1095 | 397.0268 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 125 |  | 93075465 | 2895 | 69.48 | 2.895 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15357285 | 1078 | 372.3661 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 |  | 93079693 | 4228 | 101.472 | 4.228 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15358426 | 1141 | 269.8675 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 130 |  | 93083894 | 4201 | 100.824 | 4.201 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15359551 | 1125 | 267.7934 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 131 |  | 93088279 | 4385 | 105.24 | 4.385 | 9 | 9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15360753 | 1202 | 274.1163 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 128 |  | 93092646 | 4367 | 104.808 | 4.367 | 8.3 | 8.3 | 3B+1S | 1048 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15361970 | 1217 | 278.681 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 93097015 | 4369 | 104.856 | 4.369 | 7.5 | 7.5 | 3B+1S | 1088 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15363251 | 1281 | 293.2021 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.49 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 133 |  | 93101025 | 4010 | 96.24 | 4.01 | 6.8 | 6.8 | 3B+1S | 1031 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15364457 | 1206 | 300.7481 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 129 |  | 93105006 | 3981 | 95.544 | 3.981 | 6.2 | 6.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15365652 | 1195 | 300.1758 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 129 |  | 93108915 | 3909 | 93.816 | 3.909 | 5.7 | 5.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15366815 | 1163 | 297.5185 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 93113229 | 4314 | 103.536 | 4.314 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15367992 | 1177 | 272.8326 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 93117368 | 4139 | 99.336 | 4.139 | 4.8 | 4.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15369152 | 1160 | 280.2609 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 93121898 | 4530 | 108.72 | 4.53 | 4.4 | 4.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15370331 | 1179 | 260.2649 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 93126437 | 4539 | 108.936 | 4.539 | 4 | 4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15371526 | 1195 | 259.7488 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 93131047 | 4610 | 110.64 | 4.61 | 3.6 | 3.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15372695 | 1169 | 259.2191 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 131 |  | 93135633 | 4586 | 110.064 | 4.586 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15373873 | 1178 | 256.8687 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 93140102 | 4469 | 107.256 | 4.469 | 2.8 | 2.8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15375052 | 1179 | 263.8174 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 129 |  | 93144912 | 4810 | 115.44 | 4.81 | 2.5 | 2.5 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15376224 | 1172 | 243.659 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | -1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 93150073 | 5161 | 123.864 | 5.161 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15377414 | 1190 | 230.5755 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | -2 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 140 |  | 93154405 | 4332 | 103.968 | 4.332 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15378522 | 1108 | 255.771 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | -1 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 136 |  | 93158979 | 4574 | 109.776 | 4.574 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15379652 | 1130 | 247.0485 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 97996 | 2351.904 | 97.996 | [13 empty] | 27846 | 284.1545 | [7 empty] | 0 | 0 | 0.92333 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:40 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
BP4 STOP @ 5:00AM DUE TO SHIFTING OPERATION
BP1 START @ 5:01AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAINTENANCE TEAM LEAD BY NOEL NERPIO ARRIVE @ 7:54AM FOR MONTHLY PREVENTIVE MAINTENANCE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 1, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:40 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)
MR. GERRARDO BUNDA OF SOUTH MAINTENANCE AND TEAM ARRIVE @ 10:42 PM TO CONDUCT MONTHLY PREVENTIVE MAINTENANCE INSPECTION OF SP1,SP2 AND BP4.

## MAY 2
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
WATER NETWORK | [14 empty] | 2pm - 10pm | A.RAYALA II /J. LLAGUNO
[15 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-02 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27923 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93158979 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15379652 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 2 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 142 |  | 93163044 | 4065 | 97.56 | 4.065 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15380872 | 1220 | 300.123 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 139 |  | 93167042 | 3998 | 95.952 | 3.998 | 7.3 | 7.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15381986 | 1114 | 278.6393 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 141 |  | 93170896 | 3854 | 92.496 | 3.854 | 8.4 | 8.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15383090 | 1104 | 286.4556 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 128 |  | 93174643 | 3747 | 89.928 | 3.747 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15384144 | 1054 | 281.2917 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 126 |  | 93178021 | 3378 | 81.072 | 3.378 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15385217 | 1073 | 317.6436 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 140 |  | 93182114 | 4093 | 98.232 | 4.093 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15386322 | 1105 | 269.9731 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 128 |  | 93186506 | 4392 | 105.408 | 4.392 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15387526 | 1204 | 274.1348 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 131 |  | 93191184 | 4678 | 112.272 | 4.678 | 8.6 | 8.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15388708 | 1182 | 252.6721 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 130 |  | 93195684 | 4500 | 108 | 4.5 | 8 | 8 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15389876 | 1168 | 259.5556 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 93199456 | 3772 | 90.528 | 3.772 | 7.3 | 7.3 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15391070 | 1194 | 316.5429 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.39 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 93203076 | 3620 | 86.88 | 3.62 | 6.8 | 6.8 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15392300 | 1230 | 339.779 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 93207142 | 4066 | 97.584 | 4.066 | 6.1 | 6.1 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15393580 | 1280 | 314.8057 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 93211058 | 3916 | 93.984 | 3.916 | 5.6 | 5.6 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15394714 | 1134 | 289.5812 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 93215591 | 4533 | 108.792 | 4.533 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15395951 | 1237 | 272.8877 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 128 |  | 93220043 | 4452 | 106.848 | 4.452 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15397153 | 1202 | 269.991 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 93224422 | 4379 | 105.096 | 4.379 | 4.1 | 4.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15398315 | 1162 | 265.3574 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 93228951 | 4529 | 108.696 | 4.529 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15399421 | 1106 | 256.5688 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 93233376 | 4425 | 106.2 | 4.425 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15400674 | 1253 | 249.9435 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 69 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 93237812 | 4436 | 106.464 | 4.436 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15401854 | 1180 | 266.0054 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 69 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 93242225 | 4413 | 105.912 | 4.413 | 2.5 | 2.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15403022 | 1168 | 264.6726 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 93246457 | 4232 | 101.568 | 4.232 | 2.1 | 2.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15404204 | 1182 | 279.3006 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 128 |  | 93250836 | 4379 | 105.096 | 4.379 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15405333 | 1129 | 257.8214 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.06 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 131 |  | 93255054 | 4218 | 101.232 | 4.218 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15406461 | 1128 | 267.4253 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 2 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 137 |  | 93259452 | 4398 | 105.552 | 4.398 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15407575 | 1114 | 253.297 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 100473 | 2411.352 | 100.473 | [13 empty] | 27923 | 277.9155 | [7 empty] | 0 | 0 | 1.0867 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:31 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 2, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:40 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## MAY 3
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[15 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-03 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27937 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93259452 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15407575 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 3 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 |  |  | 93263763 | 4311 | 103.464 | 4.311 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15408784 | 1209 | 280.4454 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 4 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 |  |  | 93267986 | 4223 | 101.352 | 4.223 | 6.1 | 6.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15409897 | 1113 | 263.5567 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 6 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 |  |  | 93272129 | 4143 | 99.432 | 4.143 | 7.6 | 7.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15410998 | 1101 | 265.7495 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | DEF | #VALUE! | 7 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 |  |  | 93276270 | 4141 | 99.384 | 4.141 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15412086 | 1088 | 262.7385 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 |  |  | 93280495 | 4225 | 101.4 | 4.225 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15413171 | 1085 | 256.8047 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 128 |  | 93284496 | 4001 | 96.024 | 4.001 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15414258 | 1087 | 271.6821 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.01 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 133 |  | 93288930 | 4434 | 106.416 | 4.434 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15415456 | 1198 | 270.1849 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 131 |  | 93293826 | 4896 | 117.504 | 4.896 | 8.4 | 8.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15416668 | 1212 | 247.549 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 129 |  | 93298034 | 4208 | 100.992 | 4.208 | 7.8 | 7.8 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15417886 | 1218 | 289.4487 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 93302148 | 4114 | 98.736 | 4.114 | 7.2 | 7.2 | 3B+1S | 1027 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15419070 | 1184 | 287.7978 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.08 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 93306248 | 4100 | 98.4 | 4.1 | 6.6 | 6.6 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15420268 | 1198 | 292.1951 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 93310527 | 4279 | 102.696 | 4.279 | 6.1 | 6.1 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15421490 | 1222 | 285.5807 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 93314424 | 3897 | 93.528 | 3.897 | 5.5 | 5.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15422664 | 1174 | 301.2574 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 93318543 | 4119 | 98.856 | 4.119 | 5 | 5 | 3B+1S | 1025 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15423859 | 1195 | 290.119 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 93322667 | 4124 | 98.976 | 4.124 | 4.6 | 4.6 | 3B+1S | 1025 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15425049 | 1190 | 288.5548 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 93326950 | 4283 | 102.792 | 4.283 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15426217 | 1168 | 272.706 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | 2 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 127 |  | 93331244 | 4294 | 103.056 | 4.294 | 3.7 | 3.7 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15427410 | 1193 | 272.0075 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 93335659 | 4415 | 105.96 | 4.415 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15428569 | 1159 | 270.2152 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 93340378 | 4719 | 113.256 | 4.719 | 2.9 | 2.9 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15429751 | 1182 | 250.4768 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 93344831 | 4453 | 106.872 | 4.453 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15430922 | 1171 | 262.9688 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 128 |  | 93349185 | 4354 | 104.496 | 4.354 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15432090 | 1168 | 268.2591 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | -3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 125 |  | 93353739 | 4554 | 109.296 | 4.554 | 2 | 2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15433272 | 1182 | 259.552 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.11 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | -3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 132 |  | 93357942 | 4203 | 100.872 | 4.203 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15434420 | 1148 | 273.1382 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | -1 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 136 |  | 93362097 | 4155 | 99.72 | 4.155 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15435512 | 1092 | 262.8159 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 102645 | 2463.48 | 102.645 | [13 empty] | 27937 | 272.1711 | [7 empty] | 0 | 0 | 1.025 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:03 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 3, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:40 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## MAY 4
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[15 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-04 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27823 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93362097 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15435512 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 2 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 131 |  | 93366463 | 4366 | 104.784 | 4.366 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15436703 | 1191 | 272.7897 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 134 |  | 93370729 | 4266 | 102.384 | 4.266 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15437804 | 1101 | 258.0872 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 6 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 135 |  | 93374895 | 4166 | 99.984 | 4.166 | 7 | 7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15438882 | 1078 | 258.7614 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 7 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 138 |  | 93379162 | 4267 | 102.408 | 4.267 | 8.2 | 8.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15439985 | 1103 | 258.4954 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 128 |  | 93383398 | 4236 | 101.664 | 4.236 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15441096 | 1111 | 262.2757 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 136 |  | 93387948 | 4550 | 109.2 | 4.55 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15442286 | 1190 | 261.5385 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 131 |  | 93392262 | 4314 | 103.536 | 4.314 | 9 | 9 | 3B+1S | 0 | 1026 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15443462 | 1176 | 272.6008 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 130 |  | 93396594 | 4332 | 103.968 | 4.332 | 8.4 | 8.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15444598 | 1136 | 262.2345 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 128 |  | 93400976 | 4382 | 105.168 | 4.382 | 7.7 | 7.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15445834 | 1236 | 282.063 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 93404928 | 3952 | 94.848 | 3.952 | 7 | 7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15447027 | 1193 | 301.8725 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.12 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 93408936 | 4008 | 96.192 | 4.008 | 6.4 | 6.4 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15448244 | 1217 | 303.6427 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 131 |  | 93412678 | 3742 | 89.808 | 3.742 | 5.9 | 5.9 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15449396 | 1152 | 307.8568 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 93416928 | 4250 | 102 | 4.25 | 5.3 | 5.3 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15450602 | 1206 | 283.7647 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 125 |  | 93421208 | 4280 | 102.72 | 4.28 | 4.8 | 4.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15451758 | 1156 | 270.0935 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 128 |  | 93421208 | 0 | 0 | 0 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15452875 | 1117 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 128 |  | 93421208 | 0 | 0 | 0 | 4 | 4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15454054 | 1179 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 127 |  | 93421208 | 0 | 0 | 0 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15455236 | 1182 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 127 |  | 93421208 | 0 | 0 | 0 | 3.2 | 3.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15456391 | 1155 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 93421208 | 0 | 0 | 0 | 2.8 | 2.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 15457585 | 1194 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 93421208 | 0 | 0 | 0 | 2.5 | 2.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15458742 | 1157 | #DIV/0! | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 93452074 | 30866 | 740.784 | 30.866 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15459916 | 1174 | 38.0354 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 129 |  | 93456717 | 4643 | 111.432 | 4.643 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15461104 | 1188 | 255.8691 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | 131 |  | 93460901 | 4184 | 100.416 | 4.184 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15462198 | 1094 | 261.4723 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 2 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 137 |  | 93465104 | 4203 | 100.872 | 4.203 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15463335 | 1137 | 270.5211 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 103007 | 2472.168 | 103.007 | [13 empty] | 27823 | 270.1079 | [7 empty] | 0 | 0 | 1.0617 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:44 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 4, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
PI @ 1:51 PM ALL PUMP STOPPED
BP2- STARTED 1:53 PM
BP1- STARTED 1:55 PM
BP3- STARTED 1:57 PM
SP2- STARTED 1:59 PM
RNOM @ 2:00 PM
FLOWMETER FAULT DUE TO POWER INTERUPTION
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 5
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / FIDEL A. RAMOS
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[15 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-05 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27891 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93465104 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15463335 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | DEF | #VALUE! | 3 | 70 | 49.2958 | 77 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 93468994 | 3890 | 93.36 | 3.89 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15464455 | 1120 | 287.9177 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | DEF | #VALUE! | 5 | 71 | 50 | 78 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 93472999 | 4005 | 96.12 | 4.005 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15465555 | 1100 | 274.6567 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | DEF | #VALUE! | 7 | 73 | 51.4085 | 78 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 93477008 | 4009 | 96.216 | 4.009 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15466673 | 1118 | 278.8725 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 8 | 72 | 50.7042 | 79 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | 142 |  | 93481218 | 4210 | 101.04 | 4.21 | 8 | 8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15467802 | 1129 | 268.171 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 |  | 93485013 | 3795 | 91.08 | 3.795 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15468897 | 1095 | 288.5375 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 9 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | 136 |  | 93489000 | 3987 | 95.688 | 3.987 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15470062 | 1165 | 292.1996 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 8 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 131 |  | 93493074 | 4074 | 97.776 | 4.074 | 9.2 | 9.2 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15471196 | 1134 | 278.3505 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 129 |  | 93497652 | 4578 | 109.872 | 4.578 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15472394 | 1198 | 261.6863 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 129 |  | 93502488 | 4836 | 116.064 | 4.836 | 7.8 | 7.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15473650 | 1256 | 259.7188 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 93506956 | 4468 | 107.232 | 4.468 | 7.2 | 7.2 | 3B+1S | 1039 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15474842 | 1192 | 266.786 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.12 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 128 |  | 93511636 | 4680 | 112.32 | 4.68 | 6.6 | 6.6 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15476048 | 1206 | 257.6923 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 132 |  | 93516118 | 4482 | 107.568 | 4.482 | 6 | 6 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15477238 | 1190 | 265.5065 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 93520880 | 4762 | 114.288 | 4.762 | 5.3 | 5.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15478454 | 1216 | 255.3549 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 93524916 | 4036 | 96.864 | 4.036 | 4.8 | 4.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15479649 | 1195 | 296.0852 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 130 |  | 93529337 | 4421 | 106.104 | 4.421 | 4.4 | 4.4 | 3B+1S | 1014 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15480812 | 1163 | 263.0627 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 93533672 | 4335 | 104.04 | 4.335 | 3.9 | 3.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15481982 | 1170 | 269.8962 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 93537906 | 4234 | 101.616 | 4.234 | 3.5 | 3.5 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15483162 | 1180 | 276.3344 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 128 |  | 93542399 | 4493 | 107.832 | 4.493 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15484333 | 1171 | 262.6308 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 93546893 | 4494 | 107.856 | 4.494 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 1186 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15485509 | 1176 | 261.6822 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 93551441 | 4548 | 109.152 | 4.548 | 2.4 | 2.4 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15486673 | 1164 | 255.9367 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 93556043 | 4602 | 110.448 | 4.602 | 2.1 | 2.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15487844 | 1171 | 254.4546 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | 0 | 77 | 54.2254 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 93560914 | 4871 | 116.904 | 4.871 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15489042 | 1198 | 245.9454 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | 1 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 142 |  | 93564982 | 4068 | 97.632 | 4.068 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15490116 | 1074 | 264.0118 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 1 | 71 | 50 | 71 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | 134 |  | 93568988 | 4006 | 96.144 | 4.006 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15491226 | 1110 | 277.0844 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 103884 | 2493.216 | 103.884 | [13 empty] | 27891 | 268.4822 | [7 empty] | 0 | 0 | 1.0217 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:44 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 5, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 6
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / GEORGE O. HERNANDEZ
[15 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-06 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27890 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93568988 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15491226 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 76 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 140 |  | 93573588 | 4600 | 110.4 | 4.6 | 5.1 | 5.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15492366 | 1140 | 247.8261 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 6 | 71 | 50 | 78 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 140 |  | 93577658 | 4070 | 97.68 | 4.07 | 6.2 | 6.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15493478 | 1112 | 273.2187 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 8 | 74 | 52.1127 | 78 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 137 |  | 93581832 | 4174 | 100.176 | 4.174 | 7.3 | 7.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15494596 | 1118 | 267.8486 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 8 | 74 | 52.1127 | 78 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 12.8 | 134 |  | 93585736 | 3904 | 93.696 | 3.904 | 8.4 | 8.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15495670 | 1074 | 275.1025 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 9 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 124 |  | 93589620 | 3884 | 93.216 | 3.884 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15496730 | 1060 | 272.9145 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 9 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | 128 |  | 93593432 | 3812 | 91.488 | 3.812 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15497880 | 1150 | 301.6789 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 9 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | 141 |  | 93597318 | 3886 | 93.264 | 3.886 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15498948 | 1068 | 274.8327 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 8 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 131 |  | 93601792 | 4474 | 107.376 | 4.474 | 9 | 9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15500186 | 1238 | 276.7099 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 8 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 130 |  | 93606320 | 4528 | 108.672 | 4.528 | 8.4 | 8.4 | 3B+1S | 0 | 1028 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15501376 | 1190 | 262.8092 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | A.RAYALA II /J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 131 |  | 93610612 | 4292 | 103.008 | 4.292 | 7.9 | 7.9 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15502566 | 1190 | 277.26 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.16 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 93614724 | 4112 | 98.688 | 4.112 | 7.1 | 7.1 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15503748 | 1182 | 287.4514 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 93618796 | 4072 | 97.728 | 4.072 | 6.6 | 6.6 | 3B+1S | 0 | 1027 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15505000 | 1252 | 307.4656 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 93622642 | 3846 | 92.304 | 3.846 | 6 | 6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15506210 | 1210 | 314.6126 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 93626599 | 3957 | 94.968 | 3.957 | 5.5 | 5.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15507407 | 1197 | 302.5019 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.2 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 125 |  | 93630761 | 4162 | 99.888 | 4.162 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15508583 | 1176 | 282.5565 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 93635087 | 4326 | 103.824 | 4.326 | 4.5 | 4.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15509760 | 1177 | 272.0758 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 127 |  | 93639529 | 4442 | 106.608 | 4.442 | 4 | 4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15510975 | 1215 | 264.9707 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 128 |  | 93643748 | 4219 | 101.256 | 4.219 | 3.5 | 3.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15512129 | 1154 | 287.9829 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 93648318 | 4570 | 109.68 | 4.57 | 3 | 3 | 3B+1S | 0 | 1026 | 1186 | 1185 | 1186 | 0 | N/A | N/A | N/A | 15513332 | 1203 | 263.2385 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 93652634 | 4316 | 103.584 | 4.316 | 2.6 | 2.6 | 3B+1S | 0 | 1025 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15514514 | 1182 | 273.8647 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 93657131 | 4497 | 107.928 | 4.497 | 2.2 | 2.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15515706 | 1192 | 265.0656 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 129 |  | 93661754 | 4623 | 110.952 | 4.623 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15516894 | 1188 | 256.976 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | -3 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 134 |  | 93665739 | 3985 | 95.64 | 3.985 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15518009 | 1115 | 279.7992 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | -2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 132 |  | 93669708 | 3969 | 95.256 | 3.969 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15519116 | 1107 | 278.9116 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 100720 | 2417.28 | 100.72 | [13 empty] | 27890 | 276.9063 | [7 empty] | 0 | 0 | 1.0667 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:42 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 6, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 7
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
[15 empty] | 10pm - 6am | R.PROVIDENCIA / J. LLAGUNO
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-07 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27505 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93669708 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15519116 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | 139 |  | 93673809 | 4101 | 98.424 | 4.101 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15520310 | 1194 | 291.1485 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 141 |  | 93677861 | 4052 | 97.248 | 4.052 | 5.1 | 5.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15521454 | 1144 | 282.3297 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 5 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 137 |  | 93681872 | 4011 | 96.264 | 4.011 | 6.9 | 6.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15522569 | 1115 | 277.9855 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 6 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 140 |  | 93685810 | 3938 | 94.512 | 3.938 | 8.1 | 8.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15523588 | 1019 | 258.7608 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | DEF | #VALUE! | 7 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | DEF |  | 93689792 | 3982 | 95.568 | 3.982 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 15524703 | 1115 | 280.01 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 136 |  | 93694028 | 4236 | 101.664 | 4.236 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15525813 | 1110 | 262.0397 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 132 |  | 93698751 | 4723 | 113.352 | 4.723 | 9 | 9 | 3B+1S | 1018 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15526990 | 1177 | 249.206 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 93703580 | 4829 | 115.896 | 4.829 | 8.4 | 8.4 | 3B+1S | 1028 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15528178 | 1188 | 246.0137 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 128 |  | 93707805 | 4225 | 101.4 | 4.225 | 7.8 | 7.8 | 3B+1S | 1028 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15529355 | 1177 | 278.5799 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 129 |  | 93711600 | 3795 | 91.08 | 3.795 | 7.2 | 7.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15530563 | 1208 | 318.3136 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 129 |  | 93715090 | 3490 | 83.76 | 3.49 | 6.5 | 6.5 | 3B+1S | 1038 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15531749 | 1186 | 339.8281 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 126 |  | 93719022 | 3932 | 94.368 | 3.932 | 5.9 | 5.9 | 3B+1S | 1038 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15532954 | 1205 | 306.4598 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 19 | A ONG | 17.5 | 125 |  | 93722907 | 3885 | 93.24 | 3.885 | 5.3 | 5.3 | 3B+1S | 1038 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15534116 | 1162 | 299.0991 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 0 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 17.3 | 120 |  | 93726315 | 3408 | 81.792 | 3.408 | 4.7 | 4.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15535269 | 1153 | 338.3216 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 0 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.9 | 118 |  | 93729623 | 3308 | 79.392 | 3.308 | 4 | 4 | 3B+1S | 1026 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15536427 | 1158 | 350.0605 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | -2 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 18 | A ONG | 16.7 | 116 |  | 93732677 | 3054 | 73.296 | 3.054 | 3.4 | 3.4 | 3B+1S | 1027 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15537585 | 1158 | 379.1749 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | -2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.7 | 121 |  | 93735995 | 3318 | 79.632 | 3.318 | 2.8 | 2.8 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15538757 | 1172 | 349.0054 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | -3 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.7 | 126 |  | 93739720 | 3725 | 89.4 | 3.725 | 2.2 | 2.2 | 3B+1S | 1027 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15539913 | 1156 | 314.6309 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | -3 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 127 |  | 93743774 | 4054 | 97.296 | 4.054 | 1.8 | 1.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15541093 | 1180 | 291.0705 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -4 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.6 | 128 |  | 93747681 | 3907 | 93.768 | 3.907 | 1.5 | 1.5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15542230 | 1137 | 291.0161 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -4 | 71 | 50 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.1 | 130 |  | 93751563 | 3882 | 93.168 | 3.882 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15543331 | 1101 | 283.6167 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | DEF | #VALUE! | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 12.6 | DEF |  | 93755392 | 3829 | 91.896 | 3.829 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15544424 | 1093 | 285.4531 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | -1 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 133 |  | 93758861 | 3469 | 83.256 | 3.469 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15545519 | 1095 | 315.6529 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 0 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | 130 |  | 93762539 | 3678 | 88.272 | 3.678 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15546621 | 1102 | 299.6194 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 92831 | 2227.944 | 92.831 | [13 empty] | 27505 | 296.2911 | [7 empty] | 0 | 0 | 1.055 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:44 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
BP3 STOPPED @ 5:19 AM DUE TO SHIFTING OF PUMP
BP4 STARTED @ 5:20 AM DUE TO SHIFTING OF PUMP
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 6, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 8:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 8
ENGINEER / OPERATOR ON DUTY
BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / ARMAN R. RAYALA II
WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[15 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
2018-05-08 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27576 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93762539 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15546621 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
48:00 | 1:00 | 3 | 2.1127 | 2 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 133 |  | 93766501 | 3962 | 95.088 | 3.962 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15547724 | 1103 | 278.3948 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
49:00 | 2:00 | 3 | 2.1127 | 4 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 129 |  | 93770519 | 4018 | 96.432 | 4.018 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15548884 | 1160 | 288.7008 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
50:00 | 3:00 | 3 | 2.1127 | 5 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 136 |  | 93774434 | 3915 | 93.96 | 3.915 | 6.6 | 6.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15549992 | 1108 | 283.014 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
51:00 | 4:00 | 3 | 2.1127 | 6 | 71 | 50 | 71 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 135 |  | 93778316 | 3882 | 93.168 | 3.882 | 8.1 | 8.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15551087 | 1095 | 282.0711 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
52:00 | 5:00 | 3 | 2.1127 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A.ONG | 13.1 | 126 |  | 93782193 | 3877 | 93.048 | 3.877 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15552201 | 1114 | 287.3356 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
53:00 | 6:00 | 3 | 2.1127 | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 124 |  | 93787053 | 4860 | 116.64 | 4.86 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15553315 | 1114 | 229.2181 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
54:00 | 7:00 | 3 | 2.1127 | 8 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 16.7 | 123 |  | 93791814 | 4761 | 114.264 | 4.761 | 8.8 | 8.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1187 | N/A | N/A | N/A | 15554532 | 1217 | 255.6186 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
55:00 | 8:00 | 3 | 2.1127 | 8 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 93796814 | 5000 | 120 | 5 | 8.1 | 8.1 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1187 | N/A | N/A | N/A | 15555717 | 1185 | 237 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
56:00 | 9:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 127 |  | 93801254 | 4440 | 106.56 | 4.44 | 7.4 | 7.4 | 3B+1S | 0 | 1087 | 1187 | 1185 | 0 | 1187 | N/A | N/A | N/A | 15556915 | 1198 | 269.8198 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
57:00 | 10:00 | 3 | 2.1127 | 7 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 127 |  | 93805643 | 4389 | 105.336 | 4.389 | 6.7 | 6.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1187 | N/A | N/A | N/A | 15558130 | 1215 | 276.8284 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
58:00 | 11:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 128 |  | 93810000 | 4357 | 104.568 | 4.357 | 6 | 6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1187 | N/A | N/A | N/A | 15559252 | 1122 | 257.5166 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
59:00 | 12:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 124 |  | 93813390 | 3390 | 81.36 | 3.39 | 5.3 | 5.3 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1187 | N/A | N/A | N/A | 15560529 | 1277 | 376.6962 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
60:00 | 13:00 | 3 | 2.1127 | 5 | 72 | 50.7042 | 76 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 19 | A ONG | 17.5 | 117 |  | 93816921 | 3531 | 84.744 | 3.531 | 4.6 | 4.6 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1187 | N/A | N/A | N/A | 15561709 | 1180 | 334.183 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
61:00 | 14:00 | 3 | 2.1127 | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 17.3 | 117 |  | 93820173 | 3252 | 78.048 | 3.252 | 3.9 | 3.9 | 3B+1S | 0 | 1046 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15562886 | 1177 | 361.9311 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
62:00 | 15:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | 125 |  | 93823851 | 3678 | 88.272 | 3.678 | 3.2 | 3.2 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15563992 | 1106 | 300.7069 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
63:00 | 16:00 | 3 | 2.1127 | 0 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 125 |  | 93827725 | 3874 | 92.976 | 3.874 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15565147 | 1155 | 298.1415 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
64:00 | 17:00 | 3 | 2.1127 | -2 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 128 |  | 93832010 | 4285 | 102.84 | 4.285 | 2.4 | 2.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15566424 | 1277 | 269.5449 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
65:00 | 18:00 | 3 | 2.1127 | -3 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 130 |  | 93835981 | 3971 | 95.304 | 3.971 | 2.1 | 2.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15567468 | 1044 | 321.5815 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
66:00 | 19:00 | 3 | 2.1127 | -4 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.6 | 131 |  | 93840371 | 4390 | 105.36 | 4.39 | 1.9 | 1.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15568669 | 1201 | 273.5763 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
67:00 | 20:00 | 3 | 2.1127 | -4 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 130 |  | 93844550 | 4179 | 100.296 | 4.179 | 1.5 | 1.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15569844 | 1175 | 281.1677 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
68:00 | 21:00 | 3 | 2.1127 | -3 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.1 | 133 |  | 93849025 | 4475 | 107.4 | 4.475 | 1.4 | 1.4 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15570940 | 1096 | 244.9162 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
69:00 | 22:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 130 |  | 93853285 | 4260 | 102.24 | 4.26 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15571977 | 1037 | 243.4272 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
70:00 | 23:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | 138 |  | 93857515 | 4230 | 101.52 | 4.23 | 1.8 | 1.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15573082 | 1105 | 261.2293 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
71:00 | 24:00 | 3 | 2.1127 | 0 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | DEF |  | 93861927 | 4412 | 105.888 | 4.412 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15574197 | 1115 | 252.7199 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[12 empty] | TOTAL | [5 empty] | 99388 | 2385.312 | 99.388 | [13 empty] | 27576 | 277.458 | [7 empty] | 0 | 0 | 0.98833 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[47 empty] | m3/hr | 41.67
NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:47 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 8, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 8:25 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 9
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | A.RAYALA II /J. LLAGUNO
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-09 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27648 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93861927 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15574197 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 69 | 48.5915 | 69 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 149 |  | 93866407 | 4480 | 107.52 | 4.48 | 4.4 | 4.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15575334 | 1137 | 253.7946 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 143 |  | 93870476 | 4069 | 97.656 | 4.069 | 6.2 | 6.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15576442 | 1108 | 272.3028 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 140 |  | 93874548 | 4072 | 97.728 | 4.072 | 7.6 | 7.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15577554 | 1112 | 273.0845 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 14 | A.ONG | 12.8 | 141 |  | 93878624 | 4076 | 97.824 | 4.076 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15578671 | 1117 | 274.0432 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 125 |  | 93882726 | 4102 | 98.448 | 4.102 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15579763 | 1092 | 266.2116 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 129 |  | 93887250 | 4524 | 108.576 | 4.524 | 9.5 | 9.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15580901 | 1138 | 251.5473 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 6 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 131 |  | 93891907 | 4657 | 111.768 | 4.657 | 8.9 | 8.9 | 3B+1S | 1027 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15582093 | 1192 | 255.9588 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 5 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 127 |  | 93896772 | 4865 | 116.76 | 4.865 | 8.2 | 8.2 | 3B+1S | 1038 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15583293 | 1200 | 246.6598 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 18.4 | 127 |  | 93900773 | 4001 | 96.024 | 4.001 | 7.6 | 7.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15584414 | 1121 | 280.18 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 129 |  | 93904187 | 3414 | 81.936 | 3.414 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15585669 | 1255 | 367.604 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.88 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 127 |  | 93907740 | 3553 | 85.272 | 3.553 | 6.1 | 6.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15586963 | 1294 | 364.1993 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 126 |  | 93911225 | 3485 | 83.64 | 3.485 | 5.5 | 5.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15588060 | 1097 | 314.7776 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 125 |  | 93914950 | 3725 | 89.4 | 3.725 | 5 | 5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15589246 | 1186 | 318.3893 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | -2 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 17.3 | 120 |  | 93918313 | 3363 | 80.712 | 3.363 | 4.3 | 4.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15590408 | 1162 | 345.5248 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | 126 |  | 93921948 | 3635 | 87.24 | 3.635 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15591585 | 1177 | 323.7964 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 126 |  | 93926020 | 4072 | 97.728 | 4.072 | 3.2 | 3.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15592745 | 1160 | 284.8723 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 127 |  | 93930354 | 4334 | 104.016 | 4.334 | 2.8 | 2.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15593897 | 1152 | 267.6511 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 93934766 | 4412 | 105.888 | 4.412 | 2.4 | 2.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15595058 | 1161 | 261.1061 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 130 |  | 93939119 | 4353 | 104.472 | 4.353 | 2.1 | 2.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15596232 | 1174 | 269.6991 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -3 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 129 |  | 93943122 | 4003 | 96.072 | 4.003 | 1.7 | 1.7 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15597370 | 1138 | 284.2868 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 93947416 | 4294 | 103.056 | 4.294 | 1.5 | 1.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15598565 | 1195 | 278.2953 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 132 |  | 93951652 | 4236 | 101.664 | 4.236 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15599630 | 1065 | 251.4164 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 0 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 145 |  | 93955537 | 3885 | 93.24 | 3.885 | 1.8 | 1.8 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15600718 | 1088 | 280.0515 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 2 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 143 |  | 93959413 | 3876 | 93.024 | 3.876 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15601845 | 1127 | 290.7637 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 97486 | 2339.664 | 97.486 | [13 empty] | 27648 | 283.61 | [7 empty] | 0 | 0 | 0.97167 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:52 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 8, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 10
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-10 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27719 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 93959413 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15601845 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | 148 |  | 93963518 | 4105 | 98.52 | 4.105 | 4.4 | 4.4 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15602976 | 1131 | 275.5177 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 143 |  | 93967396 | 3878 | 93.072 | 3.878 | 6 | 6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15604104 | 1128 | 290.8716 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 146 |  | 93971364 | 3968 | 95.232 | 3.968 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15605262 | 1158 | 291.8347 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 71 | 50 | 72 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 145 |  | 93975113 | 3749 | 89.976 | 3.749 | 9 | 9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15606346 | 1084 | 289.1438 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 82 | 57.7465 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 127 |  | 93978987 | 3874 | 92.976 | 3.874 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15607423 | 1077 | 278.0072 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 81 | 57.0423 | 79 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 137 |  | 93983530 | 4543 | 109.032 | 4.543 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15608518 | 1095 | 241.0302 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 132 |  | 93988303 | 4773 | 114.552 | 4.773 | 9 | 9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15609711 | 1193 | 249.9476 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 93993062 | 4759 | 114.216 | 4.759 | 8.4 | 8.4 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15610906 | 1195 | 251.1032 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 128 |  | 93997510 | 4448 | 106.752 | 4.448 | 8.1 | 8.1 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15612106 | 1200 | 269.7842 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 94001787 | 4277 | 102.648 | 4.277 | 7.1 | 7.1 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15613310 | 1204 | 281.5057 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.94 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 128 |  | 94005941 | 4154 | 99.696 | 4.154 | 6.5 | 6.5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15614498 | 1188 | 285.9894 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 94009928 | 3987 | 95.688 | 3.987 | 5.8 | 5.8 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15615691 | 1193 | 299.2225 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 125 |  | 94014160 | 4232 | 101.568 | 4.232 | 5.2 | 5.2 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15616878 | 1187 | 280.482 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 126 |  | 94018392 | 4232 | 101.568 | 4.232 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15618042 | 1164 | 275.0473 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 94022858 | 4466 | 107.184 | 4.466 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15619247 | 1205 | 269.8164 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 132 |  | 94027303 | 4445 | 106.68 | 4.445 | 3.7 | 3.7 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15620424 | 1177 | 264.7919 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94031593 | 4290 | 102.96 | 4.29 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15621568 | 1144 | 274.359 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94036424 | 4831 | 115.944 | 4.831 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15622770 | 1202 | 236.804 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 94041127 | 4703 | 112.872 | 4.703 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15623911 | 1141 | 242.6111 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 94045713 | 4586 | 110.064 | 4.586 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15625011 | 1100 | 239.8604 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 69 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 128 |  | 94050202 | 4489 | 107.736 | 4.489 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15626260 | 1249 | 278.2357 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | 0 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 |  | 94054641 | 4439 | 106.536 | 4.439 | 1.7 | 1.7 | 3B+1S | 0 | 1015 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15627356 | 1096 | 246.9025 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 137 |  | 94058896 | 4255 | 102.12 | 4.255 | 2 | 2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15628464 | 1108 | 260.3995 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 94062963 | 4067 | 97.608 | 4.067 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15629564 | 1100 | 270.4696 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 103550 | 2485.2 | 103.55 | [13 empty] | 27719 | 267.6871 | [7 empty] | 0 | 0 | 1 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:12 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 10, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 11
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-11 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27640 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94062963 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15629564 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 94066755 | 3792 | 91.008 | 3.792 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15630670 | 1106 | 291.6667 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.2 | 144 |  | 94070552 | 3797 | 91.128 | 3.797 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15631807 | 1137 | 299.4469 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 71 | 50 | 71 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 143 |  | 94074394 | 3842 | 92.208 | 3.842 | 7.4 | 7.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15632912 | 1105 | 287.6106 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 146 |  | 94078530 | 4136 | 99.264 | 4.136 | 9.1 | 9.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15634026 | 1114 | 269.3424 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 123 |  | 94083324 | 4794 | 115.056 | 4.794 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15635089 | 1063 | 221.7355 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 138 |  | 94086842 | 3518 | 84.432 | 3.518 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15636202 | 1113 | 316.3729 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 130 |  | 94091750 | 4908 | 117.792 | 4.908 | 9.2 | 9.2 | 3B+1S | 1027 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15637404 | 1202 | 244.9063 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 129 |  | 94096456 | 4706 | 112.944 | 4.706 | 8.5 | 8.5 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15638600 | 1196 | 254.1436 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 128 |  | 94100773 | 4317 | 103.608 | 4.317 | 7.9 | 7.9 | 3B+1S | 1046 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15639760 | 1160 | 268.7051 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 94105119 | 4346 | 104.304 | 4.346 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15640975 | 1215 | 279.5674 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.87 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 128 |  | 94109450 | 4331 | 103.944 | 4.331 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15642160 | 1185 | 273.6089 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 125 |  | 94113767 | 4317 | 103.608 | 4.317 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15643370 | 1210 | 280.2872 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 94118091 | 4324 | 103.776 | 4.324 | 5.3 | 5.3 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15644548 | 1178 | 272.4329 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 94122499 | 4408 | 105.792 | 4.408 | 4.8 | 4.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15645706 | 1158 | 262.7042 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 128 |  | 94126592 | 4093 | 98.232 | 4.093 | 4.4 | 4.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15646824 | 1118 | 273.1493 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 131 |  | 94131170 | 4578 | 109.872 | 4.578 | 3.8 | 3.8 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15648034 | 1210 | 264.3076 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 94135364 | 4194 | 100.656 | 4.194 | 3.4 | 3.4 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15649182 | 1148 | 288.5074 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94139893 | 4529 | 108.696 | 4.529 | 2.9 | 2.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15650334 | 1152 | 253.4776 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 94144501 | 4608 | 110.592 | 4.608 | 2.6 | 2.6 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15651531 | 1197 | 259.7656 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 94148870 | 4369 | 104.856 | 4.369 | 2.2 | 2.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15652701 | 1170 | 267.7958 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 94153126 | 4256 | 102.144 | 4.256 | 1.9 | 1.9 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15653817 | 1116 | 262.218 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 127 |  | 94157956 | 4830 | 115.92 | 4.83 | 1.6 | 1.6 | 3B+1S | 1025 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15655027 | 1210 | 250.5176 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 139 |  | 94162214 | 4258 | 102.192 | 4.258 | 1.9 | 1.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15656109 | 1082 | 254.1099 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 2 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 137 |  | 94166479 | 4265 | 102.36 | 4.265 | 2.7 | 2.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15657204 | 1095 | 256.7409 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 103516 | 2484.384 | 103.516 | [13 empty] | 27640 | 267.0119 | [7 empty] | 0 | 0 | 0.98 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:05 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 11, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 12
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-11 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27726 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94166479 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15657204 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 139 |  | 94170482 | 4003 | 96.072 | 4.003 | 3.9 | 3.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15658332 | 1128 | 281.7887 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 141 |  | 94174552 | 4070 | 97.68 | 4.07 | 5.7 | 5.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15659471 | 1139 | 279.8526 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 71 | 50 | 71 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 143 |  | 94178643 | 4091 | 98.184 | 4.091 | 7.3 | 7.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15660617 | 1146 | 280.1271 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | 144 |  | 94182442 | 3799 | 91.176 | 3.799 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15661661 | 1044 | 274.8092 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 126 |  | 94186439 | 3997 | 95.928 | 3.997 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15662775 | 1114 | 278.709 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 138 |  | 94190666 | 4227 | 101.448 | 4.227 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15663862 | 1087 | 257.1564 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 134 |  | 94195275 | 4609 | 110.616 | 4.609 | 9.4 | 9.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15665015 | 1153 | 250.1627 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 5 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 131 |  | 94200070 | 4795 | 115.08 | 4.795 | 8.9 | 8.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15666220 | 1205 | 251.3034 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 94204450 | 4380 | 105.12 | 4.38 | 8.2 | 8.2 | 3B+1S | 0 | 1035 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15667400 | 1180 | 269.4064 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 130 |  | 94208150 | 3700 | 88.8 | 3.7 | 7.5 | 7.5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15668619 | 1219 | 329.4595 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.79 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 130 |  | 94211759 | 3609 | 86.616 | 3.609 | 6.9 | 6.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15669784 | 1165 | 322.8041 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 94215811 | 4052 | 97.248 | 4.052 | 6.3 | 6.3 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15671018 | 1234 | 304.541 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 94219896 | 4085 | 98.04 | 4.085 | 5.7 | 5.7 | 3B+1S | 0 | 1036 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15672167 | 1149 | 281.2729 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 94224025 | 4129 | 99.096 | 4.129 | 5.1 | 5.1 | 3B+1S | 0 | 1026 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15673321 | 1154 | 279.4866 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.21 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 128 |  | 94228446 | 4421 | 106.104 | 4.421 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15674473 | 1152 | 260.5745 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 94232971 | 4525 | 108.6 | 4.525 | 4 | 4 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15675696 | 1223 | 270.2762 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94237415 | 4444 | 106.656 | 4.444 | 3.5 | 3.5 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15676834 | 1138 | 275.2025 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 94241881 | 4466 | 107.184 | 4.466 | 3.1 | 3.1 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15678009 | 1175 | 254.8142 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.15 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 94246375 | 4494 | 107.856 | 4.494 | 2.7 | 2.7 | 3B+1S | 0 | 1026 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15679187 | 1178 | 262.1273 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 94250892 | 4517 | 108.408 | 4.517 | 2.3 | 2.3 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15680366 | 1179 | 261.0139 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 94255375 | 4483 | 107.592 | 4.483 | 1.9 | 1.9 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15681510 | 1144 | 255.1863 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 130 |  | 94260238 | 4863 | 116.712 | 4.863 | 1.7 | 1.7 | 3B+1S | 0 | 1025 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15682741 | 1231 | 253.1359 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 132 |  | 94264592 | 4354 | 104.496 | 4.354 | 1.9 | 1.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15683820 | 1079 | 247.8181 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 76 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 140 |  | 94268675 | 4083 | 97.992 | 4.083 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15684930 | 1110 | 271.8589 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 102196 | 2452.704 | 102.196 | [13 empty] | 27726 | 271.3022 | [7 empty] | 0 | 0 | 1.03 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:23 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 12, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR.JIMMY DIOKNO AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 3:10 PM TO DEWATERING OF BP3 CHAMBER AND MAIN SUCTION CHAMBER.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 13
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-13 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27518 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94268675 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15684930 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 70 | 49.2958 | 76 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 140 |  | 94273100 | 4425 | 106.2 | 4.425 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15686000 | 1070 | 241.8079 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 5 | 70 | 49.2958 | 78 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 142 |  | 94277500 | 4400 | 105.6 | 4.4 | 6.1 | 6.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15687120 | 1120 | 254.5455 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 6 | 71 | 50 | 78 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 141 |  | 94281912 | 4412 | 105.888 | 4.412 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15688312 | 1192 | 270.1723 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 8 | 71 | 50 | 80 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 134 |  | 94286362 | 4450 | 106.8 | 4.45 | 9.4 | 9.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15689372 | 1060 | 238.2022 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 |  | 94290709 | 4347 | 104.328 | 4.347 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15690469 | 1097 | 252.3579 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 133 |  | 94295902 | 5193 | 124.632 | 5.193 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15691687 | 1218 | 234.5465 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.84 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | 141 |  | 94300523 | 4621 | 110.904 | 4.621 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15692640 | 953 | 206.2324 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 9 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 132 |  | 94305635 | 5112 | 122.688 | 5.112 | 9.5 | 9.5 | 3B+1S | 1027 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15693736 | 1096 | 214.3975 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 131 |  | 94310390 | 4755 | 114.12 | 4.755 | 9 | 9 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15694937 | 1201 | 252.5762 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 132 |  | 94314788 | 4398 | 105.552 | 4.398 | 8.4 | 8.4 | 3B+1S | 1027 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15696135 | 1198 | 272.3965 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 5 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 131 |  | 94319108 | 4320 | 103.68 | 4.32 | 7.8 | 7.8 | 3B+1S | 1028 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15697336 | 1201 | 278.0093 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 3 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 129 |  | 94323475 | 4367 | 104.808 | 4.367 | 7.2 | 7.2 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15698513 | 1177 | 269.5214 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 129 |  | 94327765 | 4290 | 102.96 | 4.29 | 6.7 | 6.7 | 3B+1S | 1027 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15699695 | 1182 | 275.5245 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 94332004 | 4239 | 101.736 | 4.239 | 6.1 | 6.1 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15700852 | 1157 | 272.9417 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 130 |  | 94336626 | 4622 | 110.928 | 4.622 | 5.7 | 5.7 | 3B+1S | 1027 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15702048 | 1196 | 258.7624 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 131 |  | 94341244 | 4618 | 110.832 | 4.618 | 5.2 | 5.2 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15703220 | 1172 | 253.7895 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 94345842 | 4598 | 110.352 | 4.598 | 4.7 | 4.7 | 3B+1S | 1026 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15704394 | 1174 | 254.8934 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 94350628 | 4786 | 114.864 | 4.786 | 4.3 | 4.3 | 3B+1S | 1025 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15705588 | 1194 | 245.2988 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 131 |  | 94355330 | 4702 | 112.848 | 4.702 | 3.8 | 3.8 | 3B+1S | 1025 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15706732 | 1144 | 243.3007 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.6 | 128 |  | 94360204 | 4874 | 116.976 | 4.874 | 3.3 | 3.3 | 3B+1S | 1036 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15707915 | 1183 | 242.7165 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.1 | 127 |  | 94365055 | 4851 | 116.424 | 4.851 | 2.9 | 2.9 | 3B+1S | 1035 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15709063 | 1148 | 236.6522 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -2 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A ONG | 12.6 | 125 |  | 94370238 | 5183 | 124.392 | 5.183 | 2.6 | 2.6 | 3B+1S | 1035 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15710255 | 1192 | 229.9826 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -1 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 141 |  | 94374966 | 4728 | 113.472 | 4.728 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15711338 | 1083 | 229.0609 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 140 |  | 94379822 | 4856 | 116.544 | 4.856 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15712448 | 1110 | 228.5832 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 111147 | 2667.528 | 111.147 | [13 empty] | 27518 | 247.582 | [7 empty] | 0 | 0 | 0.99667 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:00 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 13, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 14
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-14 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27279 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94379822 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15712448 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 2 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 139 |  | 94384336 | 4514 | 108.336 | 4.514 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15713552 | 1104 | 244.5724 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 142 |  | 94388879 | 4543 | 109.032 | 4.543 | 7 | 7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15714657 | 1105 | 243.2313 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 142 |  | 94393193 | 4314 | 103.536 | 4.314 | 8.5 | 8.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15715761 | 1104 | 255.911 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 83 | 58.4507 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 117 |  | 94397383 | 4190 | 100.56 | 4.19 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 0 | 1185 | N/A | N/A | N/A | 15716821 | 1060 | 252.9833 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 124 |  | 94402195 | 4812 | 115.488 | 4.812 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15717905 | 1084 | 225.2702 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 135 |  | 94407670 | 5475 | 131.4 | 5.475 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15719005 | 1100 | 200.9132 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.83 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 140 |  | 94412122 | 4452 | 106.848 | 4.452 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15720050 | 1045 | 234.726 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 8 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 140 |  | 94416495 | 4373 | 104.952 | 4.373 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15721160 | 1110 | 253.8303 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 6 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | 132 |  | 94420838 | 4343 | 104.232 | 4.343 | 8.9 | 8.9 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15722357 | 1197 | 275.6159 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 133 |  | 94424540 | 3702 | 88.848 | 3.702 | 8.4 | 8.4 | 3B+1S | 0 | 1028 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15723541 | 1184 | 319.8271 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 5 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 132 |  | 94428770 | 4230 | 101.52 | 4.23 | 7.7 | 7.7 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15724934 | 1393 | 329.3144 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 130 |  | 94432703 | 3933 | 94.392 | 3.933 | 7.1 | 7.1 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15725918 | 984 | 250.1907 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 129 |  | 94436635 | 3932 | 94.368 | 3.932 | 6.5 | 6.5 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15727091 | 1173 | 298.3215 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 128 |  | 94440515 | 3880 | 93.12 | 3.88 | 6.1 | 6.1 | 3B+1S | 0 | 1028 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15728241 | 1150 | 296.3918 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 1 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | 129 |  | 94444996 | 4481 | 107.544 | 4.481 | 5.6 | 5.6 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15729391 | 1150 | 256.6391 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 0 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | 130 |  | 94449375 | 4379 | 105.096 | 4.379 | 5.3 | 5.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15730521 | 1130 | 258.0498 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 94453530 | 4155 | 99.72 | 4.155 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15731690 | 1169 | 271.9615 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 94458009 | 4479 | 107.496 | 4.479 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15732858 | 1168 | 260.9958 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.6 | 129 |  | 94463039 | 5030 | 120.72 | 5.03 | 4 | 4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15734004 | 1146 | 227.833 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 94467794 | 4755 | 114.12 | 4.755 | 3.6 | 3.6 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15735157 | 1153 | 242.4816 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | 127 |  | 94472659 | 4865 | 116.76 | 4.865 | 3.2 | 3.2 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15736339 | 1182 | 242.9599 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -1 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 94477076 | 4417 | 106.008 | 4.417 | 2.9 | 2.9 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15737481 | 1142 | 258.5465 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 141 |  | 94481585 | 4509 | 108.216 | 4.509 | 3.2 | 3.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15738566 | 1085 | 240.6299 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | 139 |  | 94486187 | 4602 | 110.448 | 4.602 | 4.2 | 4.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15739727 | 1161 | 252.2816 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 106365 | 2552.76 | 106.365 | [13 empty] | 27279 | 256.4659 | [7 empty] | 0 | 0 | 0.98167 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:28 AM WATER ELEVATION (9.5 M)
BP1 STOPPED @ 4:45 AM DUE TO SHIFTING OF PUMP
BP3 STARTED @ 4:46 AM DUE TO SHIFTING OF PUMP
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 14, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 15
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-15 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27420 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94486187 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15739727 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 72 | 50.7042 | 72 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 137 |  | 94489926 | 3739 | 89.736 | 3.739 | 5.2 | 5.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15740826 | 1099 | 293.9289 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | 140 |  | 94493461 | 3535 | 84.84 | 3.535 | 6.4 | 6.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15741868 | 1042 | 294.7666 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 141 |  | 94497099 | 3638 | 87.312 | 3.638 | 7.6 | 7.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15742943 | 1075 | 295.492 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 71 | 50 | 71 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 145 |  | 94501109 | 4010 | 96.24 | 4.01 | 9.4 | 9.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15744077 | 1134 | 282.793 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 82 | 57.7465 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 125 |  | 94505025 | 3916 | 93.984 | 3.916 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15745144 | 1067 | 272.4719 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 9 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 129 |  | 94509415 | 4390 | 105.36 | 4.39 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15746251 | 1107 | 252.164 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 130 |  | 94514011 | 4596 | 110.304 | 4.596 | 9 | 9 | 3B+1S | 1045 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15747449 | 1198 | 260.6614 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 129 |  | 94518800 | 4789 | 114.936 | 4.789 | 8.4 | 8.4 | 3B+1S | 1045 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15748653 | 1204 | 251.4095 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 129 |  | 94523190 | 4390 | 105.36 | 4.39 | 7.7 | 7.7 | 3B+1S | 1045 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15749825 | 1172 | 266.9704 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 94527837 | 4647 | 111.528 | 4.647 | 7 | 7 | 3B+1S | 1045 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15751033 | 1208 | 259.9527 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 94532384 | 4547 | 109.128 | 4.547 | 6.4 | 6.4 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15752248 | 1215 | 267.2091 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 129 |  | 94537170 | 4786 | 114.864 | 4.786 | 5.8 | 5.8 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15753419 | 1171 | 244.672 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 130 |  | 94541721 | 4551 | 109.224 | 4.551 | 5.3 | 5.3 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15754563 | 1144 | 251.3733 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 127 |  | 94545698 | 3977 | 95.448 | 3.977 | 4.8 | 4.8 | 3B+1S | 1025 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15755691 | 1128 | 283.6309 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | -1 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 128 |  | 94550345 | 4647 | 111.528 | 4.647 | 4.4 | 4.4 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15756861 | 1170 | 251.7753 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | -2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 131 |  | 94554872 | 4527 | 108.648 | 4.527 | 3.9 | 3.9 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15758041 | 1180 | 260.6583 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 94559086 | 4214 | 101.136 | 4.214 | 3.5 | 3.5 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15759171 | 1130 | 280.019 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 131 |  | 94563149 | 4063 | 97.512 | 4.063 | 3.1 | 3.1 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15760350 | 1179 | 278.1196 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 94568035 | 4886 | 117.264 | 4.886 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15761506 | 1156 | 236.5944 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 94573889 | 5854 | 140.496 | 5.854 | 2.5 | 2.5 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15762649 | 1143 | 195.2511 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 94578917 | 5028 | 120.672 | 5.028 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15763805 | 1156 | 229.9125 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 |  | 94583654 | 4737 | 113.688 | 4.737 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15764961 | 1156 | 244.0363 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | 136 |  | 94588113 | 4459 | 107.016 | 4.459 | 2.2 | 2.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15766054 | 1093 | 245.1222 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 141 |  | 94592405 | 4292 | 103.008 | 4.292 | 2.9 | 2.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15767147 | 1093 | 254.6598 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 106218 | 2549.232 | 106.218 | [13 empty] | 27420 | 258.1483 | [7 empty] | 0 | 0 | 0.97833 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:01 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 15, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 16
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
| WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA/J. LLAGUNO
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-16 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27451 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94592405 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15767147 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 69 | 48.5915 | 69 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 145 |  | 94596611 | 4206 | 100.944 | 4.206 | 4.3 | 4.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15768262 | 1115 | 265.0975 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 142 |  | 94600642 | 4031 | 96.744 | 4.031 | 6 | 6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15769385 | 1123 | 278.5909 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 143 |  | 94604561 | 3919 | 94.056 | 3.919 | 7.6 | 7.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15770487 | 1102 | 281.1942 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | 147 |  | 94608401 | 3840 | 92.16 | 3.84 | 9.2 | 9.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15771584 | 1097 | 285.6771 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 83 | 58.4507 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 129 |  | 94612691 | 4290 | 102.96 | 4.29 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15772634 | 1050 | 244.7552 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | 139 |  | 94617762 | 5071 | 121.704 | 5.071 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15773826 | 1192 | 235.0621 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 131 |  | 94622306 | 4544 | 109.056 | 4.544 | 9.2 | 9.2 | 3B+1S | 0 | 1027 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15774890 | 1064 | 234.1549 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 131 |  | 94627758 | 5452 | 130.848 | 5.452 | 8.6 | 8.6 | 3B+1S | 0 | 1027 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15776146 | 1256 | 230.3742 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 130 |  | 94632604 | 4846 | 116.304 | 4.846 | 7.9 | 7.9 | 3B+1S | 0 | 1028 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15777312 | 1166 | 240.6108 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 131 |  | 94637168 | 4564 | 109.536 | 4.564 | 7.4 | 7.4 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15778482 | 1170 | 256.3541 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.22 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 94641056 | 3888 | 93.312 | 3.888 | 6.8 | 6.8 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15779642 | 1160 | 298.3539 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 94645118 | 4062 | 97.488 | 4.062 | 6.2 | 6.2 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15780870 | 1228 | 302.3141 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 129 |  | 94648932 | 3814 | 91.536 | 3.814 | 5.7 | 5.7 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15781978 | 1108 | 290.5087 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 130 |  | 94653685 | 4753 | 114.072 | 4.753 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15783175 | 1197 | 251.8409 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 130 |  | 94657877 | 4192 | 100.608 | 4.192 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15784329 | 1154 | 275.2863 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 131 |  | 94662299 | 4422 | 106.128 | 4.422 | 4.4 | 4.4 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15785489 | 1160 | 262.3247 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 94666824 | 4525 | 108.6 | 4.525 | 3.9 | 3.9 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15786640 | 1151 | 256.3536 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 94671478 | 4654 | 111.696 | 4.654 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15787802 | 1162 | 247.3141 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 94676129 | 4651 | 111.624 | 4.651 | 3.1 | 3.1 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15788965 | 1163 | 250.0538 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 94680710 | 4581 | 109.944 | 4.581 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15790111 | 1146 | 250.1637 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 126 |  | 94685648 | 4938 | 118.512 | 4.938 | 2.3 | 2.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15791262 | 1151 | 233.0903 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 130 |  | 94690104 | 4456 | 106.944 | 4.456 | 2 | 2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15792410 | 1148 | 257.6302 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -2 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 133 |  | 94694757 | 4653 | 111.672 | 4.653 | 2.4 | 2.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15793511 | 1101 | 236.6215 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 135 |  | 94699376 | 4619 | 110.856 | 4.619 | 3 | 3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15794598 | 1087 | 235.3323 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 106971 | 2567.304 | 106.971 | [13 empty] | 27451 | 256.621 | [7 empty] | 0 | 0 | 1.0417 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:05 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 16, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 17
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-17 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27597 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94699376 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15794598 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 143 |  | 94703704 | 4328 | 103.872 | 4.328 | 4.6 | 4.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15795809 | 1211 | 279.8059 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 142 |  | 94707906 | 4202 | 100.848 | 4.202 | 5.4 | 5.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15796911 | 1102 | 262.2561 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 145 |  | 94712062 | 4156 | 99.744 | 4.156 | 6.1 | 6.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15797993 | 1082 | 260.3465 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 146 |  | 94715631 | 3569 | 85.656 | 3.569 | 8.2 | 8.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15798997 | 1004 | 281.3113 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 128 |  | 94720063 | 4432 | 106.368 | 4.432 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15800099 | 1102 | 248.6462 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 76 | 53.5211 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 13.1 | 139 |  | 94725126 | 5063 | 121.512 | 5.063 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15801240 | 1141 | 225.3605 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 133 |  | 94729794 | 4668 | 112.032 | 4.668 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15802330 | 1090 | 233.5047 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 128 |  | 94734710 | 4916 | 117.984 | 4.916 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15803544 | 1214 | 246.9487 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 130 |  | 94739114 | 4404 | 105.696 | 4.404 | 7.7 | 7.7 | 3B+1S | 1046 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15804734 | 1190 | 270.2089 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 94743158 | 4044 | 97.056 | 4.044 | 7 | 7 | 3B+1S | 1048 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15805932 | 1198 | 296.2413 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.18 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 128 |  | 94746656 | 3498 | 83.952 | 3.498 | 6.4 | 6.4 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15807066 | 1134 | 324.1852 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 94750492 | 3836 | 92.064 | 3.836 | 5.8 | 5.8 | 3B+1S | 1046 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15808230 | 1164 | 303.4411 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 94755166 | 4674 | 112.176 | 4.674 | 5.1 | 5.1 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15809508 | 1278 | 273.4275 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 94759041 | 3875 | 93 | 3.875 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15810660 | 1152 | 297.2903 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 94763227 | 4186 | 100.464 | 4.186 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15811812 | 1152 | 275.2031 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 94767667 | 4440 | 106.56 | 4.44 | 3.7 | 3.7 | 3B+1S | 1015 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15812978 | 1166 | 262.6126 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94772203 | 4536 | 108.864 | 4.536 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15814149 | 1171 | 257.0547 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 128 |  | 94776450 | 4247 | 101.928 | 4.247 | 2.9 | 2.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15815320 | 1171 | 275.724 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 94780949 | 4499 | 107.976 | 4.499 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15816488 | 1168 | 259.6132 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -2 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 128 |  | 94786089 | 5140 | 123.36 | 5.14 | 2.2 | 2.2 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15817646 | 1158 | 225.2918 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | 128 |  | 94790779 | 4690 | 112.56 | 4.69 | 1.9 | 1.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15818783 | 1137 | 242.4307 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 127 |  | 94795650 | 4871 | 116.904 | 4.871 | 1.6 | 1.6 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15819944 | 1161 | 238.3494 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 134 |  | 94800355 | 4705 | 112.92 | 4.705 | 1.8 | 1.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15821082 | 1138 | 241.8704 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | -1 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 139 |  | 94804705 | 4350 | 104.4 | 4.35 | 2.6 | 2.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15822195 | 1113 | 255.8621 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 105329 | 2527.896 | 105.329 | [13 empty] | 27597 | 262.0076 | [7 empty] | 0 | 0 | 1.045 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:27 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 17, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 18
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-18 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27652 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94804705 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15822195 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 1 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 142 |  | 94808809 | 4104 | 98.496 | 4.104 | 3.8 | 3.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15823349 | 1154 | 281.1891 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 140 |  | 94812849 | 4040 | 96.96 | 4.04 | 5.5 | 5.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15824466 | 1117 | 276.4851 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 138 |  | 94816859 | 4010 | 96.24 | 4.01 | 6.4 | 6.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15825571 | 1105 | 275.5611 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 7 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 144 |  | 94820896 | 4037 | 96.888 | 4.037 | 8.1 | 8.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15826674 | 1103 | 273.2227 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 128 |  | 94825197 | 4301 | 103.224 | 4.301 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15827780 | 1106 | 257.1495 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 13.1 | 140 |  | 94830038 | 4841 | 116.184 | 4.841 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15828878 | 1098 | 226.8126 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 132 |  | 94835140 | 5102 | 122.448 | 5.102 | 9.2 | 9.2 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15830110 | 1232 | 241.4739 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 130 |  | 94839970 | 4830 | 115.92 | 4.83 | 8.5 | 8.5 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15831312 | 1202 | 248.8613 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 128 |  | 94844414 | 4444 | 106.656 | 4.444 | 7.9 | 7.9 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15832392 | 1080 | 243.0243 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 94848766 | 4352 | 104.448 | 4.352 | 7.2 | 7.2 | 3B+1S | 0 | 1046 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15833644 | 1252 | 287.6838 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.17 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 129 |  | 94852508 | 3742 | 89.808 | 3.742 | 6.5 | 6.5 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15834840 | 1196 | 319.6152 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 132 |  | 94856520 | 4012 | 96.288 | 4.012 | 5.7 | 5.7 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15836070 | 1230 | 306.5803 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 126 |  | 94860356 | 3836 | 92.064 | 3.836 | 5.2 | 5.2 | 3B+1S | 0 | 1036 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15837234 | 1164 | 303.4411 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 94864687 | 4331 | 103.944 | 4.331 | 4.7 | 4.7 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15838397 | 1163 | 268.5292 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 128 |  | 94869135 | 4448 | 106.752 | 4.448 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15839548 | 1151 | 258.768 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 132 |  | 94873604 | 4469 | 107.256 | 4.469 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15840711 | 1163 | 260.2372 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 94878089 | 4485 | 107.64 | 4.485 | 3.4 | 3.4 | 3B+1S | 0 | 1006 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15841868 | 1157 | 259.3088 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94882737 | 4648 | 111.552 | 4.648 | 3.1 | 3.1 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15843018 | 1150 | 248.9243 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 94887122 | 4385 | 105.24 | 4.385 | 2.8 | 2.8 | 3B+1S | 0 | 1005 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15844174 | 1156 | 263.626 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 94892282 | 5160 | 123.84 | 5.16 | 2.4 | 2.4 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15845354 | 1180 | 228.6822 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 94897069 | 4787 | 114.888 | 4.787 | 2 | 2 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15846496 | 1142 | 238.5628 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | DEF |  | 94901924 | 4855 | 116.52 | 4.855 | 1.7 | 1.7 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15847697 | 1201 | 247.3738 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | DEF |  | 94906211 | 4287 | 102.888 | 4.287 | 1.9 | 1.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15848774 | 1077 | 251.2246 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 94910342 | 4131 | 99.144 | 4.131 | 2 | 2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15849847 | 1073 | 259.7434 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 105637 | 2535.288 | 105.637 | [13 empty] | 27652 | 261.7643 | [7 empty] | 0 | 0 | 1.0883 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:49 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 18, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 19
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-19 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27569 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 94910342 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15849847 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 68 | 47.8873 | 74 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | DEF |  | 94914765 | 4423 | 106.152 | 4.423 | 3.6 | 3.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15850991 | 1144 | 258.648 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 3 | 71 | 50 | 76 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 94918665 | 3900 | 93.6 | 3.9 | 5.4 | 5.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15852091 | 1100 | 282.0513 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 4 | 71 | 50 | 78 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 94922608 | 3943 | 94.632 | 3.943 | 7 | 7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15853209 | 1118 | 283.5405 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 70 | 49.2958 | 78 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 147 |  | 94926571 | 3963 | 95.112 | 3.963 | 8.6 | 8.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15854335 | 1126 | 284.1282 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 126 |  | 94930590 | 4019 | 96.456 | 4.019 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15855392 | 1057 | 263.0007 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | 130 |  | 94934715 | 4125 | 99 | 4.125 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15856532 | 1140 | 276.3636 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 134 |  | 94939802 | 5087 | 122.088 | 5.087 | 9.1 | 9.1 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15857632 | 1100 | 216.2375 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 94945188 | 5386 | 129.264 | 5.386 | 8.4 | 8.4 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15858898 | 1266 | 235.0538 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 129 |  | 94949902 | 4714 | 113.136 | 4.714 | 7.7 | 7.7 | 3B+1S | 1047 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15860132 | 1234 | 261.7734 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 94954094 | 4192 | 100.608 | 4.192 | 7 | 7 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15861238 | 1106 | 263.8359 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.16 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 128 |  | 94958246 | 4152 | 99.648 | 4.152 | 6.3 | 6.3 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15862388 | 1150 | 276.975 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 94962144 | 3898 | 93.552 | 3.898 | 5.7 | 5.7 | 3B+1S | 1037 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15863618 | 1230 | 315.5464 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 94965798 | 3654 | 87.696 | 3.654 | 5.1 | 5.1 | 3B+1S | 1036 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15864802 | 1184 | 324.0285 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 17.3 | 128 |  | 94970242 | 4444 | 106.656 | 4.444 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15865992 | 1190 | 267.7768 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 94974633 | 4391 | 105.384 | 4.391 | 4.2 | 4.2 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15867155 | 1163 | 264.8599 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 94978945 | 4312 | 103.488 | 4.312 | 3.7 | 3.7 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15868299 | 1144 | 265.3061 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94983694 | 4749 | 113.976 | 4.749 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15869460 | 1161 | 240.8928 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 94988294 | 4600 | 110.4 | 4.6 | 2.9 | 2.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15870613 | 1153 | 252.3913 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 94993232 | 4938 | 118.512 | 4.938 | 2.6 | 2.6 | 3B+1S | 1014 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15871804 | 1191 | 241.1908 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 94997801 | 4569 | 109.656 | 4.569 | 2.3 | 2.3 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15872931 | 1127 | 246.6623 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -5 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 95002567 | 4766 | 114.384 | 4.766 | 1.9 | 1.9 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15874069 | 1138 | 238.7747 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -5 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 133 |  | 95007125 | 4558 | 109.392 | 4.558 | 1.7 | 1.7 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15875230 | 1161 | 254.717 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 138 |  | 95011862 | 4737 | 113.688 | 4.737 | 1.9 | 1.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15876318 | 1088 | 229.6812 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | -1 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | DEF |  | 95016120 | 4258 | 102.192 | 4.258 | 2.8 | 2.8 |  | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15877416 | 1098 | 257.8675 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 105778 | 2538.672 | 105.778 | [13 empty] | 27569 | 260.6308 | [7 empty] | 0 | 0 | 1.0583 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:28 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 19, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 20
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-20 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27525 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95016120 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15877416 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 144 |  | 95020533 | 4413 | 105.912 | 4.413 | 3.9 | 3.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15878584 | 1168 | 264.6726 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 140 |  | 95024919 | 4386 | 105.264 | 4.386 | 5.8 | 5.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15879697 | 1113 | 253.762 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 4 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 142 |  | 95029037 | 4118 | 98.832 | 4.118 | 7.2 | 7.2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15880799 | 1102 | 267.6056 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 145 |  | 95033041 | 4004 | 96.096 | 4.004 | 8.8 | 8.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15881894 | 1095 | 273.4765 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 95036672 | 3631 | 87.144 | 3.631 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1147 | 1185 | N/A | N/A | N/A | 15882936 | 1042 | 286.9733 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 132 |  | 95041398 | 4726 | 113.424 | 4.726 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15883964 | 1028 | 217.5201 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 141 |  | 95047058 | 5660 | 135.84 | 5.66 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15885190 | 1226 | 216.6078 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 6 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | 132 |  | 95051868 | 4810 | 115.44 | 4.81 | 9.1 | 9.1 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15886300 | 1110 | 230.7692 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 131 |  | 95056132 | 4264 | 102.336 | 4.264 | 8.6 | 8.6 | 3B+1S | 0 | 1047 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15887460 | 1160 | 272.045 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 131 |  | 95060214 | 4082 | 97.968 | 4.082 | 7.9 | 7.9 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15888658 | 1198 | 293.4836 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.16 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 5 | 78 | 54.9296 | 74 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | 131 |  | 95064126 | 3912 | 93.888 | 3.912 | 7.2 | 7.2 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15889856 | 1198 | 306.2372 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 130 |  | 95068042 | 3916 | 93.984 | 3.916 | 6.5 | 6.5 | 3B+1S | 0 | 1047 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15891018 | 1162 | 296.7314 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 128 |  | 95071874 | 3832 | 91.968 | 3.832 | 5.9 | 5.9 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15892184 | 1166 | 304.2797 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 95076574 | 4700 | 112.8 | 4.7 | 5.3 | 5.3 | 3B+1S | 0 | 1037 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15893445 | 1261 | 268.2979 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.23 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 95081173 | 4599 | 110.376 | 4.599 | 4.8 | 4.8 | 3B+1S | 0 | 1037 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15894611 | 1166 | 253.5334 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 130 |  | 95085807 | 4634 | 111.216 | 4.634 | 4.3 | 4.3 | 3B+1S | 0 | 1025 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15895793 | 1182 | 255.0712 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 95090538 | 4731 | 113.544 | 4.731 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15896944 | 1151 | 249.8415 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 95094723 | 4185 | 100.44 | 4.185 | 3.3 | 3.3 | 3B+1S | 0 | 1026 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15898015 | 1071 | 275.0299 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 95099518 | 4795 | 115.08 | 4.795 | 2.9 | 2.9 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15899269 | 1254 | 261.5224 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 95104293 | 4775 | 114.6 | 4.775 | 2.5 | 2.5 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15900445 | 1176 | 246.2827 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 95108729 | 4436 | 106.464 | 4.436 | 2.2 | 2.2 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15901568 | 1123 | 253.156 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | DEF |  | 95113580 | 4851 | 116.424 | 4.851 | 1.9 | 1.9 | 3B+1S | 0 | 1025 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15902770 | 1202 | 247.784 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | DEF |  | 95118191 | 4611 | 110.664 | 4.611 | 2.1 | 2.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15903836 | 1066 | 231.1863 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | DEF |  | 95122443 | 4252 | 102.048 | 4.252 | 3.1 | 3.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15904941 | 1105 | 259.8777 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 106323 | 2551.752 | 106.323 | [13 empty] | 27525 | 258.881 | [7 empty] | 0 | 0 | 1.1017 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:30 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 20, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 21
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-21 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27541 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95122443 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15904941 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 137 |  | 95126552 | 4109 | 98.616 | 4.109 | 4.5 | 4.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15906087 | 1146 | 278.9 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 139 |  | 95130599 | 4047 | 97.128 | 4.047 | 5.3 | 5.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15907191 | 1104 | 272.7947 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 140 |  | 95134625 | 4026 | 96.624 | 4.026 | 6.8 | 6.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15908259 | 1068 | 265.2757 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | 143 |  | 95138714 | 4089 | 98.136 | 4.089 | 8.3 | 8.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15909363 | 1104 | 269.9927 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 129 |  | 95142910 | 4196 | 100.704 | 4.196 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15910479 | 1116 | 265.9676 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | 131 |  | 95147876 | 4966 | 119.184 | 4.966 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15911546 | 1067 | 214.8611 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 134 |  | 95153015 | 5139 | 123.336 | 5.139 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15912788 | 1242 | 241.6813 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 130 |  | 95158000 | 4985 | 119.64 | 4.985 | 8.5 | 8.5 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15913973 | 1185 | 237.7131 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | DEF |  | 95162899 | 4899 | 117.576 | 4.899 | 7.8 | 7.8 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15915189 | 1216 | 248.2139 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 132 |  | 95166860 | 3961 | 95.064 | 3.961 | 7.2 | 7.2 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15916388 | 1199 | 302.7013 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 131 |  | 95170652 | 3792 | 91.008 | 3.792 | 6.5 | 6.5 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15917577 | 1189 | 313.5549 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 95174394 | 3742 | 89.808 | 3.742 | 6 | 6 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15918738 | 1161 | 310.2619 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 127 |  | 95178164 | 3770 | 90.48 | 3.77 | 5.4 | 5.4 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15919909 | 1171 | 310.6101 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 127 |  | 95182025 | 3861 | 92.664 | 3.861 | 5 | 5 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15921041 | 1132 | 293.1883 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 130 |  | 95186319 | 4294 | 103.056 | 4.294 | 4.5 | 4.5 | 3B+1S | 1025 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15922202 | 1161 | 270.3773 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 95191076 | 4757 | 114.168 | 4.757 | 4.1 | 4.1 | 3B+1S | 1026 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15923360 | 1158 | 243.4307 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 95195693 | 4617 | 110.808 | 4.617 | 3.5 | 3.5 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15924492 | 1132 | 250.8122 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 129 |  | 95200266 | 4573 | 109.752 | 4.573 | 3.1 | 3.1 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15925688 | 1196 | 247.5399 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 95204602 | 4336 | 104.064 | 4.336 | 2.7 | 2.7 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15926856 | 1168 | 269.3727 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 95209170 | 4568 | 109.632 | 4.568 | 2.3 | 2.3 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15928011 | 1155 | 252.8459 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 128 |  | 95213791 | 4621 | 110.904 | 4.621 | 2 | 2 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15929179 | 1168 | 252.7591 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -4 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 127 |  | 95218583 | 4792 | 115.008 | 4.792 | 1.6 | 1.6 | 3B+1S | 1014 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15930292 | 1113 | 232.2621 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -4 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | 134 |  | 95223297 | 4714 | 113.136 | 4.714 | 1.8 | 1.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15931380 | 1088 | 230.8019 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | 137 |  | 95227412 | 4115 | 98.76 | 4.115 | 2.6 | 2.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15932482 | 1102 | 267.8007 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 104969 | 2519.256 | 104.969 | [13 empty] | 27541 | 262.3727 | [7 empty] | 0 | 0 | 1.0467 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:45 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 21, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 22
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-22 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27558 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95227412 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15932482 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 72 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | 139 |  | 95231563 | 4151 | 99.624 | 4.151 | 3.9 | 3.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15933599 | 1117 | 269.0918 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 2 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 140 |  | 95235679 | 4116 | 98.784 | 4.116 | 5 | 5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15934703 | 1104 | 268.2216 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 4 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 142 |  | 95239716 | 4037 | 96.888 | 4.037 | 6.5 | 6.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15935789 | 1086 | 269.0116 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 145 |  | 95243849 | 4133 | 99.192 | 4.133 | 8 | 8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15936904 | 1115 | 269.7798 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 128 |  | 95248261 | 4412 | 105.888 | 4.412 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15938007 | 1103 | 250 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 13.1 | 139 |  | 95253086 | 4825 | 115.8 | 4.825 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15939182 | 1175 | 243.5233 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 132 |  | 95258766 | 5680 | 136.32 | 5.68 | 9.1 | 9.1 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15940450 | 1268 | 223.2394 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 130 |  | 95262808 | 4042 | 97.008 | 4.042 | 8.6 | 8.6 | 3B+1S | 0 | 1028 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15941498 | 1048 | 259.2776 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 131 |  | 95267386 | 4578 | 109.872 | 4.578 | 8 | 8 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15942654 | 1156 | 252.512 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 132 |  | 95271302 | 3916 | 93.984 | 3.916 | 7.2 | 7.2 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15943868 | 1214 | 310.0102 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 130 |  | 95275134 | 3832 | 91.968 | 3.832 | 6.4 | 6.4 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15945074 | 1206 | 314.7182 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 127 |  | 95278816 | 3682 | 88.368 | 3.682 | 6.2 | 6.2 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15946214 | 1140 | 309.6143 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 126 |  | 95283394 | 4578 | 109.872 | 4.578 | 5.4 | 5.4 | 3B+1S | 0 | 1046 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15947511 | 1297 | 283.3115 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 17.3 | 127 |  | 95286904 | 3510 | 84.24 | 3.51 | 4.9 | 4.9 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15948521 | 1010 | 287.7493 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 95291087 | 4183 | 100.392 | 4.183 | 4.4 | 4.4 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15949715 | 1194 | 285.4411 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 95295464 | 4377 | 105.048 | 4.377 | 3.9 | 3.9 | 3B+1S | 0 | 1025 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15950885 | 1170 | 267.3064 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 95300225 | 4761 | 114.264 | 4.761 | 3.4 | 3.4 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15952045 | 1160 | 245.7467 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 95305284 | 5059 | 121.416 | 5.059 | 3 | 3 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15953210 | 1165 | 229.2943 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 95310128 | 4844 | 116.256 | 4.844 | 2.6 | 2.6 | 3B+1S | 0 | 1025 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15954377 | 1167 | 240.9166 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 95315030 | 4902 | 117.648 | 4.902 | 2.2 | 2.2 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15955534 | 1157 | 236.0261 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 95319787 | 4757 | 114.168 | 4.757 | 1.8 | 1.8 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15956693 | 1159 | 243.641 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | 0 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 131 |  | 95325411 | 5624 | 134.976 | 5.624 | 1.4 | 1.4 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15957894 | 1201 | 213.5491 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 131 |  | 95330191 | 4780 | 114.72 | 4.78 | 1.6 | 1.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15958964 | 1070 | 223.8494 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 134 |  | 95334769 | 4578 | 109.872 | 4.578 | 2 | 2 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15960040 | 1076 | 235.0371 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 107357 | 2576.568 | 107.357 | [13 empty] | 27558 | 256.695 | [7 empty] | 0 | 0 | 1.0267 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:50 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 8:24 PM DUE TO FAULT
SP1 - STARTED @ 8:24 AM DUE TO FAULT SP2
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 22, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
MAINTENANCE TEAM LEAD BY BUNDA GERARDO ARRIVE @ 10:25PM FOR GRESING TO BP1/SP1/SP2

## MAY 23
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / REY PROVIDENCIA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-23 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27253 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95334769 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15960040 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 1 | 67 | 47.1831 | 75 | Automatic - Pressure Setting | 42.2535 | 43.662 | 47.8873 | 14 | A.ONG | 11.4 | 148 |  | 95339419 | 4650 | 111.6 | 4.65 | 3.4 | 3.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15961156 | 1116 | 240 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 2 | 70 | 49.2958 | 76 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 147 |  | 95343015 | 3596 | 86.304 | 3.596 | 5.1 | 5.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15962261 | 1105 | 307.2859 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 4 | 71 | 50 | 77 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 142 |  | 95346215 | 3200 | 76.8 | 3.2 | 6.7 | 6.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15963271 | 1010 | 315.625 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 70 | 49.2958 | 79 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 143 |  | 95351151 | 4936 | 118.464 | 4.936 | 8.3 | 8.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15964282 | 1011 | 204.8217 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 7 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 130 |  | 95356121 | 4970 | 119.28 | 4.97 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15965542 | 1260 | 253.5211 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 139 |  | 95360531 | 4410 | 105.84 | 4.41 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15966613 | 1071 | 242.8571 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.84 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 6 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 133 |  | 95365350 | 4819 | 115.656 | 4.819 | 9.1 | 9.1 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15967804 | 1191 | 247.1467 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 131 |  | 95370251 | 4901 | 117.624 | 4.901 | 8.5 | 8.5 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15969005 | 1201 | 245.052 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 129 |  | 95374577 | 4326 | 103.824 | 4.326 | 7.8 | 7.8 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15970197 | 1192 | 275.5432 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 95378355 | 3778 | 90.672 | 3.778 | 7.2 | 7.2 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15971387 | 1190 | 314.9815 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 95382075 | 3720 | 89.28 | 3.72 | 6.6 | 6.6 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15972582 | 1195 | 321.2366 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 129 |  | 95385712 | 3637 | 87.288 | 3.637 | 6.1 | 6.1 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15973746 | 1164 | 320.044 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 95389815 | 4103 | 98.472 | 4.103 | 5.5 | 5.5 | 3B+1S | 1027 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15974927 | 1181 | 287.8382 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 126 |  | 95394344 | 4529 | 108.696 | 4.529 | 4.9 | 4.9 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15976198 | 1271 | 280.6359 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 3 | 77 | 54.2254 | 71 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 126 |  | 95398326 | 3982 | 95.568 | 3.982 | 4.5 | 4.5 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15977102 | 904 | 227.0216 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 3 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 129 |  | 95402396 | 4070 | 97.68 | 4.07 | 4.2 | 4.2 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15978126 | 1024 | 251.5971 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 95407788 | 5392 | 129.408 | 5.392 | 3.6 | 3.6 | 3B+1S | 1026 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15979387 | 1261 | 189.911 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 95412286 | 4498 | 107.952 | 4.498 | 3.3 | 3.3 | 3B+1S | 1024 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15980504 | 1117 | 280.3468 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 95417234 | 4948 | 118.752 | 4.948 | 2.8 | 2.8 | 3B+1S | 1026 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 15981632 | 1128 | 227.9709 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 95422402 | 5168 | 124.032 | 5.168 | 2.4 | 2.4 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15982766 | 1134 | 219.4272 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 127 |  | 95427324 | 4922 | 118.128 | 4.922 | 2.1 | 2.1 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15983868 | 1102 | 223.8927 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | 0 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 128 |  | 95432792 | 5468 | 131.232 | 5.468 | 1.7 | 1.7 | 3B+1S | 1025 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15985104 | 1236 | 226.0424 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | DEF |  | 95437665 | 4873 | 116.952 | 4.873 | 2.1 | 2.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15986186 | 1082 | 222.0398 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 127 |  | 95441985 | 4320 | 103.68 | 4.32 | 2.7 | 2.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15987293 | 1107 | 256.25 | 0% | 0% | 0% | 100% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 107216 | 2573.184 | 107.216 | [13 empty] | 27253 | 254.1878 | [7 empty] | 0 | 0 | 1.0283 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:30 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 23, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
POWER INTERRUPTION AT 2:50PM
ALL PUMP STOPPED AT 2:50PM
GENSET STARTED AT 2:50PM
BP4 STARTED AT 2:52PM
BP2 STARTED AT 2:54PM
BP3 STARTED AT 2:56PM
SP1 STARTED AT 2:58PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 24
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY PROVIDENCIA / FIDEL RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[16 empty] | 10pm - 6am | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-24 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27634 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95441985 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 15987293 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 74 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 139 |  | 95446474 | 4489 | 107.736 | 4.489 | 3.7 | 3.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15988384 | 1091 | 243.0385 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | 137 |  | 95451006 | 4532 | 108.768 | 4.532 | 4.9 | 4.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15989485 | 1101 | 242.9391 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 72 | 50.7042 | 75 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 139 |  | 95455019 | 4013 | 96.312 | 4.013 | 6.2 | 6.2 | 3B | 0 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15990601 | 1116 | 278.0962 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 70 | 49.2958 | 76 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | DEF |  | 95459528 | 4509 | 108.216 | 4.509 | 8.1 | 8.1 | 3B | 0 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 15991715 | 1114 | 247.0614 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | DEF |  | 95463678 | 4150 | 99.6 | 4.15 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15992798 | 1083 | 260.9639 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 76 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | DEF |  | 95468460 | 4782 | 114.768 | 4.782 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15993936 | 1138 | 237.9757 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 7 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 132 |  | 95473750 | 5290 | 126.96 | 5.29 | 9.1 | 9.1 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15995120 | 1184 | 223.8185 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 130 |  | 95478630 | 4880 | 117.12 | 4.88 | 8.4 | 8.4 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15996320 | 1200 | 245.9016 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 130 |  | 95483758 | 5128 | 123.072 | 5.128 | 7.8 | 7.8 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15997507 | 1187 | 231.4743 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 131 |  | 95487859 | 4101 | 98.424 | 4.101 | 7.1 | 7.1 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15998675 | 1168 | 284.8086 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.11 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 95492128 | 4269 | 102.456 | 4.269 | 6.5 | 6.5 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 15999863 | 1188 | 278.2853 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 129 |  | 95496673 | 4545 | 109.08 | 4.545 | 5.9 | 5.9 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16001055 | 1192 | 262.2662 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 95501657 | 4984 | 119.616 | 4.984 | 5.3 | 5.3 | 3B+1S | 0 | 1028 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16002234 | 1179 | 236.557 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 130 |  | 95507438 | 5781 | 138.744 | 5.781 | 4.7 | 4.7 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16003532 | 1298 | 224.5286 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 128 |  | 95512244 | 4806 | 115.344 | 4.806 | 4.3 | 4.3 | 3B+1S | 0 | 1025 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 16004558 | 1026 | 213.4831 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 134 |  | 95517406 | 5162 | 123.888 | 5.162 | 3.7 | 3.7 | 3B+1S | 0 | 1026 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16005786 | 1228 | 237.8923 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 95522102 | 4696 | 112.704 | 4.696 | 3.3 | 3.3 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16006980 | 1194 | 261.4991 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 95526738 | 4636 | 111.264 | 4.636 | 3 | 3 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16008058 | 1078 | 257.5496 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.18 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 95531738 | 5000 | 120 | 5 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16009224 | 1166 | 233.2 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 95537676 | 5938 | 142.512 | 5.938 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16010400 | 1176 | 198.0465 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 129 |  | 95542918 | 5242 | 125.808 | 5.242 | 1.9 | 1.9 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16011554 | 1154 | 220.145 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 95548380 | 5462 | 131.088 | 5.462 | 1.6 | 1.6 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16012736 | 1182 | 216.4042 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 137 |  | 95553350 | 4970 | 119.28 | 4.97 | 1.8 | 1.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16013838 | 1102 | 221.7304 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 69 | 48.5915 | 66 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A ONG | 11.5 | DEF |  | 95558340 | 4990 | 119.76 | 4.99 | 2.7 | 2.7 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16014927 | 1089 | 218.2365 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 116355 | 2792.52 | 116.355 | [13 empty] | 27634 | 237.4973 | [7 empty] | 0 | 0 | 1.0467 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:30 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 24, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 25
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | PAUL G. LABIAN / JONEL LLAGUNO
[16 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-25 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27691 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95558340 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16014927 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 0 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | 142 |  | 95563113 | 4773 | 114.552 | 4.773 | 4.3 | 4.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16016048 | 1121 | 234.8628 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 2 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 147 |  | 95567255 | 4142 | 99.408 | 4.142 | 5.6 | 5.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16017141 | 1093 | 263.8822 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 4 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 145 |  | 95571418 | 4163 | 99.912 | 4.163 | 6.8 | 6.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16018217 | 1076 | 258.4675 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 72 | 50.7042 | 69 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | DEF |  | 95576348 | 4930 | 118.32 | 4.93 | 8.3 | 8.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16019346 | 1129 | 229.0061 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 95581044 | 4696 | 112.704 | 4.696 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16020460 | 1114 | 237.2232 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | DEF |  | 95586244 | 5200 | 124.8 | 5.2 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16021554 | 1094 | 210.3846 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.8 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 134 |  | 95591531 | 5287 | 126.888 | 5.287 | 9.5 | 9.5 | 3B+1S | 1025 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16022627 | 1073 | 202.9506 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 78 | 54.9296 | 75 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 131 |  | 95598031 | 6500 | 156 | 6.5 | 8.8 | 8.8 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16023896 | 1269 | 195.2308 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 95602538 | 4507 | 108.168 | 4.507 | 8.2 | 8.2 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16025091 | 1195 | 265.1431 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 95606391 | 3853 | 92.472 | 3.853 | 7.5 | 7.5 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16026310 | 1219 | 316.3768 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 95610059 | 3668 | 88.032 | 3.668 | 6.9 | 6.9 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16027507 | 1197 | 326.3359 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 129 |  | 95613640 | 3581 | 85.944 | 3.581 | 6.3 | 6.3 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16028640 | 1133 | 316.3921 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 123 |  | 95617408 | 3768 | 90.432 | 3.768 | 5.8 | 5.8 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16029810 | 1170 | 310.5096 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 95622479 | 5071 | 121.704 | 5.071 | 5.2 | 5.2 | 3B+1S | 1027 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16030972 | 1162 | 229.1461 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 0 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 95628566 | 6087 | 146.088 | 6.087 | 4.8 | 4.8 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16032154 | 1182 | 194.1843 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | -1 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 132 |  | 95634360 | 5794 | 139.056 | 5.794 | 4.3 | 4.3 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16033309 | 1155 | 199.3441 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 95640219 | 5859 | 140.616 | 5.859 | 3.7 | 3.7 | 3B+1S | 0 | 1027 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16034473 | 1164 | 197.1326 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 95646270 | 6051 | 145.224 | 6.051 | 3.3 | 3.3 | 3B+1S | 0 | 1026 | 1186 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16035657 | 1184 | 192.3649 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 95651931 | 5661 | 135.864 | 5.661 | 2.9 | 2.9 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16036788 | 1131 | 199.788 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 127 |  | 95657945 | 6014 | 144.336 | 6.014 | 2.5 | 2.5 | 3B+1S | 0 | 1025 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16037964 | 1176 | 195.5437 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 95663879 | 5934 | 142.416 | 5.934 | 2.1 | 2.1 | 3B+1S | 0 | 1025 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16039123 | 1159 | 195.3151 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | 129 |  | 95669972 | 6093 | 146.232 | 6.093 | 1.8 | 1.8 | 3B+1S | 0 | 1025 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16040318 | 1195 | 196.1267 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -1 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 138 |  | 95675938 | 5966 | 143.184 | 5.966 | 2 | 2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16041426 | 1108 | 185.7191 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 95682001 | 6063 | 145.512 | 6.063 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16042618 | 1192 | 196.6023 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 123661 | 2967.864 | 123.661 | [13 empty] | 27691 | 223.9267 | [7 empty] | 0 | 0 | 0.97 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
BP2 - STOPPED @ 2:30 AM DUE TO SHIFTING OPERATION
BP1 - STARTED @ 2:31 AM
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:50 AM WATER ELEVATION (9.5 M)
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 25, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 26
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE HERNANDEZ / JONEL LLAGUNO
[16 empty] | 10pm - 6am | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-26 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27631 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95682001 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16042618 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 2 | 69 | 48.5915 | 69 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 145 |  | 95686239 | 4238 | 101.712 | 4.238 | 4 | 4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16043606 | 988 | 233.1288 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 146 |  | 95691177 | 4938 | 118.512 | 4.938 | 5.3 | 5.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16044742 | 1136 | 230.0527 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 146 |  | 95696296 | 5119 | 122.856 | 5.119 | 6.9 | 6.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16045883 | 1141 | 222.8951 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | DEF |  | 95701014 | 4718 | 113.232 | 4.718 | 8.4 | 8.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16046994 | 1111 | 235.4811 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 82 | 57.7465 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | DEF |  | 95705720 | 4706 | 112.944 | 4.706 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16048077 | 1083 | 230.1317 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | DEF |  | 95710755 | 5035 | 120.84 | 5.035 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16049226 | 1149 | 228.2026 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 16.7 | 140 |  | 95716080 | 5325 | 127.8 | 5.325 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16050346 | 1120 | 210.3286 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 130 |  | 95721555 | 5475 | 131.4 | 5.475 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16051508 | 1162 | 212.2374 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 95726218 | 4663 | 111.912 | 4.663 | 8.4 | 8.4 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16052737 | 1229 | 263.5642 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 95729888 | 3670 | 88.08 | 3.67 | 7.8 | 7.8 | 3B+1S | 1028 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16053929 | 1192 | 324.7956 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.88 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 131 |  | 95733627 | 3739 | 89.736 | 3.739 | 7.2 | 7.2 | 3B+1S | 1027 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16055133 | 1204 | 322.0112 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 95737225 | 3598 | 86.352 | 3.598 | 6.6 | 6.6 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16056311 | 1178 | 327.4041 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 129 |  | 95741138 | 3913 | 93.912 | 3.913 | 6 | 6 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16057521 | 1210 | 309.2257 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 95746433 | 5295 | 127.08 | 5.295 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16058729 | 1208 | 228.1398 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 95751835 | 5402 | 129.648 | 5.402 | 5 | 5 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16059834 | 1105 | 204.5539 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 95757610 | 5775 | 138.6 | 5.775 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16060982 | 1148 | 198.7879 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 95763697 | 6087 | 146.088 | 6.087 | 4.1 | 4.1 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16062159 | 1177 | 188.5987 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 95769543 | 5846 | 140.304 | 5.846 | 3.7 | 3.7 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16063315 | 1156 | 201.3342 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | PAUL G. LABIAN / JONEL LLAGUNO
| 66:00 | 19:00 | 3 | 2.1127 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 95775368 | 5825 | 139.8 | 5.825 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16064509 | 1194 | 204.9785 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -5 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 128 |  | 95781047 | 5679 | 136.296 | 5.679 | 2.9 | 2.9 | 3B+1S | 1015 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16065649 | 1140 | 200.7396 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 95786957 | 5910 | 141.84 | 5.91 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16066844 | 1195 | 202.1997 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -3 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | 128 |  | 95792939 | 5982 | 143.568 | 5.982 | 2.3 | 2.3 | 3B+1S | 1025 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16068047 | 1203 | 201.1033 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 135 |  | 95798106 | 5167 | 124.008 | 5.167 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16069075 | 1028 | 198.9549 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 1 | 72 | 50.7042 | 75 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 137 |  | 95803735 | 5629 | 135.096 | 5.629 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16070249 | 1174 | 208.5628 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 121734 | 2921.616 | 121.734 | [13 empty] | 27631 | 226.9785 | [7 empty] | 0 | 0 | 0.99167 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:34 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 26, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 27
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | JONEL V. LLAGUNO / PAUL G. LABIAN
[16 empty] | 10pm - 6am | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-27 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27569 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95803735 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16070249 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 2 | 69 | 48.5915 | 69 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 140 |  | 95808415 | 4680 | 112.32 | 4.68 | 4.7 | 4.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16071448 | 1199 | 256.1966 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 68 | 47.8873 | 70 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.2 | 146 |  | 95813445 | 5030 | 120.72 | 5.03 | 6.3 | 6.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16072506 | 1058 | 210.338 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 4 | 69 | 48.5915 | 72 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.2 | 145 |  | 95818215 | 4770 | 114.48 | 4.77 | 7.8 | 7.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16073606 | 1100 | 230.608 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 81 | 57.0423 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A.ONG | 12.8 | 138 |  | 95822839 | 4624 | 110.976 | 4.624 | 9.4 | 9.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16074699 | 1093 | 236.3754 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 83 | 58.4507 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 126 |  | 95828108 | 5269 | 126.456 | 5.269 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16075839 | 1140 | 216.3598 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 138 |  | 95832530 | 4422 | 106.128 | 4.422 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16076907 | 1068 | 241.5197 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.8 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 141 |  | 95836962 | 4432 | 106.368 | 4.432 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16077992 | 1085 | 244.8105 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 8 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 132 |  | 95842660 | 5698 | 136.752 | 5.698 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16079154 | 1162 | 203.9312 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 8 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 132 |  | 95847561 | 4901 | 117.624 | 4.901 | 9 | 9 | 3B+1S | 0 | 1017 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16080320 | 1166 | 237.9106 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 133 |  | 95851244 | 3683 | 88.392 | 3.683 | 8.4 | 8.4 | 3B+1S | 0 | 1017 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16081527 | 1207 | 327.722 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 5 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 132 |  | 95854870 | 3626 | 87.024 | 3.626 | 7.8 | 7.8 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16082713 | 1186 | 327.0822 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 126 |  | 95858760 | 3890 | 93.36 | 3.89 | 7.3 | 7.3 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16083933 | 1220 | 313.6247 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 129 |  | 95863490 | 4730 | 113.52 | 4.73 | 6.7 | 6.7 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16085134 | 1201 | 253.9112 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 95868380 | 4890 | 117.36 | 4.89 | 6.1 | 6.1 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16086249 | 1115 | 228.0164 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.09 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 95874051 | 5671 | 136.104 | 5.671 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16087432 | 1183 | 208.6052 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 129 |  | 95879640 | 5589 | 134.136 | 5.589 | 5.2 | 5.2 | 3B+1S | 0 | 1015 | 1187 | 0 | 1188 | 1185 | N/A | N/A | N/A | 16088578 | 1146 | 205.0456 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 95885408 | 5768 | 138.432 | 5.768 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16089738 | 1160 | 198.6824 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 129 |  | 95891415 | 6007 | 144.168 | 6.007 | 4.3 | 4.3 | 3B+1S | 0 | 1016 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16090934 | 1196 | 193.108 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 130 |  | 95897185 | 5770 | 138.48 | 5.77 | 3.8 | 3.8 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16092074 | 1140 | 197.5737 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 95903103 | 5918 | 142.032 | 5.918 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16093241 | 1167 | 197.195 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | -4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 128 |  | 95909105 | 6002 | 144.048 | 6.002 | 3 | 3 | 3B+1S | 0 | 1015 | 1186 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16094432 | 1191 | 198.4339 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 134 |  | 95914928 | 5823 | 139.752 | 5.823 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16095588 | 1156 | 198.5231 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 129 |  | 95920808 | 5880 | 141.12 | 5.88 | 3 | 3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16096690 | 1102 | 187.415 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 0 | 70 | 49.2958 | 74 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 147 |  | 95925962 | 5154 | 123.696 | 5.154 | 4 | 4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16097818 | 1128 | 218.8591 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 122227 | 2933.448 | 122.227 | [13 empty] | 27569 | 225.5557 | [7 empty] | 0 | 0 | 0.99167 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:00 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 27, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 28
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | JONEL V. LLAGUNO / PAUL G. LABIAN
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-28 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27822 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 95925962 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16097818 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 1 | 70 | 49.2958 | 74 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 140 |  | 95930912 | 4950 | 118.8 | 4.95 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16098915 | 1097 | 221.6162 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 70 | 49.2958 | 76 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 139 |  | 95935851 | 4939 | 118.536 | 4.939 | 6.5 | 6.5 | 2B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16100012 | 1097 | 222.1097 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 72 | 50.7042 | 78 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 137 |  | 95940712 | 4861 | 116.664 | 4.861 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16101121 | 1109 | 228.1424 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 83 | 58.4507 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 95945547 | 4835 | 116.04 | 4.835 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16102290 | 1169 | 241.7787 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 9 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | 129 |  | 95949899 | 4352 | 104.448 | 4.352 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16103377 | 1087 | 249.7702 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 9 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | 132 |  | 95954914 | 5015 | 120.36 | 5.015 | 9.4 | 9.4 | 3B+1S | 1006 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16104514 | 1137 | 226.7198 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 134 |  | 95959519 | 4605 | 110.52 | 4.605 | 9.1 | 9.1 | 3B+1S | 1037 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16105654 | 1140 | 247.557 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 131 |  | 95965369 | 5850 | 140.4 | 5.85 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16106858 | 1204 | 205.812 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 130 |  | 95969920 | 4551 | 109.224 | 4.551 | 7.8 | 7.8 | 3B+1S | 1048 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16108099 | 1241 | 272.6873 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 95973529 | 3609 | 86.616 | 3.609 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16109278 | 1179 | 326.6833 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.19 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 95977221 | 3692 | 88.608 | 3.692 | 6.4 | 6.4 | 3B+1S | 1046 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16110490 | 1212 | 328.2774 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 95980866 | 3645 | 87.48 | 3.645 | 5.8 | 5.8 | 3B+1S | 1049 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16111689 | 1199 | 328.9438 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 95984960 | 4094 | 98.256 | 4.094 | 5.2 | 5.2 | 3B+1S | 1027 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16112871 | 1182 | 288.7152 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 1 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 129 |  | 95990414 | 5454 | 130.896 | 5.454 | 4.7 | 4.7 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16114054 | 1183 | 216.905 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 95996103 | 5689 | 136.536 | 5.689 | 4.3 | 4.3 | 3B+1S | 1025 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16115248 | 1194 | 209.8787 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | -3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 132 |  | 96001799 | 5696 | 136.704 | 5.696 | 3.7 | 3.7 | 3B+1S | 1025 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16116405 | 1157 | 203.125 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 96007630 | 5831 | 139.944 | 5.831 | 3.3 | 3.3 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16117570 | 1165 | 198.4222 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | -4 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 96013709 | 6079 | 145.896 | 6.079 | 2.9 | 2.9 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16118778 | 1208 | 191.6434 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | -3 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 96019455 | 5746 | 137.904 | 5.746 | 2.5 | 2.5 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16119926 | 1148 | 199.7912 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -3 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | DEF |  | 96025069 | 5614 | 134.736 | 5.614 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16121067 | 1141 | 203.2419 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | DEF |  | 96030852 | 5783 | 138.792 | 5.783 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16122243 | 1176 | 203.3547 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 129 |  | 96036372 | 5520 | 132.48 | 5.52 | 1.6 | 1.6 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16123439 | 1196 | 216.6667 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 132 |  | 96042057 | 5685 | 136.44 | 5.685 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16124485 | 1046 | 183.993 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 73 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 140 |  | 96047420 | 5363 | 128.712 | 5.363 | 2.4 | 2.4 |  | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16125640 | 1155 | 215.3645 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 121458 | 2914.992 | 121.458 | [13 empty] | 27822 | 229.0668 | [7 empty] | 0 | 0 | 1.0767 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:40 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 5:55 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 28, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 29
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | A.RAYALA II /J. LLAGUNO
| WATER NETWORK | [14 empty] | 2pm - 10pm | JONEL V. LLAGUNO / PAUL G. LABIAN
[16 empty] | 10pm - 6am | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-29 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27827 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96047420 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16125640 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 69 | 48.5915 | 72 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | DEF |  | 96052493 | 5073 | 121.752 | 5.073 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16126767 | 1127 | 222.1565 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 70 | 49.2958 | 73 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 96057372 | 4879 | 117.096 | 4.879 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16127915 | 1148 | 235.2941 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 71 | 50 | 74 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 96062048 | 4676 | 112.224 | 4.676 | 7.2 | 7.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16129044 | 1129 | 241.4457 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 70 | 49.2958 | 74 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | DEF |  | 96067196 | 5148 | 123.552 | 5.148 | 8.9 | 8.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16130183 | 1139 | 221.251 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 96072120 | 4924 | 118.176 | 4.924 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16131257 | 1074 | 218.1154 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | DEF |  | 96078151 | 6031 | 144.744 | 6.031 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16132265 | 1008 | 167.1365 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | DEF |  | 96084301 | 6150 | 147.6 | 6.15 | 8.8 | 8.8 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16133627 | 1362 | 221.4634 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 96090296 | 5995 | 143.88 | 5.995 | 8.1 | 8.1 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16134822 | 1195 | 199.3328 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 18.4 | 128 |  | 96094921 | 4625 | 111 | 4.625 | 7.4 | 7.4 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16136047 | 1225 | 264.8649 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 96098592 | 3671 | 88.104 | 3.671 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16137428 | 1381 | 376.1918 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 128 |  | 96102164 | 3572 | 85.728 | 3.572 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16138453 | 1025 | 286.9541 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 96105913 | 3749 | 89.976 | 3.749 | 5.4 | 5.4 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16139670 | 1217 | 324.6199 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 96110851 | 4938 | 118.512 | 4.938 | 4.8 | 4.8 | 3B+1S | 0 | 1036 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16140849 | 1179 | 238.7606 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 96116123 | 5272 | 126.528 | 5.272 | 4.3 | 4.3 | 3B+1S | 0 | 1028 | 1188 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16141990 | 1141 | 216.4264 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 129 |  | 96121753 | 5630 | 135.12 | 5.63 | 3.7 | 3.7 | 3B+1S | 0 | 1025 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16143167 | 1177 | 209.0586 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 133 |  | 96127564 | 5811 | 139.464 | 5.811 | 3.4 | 3.4 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16144340 | 1173 | 201.8585 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 96133487 | 5923 | 142.152 | 5.923 | 3 | 3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16145501 | 1161 | 198.0415 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 130 |  | 96139408 | 5921 | 142.104 | 5.921 | 2.6 | 2.6 | 3B+1S | 0 | 1016 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16146673 | 1172 | 196.0817 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 96145039 | 5631 | 135.144 | 5.631 | 2.3 | 2.3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16147825 | 1152 | 204.5818 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | -3 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 127 |  | 96150615 | 5576 | 133.824 | 5.576 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16148983 | 1158 | 207.6758 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | -3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | 127 |  | 96156632 | 6017 | 144.408 | 6.017 | 1.6 | 1.6 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16150160 | 1177 | 195.6124 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 4 | 2.8169 | -2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 12.6 | 132 |  | 96162427 | 5795 | 139.08 | 5.795 | 1.4 | 1.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16151303 | 1143 | 197.239 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | 136 |  | 96167676 | 5249 | 125.976 | 5.249 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16152353 | 1050 | 200.0381 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 96172982 | 5306 | 127.344 | 5.306 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16153467 | 1114 | 209.951 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 125562 | 3013.488 | 125.562 | [13 empty] | 27827 | 221.6196 | [7 empty] | 0 | 0 | 1.0117 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 29, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:11 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 30
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / JONEL LLAGUNO
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-30 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27778 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96172982 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16153467 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 4 | 2.8169 | 2 | 68 | 47.8873 | 70 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 145 |  | 96177862 | 4880 | 117.12 | 4.88 | 4 | 4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16154588 | 1121 | 229.7131 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 4 | 2.8169 | 4 | 69 | 48.5915 | 73 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.2 | 146 |  | 96182665 | 4803 | 115.272 | 4.803 | 5.8 | 5.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16155719 | 1131 | 235.4778 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 4 | 2.8169 | 5 | 69 | 48.5915 | 73 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.2 | 147 |  | 96187540 | 4875 | 117 | 4.875 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16156892 | 1173 | 240.6154 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 4 | 2.8169 | 6 | 69 | 48.5915 | 73 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 12.8 | 149 |  | 96192368 | 4828 | 115.872 | 4.828 | 9.2 | 9.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16158010 | 1118 | 231.5659 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 127 |  | 96197973 | 5605 | 134.52 | 5.605 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16159096 | 1086 | 193.7556 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 138 |  | 96202964 | 4991 | 119.784 | 4.991 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16160098 | 1002 | 200.7614 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 16.7 | 130 |  | 96209445 | 6481 | 155.544 | 6.481 | 9.1 | 9.1 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16161366 | 1268 | 195.6488 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 129 |  | 96215270 | 5825 | 139.8 | 5.825 | 8.4 | 8.4 | 3B+1S | 1028 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16162592 | 1226 | 210.4721 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 130 |  | 96220260 | 4990 | 119.76 | 4.99 | 7.8 | 7.8 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16163775 | 1183 | 237.0741 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 132 |  | 96224889 | 4629 | 111.096 | 4.629 | 7.2 | 7.2 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16164958 | 1183 | 255.5628 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 131 |  | 96227910 | 3021 | 72.504 | 3.021 | 6.6 | 6.6 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16166188 | 1230 | 407.15 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.3 | 128 |  | 96231585 | 3675 | 88.2 | 3.675 | 6 | 6 | 3B+1S | 1025 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16167394 | 1206 | 328.1633 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 128 |  | 96235549 | 3964 | 95.136 | 3.964 | 5.5 | 5.5 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16168533 | 1139 | 287.336 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 128 |  | 96240130 | 4581 | 109.944 | 4.581 | 4.9 | 4.9 | 3B+1S | 1025 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16169912 | 1379 | 301.026 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 132 |  | 96247043 | 6913 | 165.912 | 6.913 | 4.6 | 4.6 | 3B+1S | 1006 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16170915 | 1003 | 145.089 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 135 |  | 96252605 | 5562 | 133.488 | 5.562 | 4.2 | 4.2 | 3B+1S | 1005 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16172094 | 1179 | 211.9741 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 96258255 | 5650 | 135.6 | 5.65 | 3.8 | 3.8 | 3B+1S | 1007 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16173255 | 1161 | 208.6726 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 96264132 | 5877 | 141.048 | 5.877 | 3.4 | 3.4 | 3B+1S | 1007 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16174432 | 1177 | 197.5498 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 131 |  | 96269853 | 5721 | 137.304 | 5.721 | 3.1 | 3.1 | 3B+1S | 1005 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16175593 | 1161 | 202.9365 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | -4 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 96275630 | 5777 | 138.648 | 5.777 | 2.8 | 2.8 | 3B+1S | 1005 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16176771 | 1178 | 203.9121 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | -4 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 129 |  | 96281230 | 5600 | 134.4 | 5.6 | 2.6 | 2.6 | 3B+1S | 1006 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16177889 | 1118 | 199.6429 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 128 |  | 96287005 | 5775 | 138.6 | 5.775 | 2.3 | 2.3 | 3B+1S | 1004 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16179060 | 1171 | 202.7706 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 137 |  | 96292369 | 5364 | 128.736 | 5.364 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16180145 | 1085 | 202.2744 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 138 |  | 96297616 | 5247 | 125.928 | 5.247 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16181245 | 1100 | 209.6436 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 124634 | 2991.216 | 124.634 | [13 empty] | 27778 | 222.8766 | [7 empty] | 0 | 0 | 1.01 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:02 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 30, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## MAY 31
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | REY L. PROVIDENCIA / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-05-31 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27624 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96297616 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16181245 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 4 | 2.8169 | 3 | 69 | 48.5915 | 71 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 144 |  | 96302613 | 4997 | 119.928 | 4.997 | 4.4 | 4.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16182349 | 1104 | 220.9326 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 4 | 2.8169 | 4 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 143 |  | 96307964 | 5351 | 128.424 | 5.351 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16183466 | 1117 | 208.746 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 142 |  | 96312948 | 4984 | 119.616 | 4.984 | 7.2 | 7.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16184592 | 1126 | 225.923 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | DEF |  | 96317778 | 4830 | 115.92 | 4.83 | 8.8 | 8.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16185702 | 1110 | 229.8137 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | DEF |  | 96322556 | 4778 | 114.672 | 4.778 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16186811 | 1109 | 232.1055 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 138 |  | 96327402 | 4846 | 116.304 | 4.846 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16187913 | 1102 | 227.404 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 77 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 132 |  | 96332970 | 5568 | 133.632 | 5.568 | 9.5 | 9.5 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16189050 | 1137 | 204.2026 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 129 |  | 96338941 | 5971 | 143.304 | 5.971 | 8.9 | 8.9 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16190232 | 1182 | 197.9568 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 129 |  | 96344030 | 5089 | 122.136 | 5.089 | 8.3 | 8.3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16191391 | 1159 | 227.7461 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 96347757 | 3727 | 89.448 | 3.727 | 7.7 | 7.7 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16192595 | 1204 | 323.048 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.78 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | DEF |  | 96351460 | 3703 | 88.872 | 3.703 | 7.1 | 7.1 | 3B+1S | 0 | 1027 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16193794 | 1199 | 323.7915 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 96355225 | 3765 | 90.36 | 3.765 | 6.5 | 6.5 | 3B+1S | 0 | 1027 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16194987 | 1193 | 316.8659 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 96359576 | 4351 | 104.424 | 4.351 | 5.9 | 5.9 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16196173 | 1186 | 272.581 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 96364570 | 4994 | 119.856 | 4.994 | 5.4 | 5.4 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16197277 | 1104 | 221.0653 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 0 | 77 | 54.2254 | 71 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | DEF |  | 96370366 | 5796 | 139.104 | 5.796 | 5 | 5 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16198512 | 1235 | 213.078 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 96375930 | 5564 | 133.536 | 5.564 | 4.6 | 4.6 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16199704 | 1192 | 214.2344 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | -1 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 96381806 | 5876 | 141.024 | 5.876 | 4 | 4 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16200884 | 1180 | 202.8591 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | -1 | 75 | 52.8169 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 96387512 | 5706 | 136.944 | 5.706 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16202047 | 1163 | 206.7999 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 69 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 96393218 | 5706 | 136.944 | 5.706 | 3.2 | 3.2 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16203198 | 1151 | 201.7175 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 96398919 | 5701 | 136.824 | 5.701 | 2.8 | 2.8 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16204362 | 1164 | 204.1747 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -3 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 96404713 | 5794 | 139.056 | 5.794 | 2.4 | 2.4 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16205528 | 1166 | 201.2427 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | DEF |  | 96410214 | 5501 | 132.024 | 5.501 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16206679 | 1151 | 209.2347 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 4 | 2.8169 | -1 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | 140 |  | 96415505 | 5291 | 126.984 | 5.291 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16207758 | 1079 | 203.9312 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 96420935 | 5430 | 130.32 | 5.43 | 3 | 3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16208869 | 1111 | 204.6041 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 123319 | 2959.656 | 123.319 | [13 empty] | 27624 | 224.0044 | [7 empty] | 0 | 0 | 0.945 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:27 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( MAY 31, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:11 PM DUE TO PARAMETER CAPACITY OF 2.1 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)