## JUN 1
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-01 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27856 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96420935 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16208869 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | DEF |  | 96426068 | 5133 | 123.192 | 5.133 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16209972 | 1103 | 214.8841 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 96430958 | 4890 | 117.36 | 4.89 | 5.8 | 5.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16211091 | 1119 | 228.8344 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 96435826 | 4868 | 116.832 | 4.868 | 7.3 | 7.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16212207 | 1116 | 229.2523 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | DEF |  | 96440735 | 4909 | 117.816 | 4.909 | 8.9 | 8.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16213331 | 1124 | 228.9672 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 82 | 57.7465 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | DEF |  | 96445324 | 4589 | 110.136 | 4.589 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16214421 | 1090 | 237.5245 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | DEF |  | 96450324 | 5000 | 120 | 5 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16215561 | 1140 | 228 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 134 |  | 96455651 | 5327 | 127.848 | 5.327 | 9 | 9 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16216754 | 1193 | 223.9534 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 7 | 76 | 53.5211 | 79 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 131 |  | 96461828 | 6177 | 148.248 | 6.177 | 8.4 | 8.4 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16217955 | 1201 | 194.431 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 7 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 18.4 | 131 |  | 96466665 | 4837 | 116.088 | 4.837 | 7.7 | 7.7 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16219137 | 1182 | 244.3663 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 132 |  | 96470698 | 4033 | 96.792 | 4.033 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16220374 | 1237 | 306.7196 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 6 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | DEF |  | 96474715 | 4017 | 96.408 | 4.017 | 3.6 | 3.6 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16221574 | 1200 | 298.7304 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 96478715 | 4000 | 96 | 4 | 5.6 | 5.6 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16222795 | 1221 | 305.25 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 96483233 | 4518 | 108.432 | 4.518 | 5.1 | 5.1 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16223957 | 1162 | 257.1934 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 130 |  | 96489222 | 5989 | 143.736 | 5.989 | 4.6 | 4.6 | 3B+1S | 1026 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16225186 | 1229 | 205.2096 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 130 |  | 96494554 | 5332 | 127.968 | 5.332 | 4.1 | 4.1 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16226280 | 1094 | 205.1763 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 136 |  | 96500102 | 5548 | 133.152 | 5.548 | 3.6 | 3.6 | 3B+1S | 1025 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16227414 | 1134 | 204.398 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 131 |  | 96506108 | 6006 | 144.144 | 6.006 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16228634 | 1220 | 188.8112 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 131 |  | 96511782 | 5674 | 136.176 | 5.674 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16229792 | 1158 | 215.0159 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 131 |  | 96517726 | 5944 | 142.656 | 5.944 | 2.4 | 2.4 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16230998 | 1206 | 202.8937 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 130 |  | 96523466 | 5740 | 137.76 | 5.74 | 2.1 | 2.1 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16232144 | 1146 | 199.6516 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 128 |  | 96529182 | 5716 | 137.184 | 5.716 | 1.7 | 1.7 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16233310 | 1166 | 203.9888 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 129 |  | 96535200 | 6018 | 144.432 | 6.018 | 1.4 | 1.4 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16234503 | 1193 | 198.2386 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 4 | 2.8169 | 0 | 70 | 49.2958 | 67 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 142 |  | 96540952 | 5752 | 138.048 | 5.752 | 1.6 | 1.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16235644 | 1141 | 198.3658 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 4 | 2.8169 | 0 | 68 | 47.8873 | 66 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.5 | 146 |  | 96546080 | 5128 | 123.072 | 5.128 | 2.4 | 2.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16236725 | 1081 | 210.8034 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 125145 | 3003.48 | 125.145 | [13 empty] | 27856 | 222.5898 | [7 empty] | 0 | 0 | 1.0367 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:17 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 1, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 2
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | PAUL G. LABIAN / REY PROVIDENCIA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-02 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27720 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96546080 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16236725 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | -5 | 68 | 47.8873 | 65 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | DEF |  | 96550950 | 4870 | 116.88 | 4.87 | 4 | 4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16237828 | 1103 | 226.4887 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | -5 | 69 | 48.5915 | 66 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.2 | DEF |  | 96556055 | 5105 | 122.52 | 5.105 | 5.6 | 5.6 | 3B | 0 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16238955 | 1127 | 220.764 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 4 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 96560888 | 4833 | 115.992 | 4.833 | 7.3 | 7.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16240066 | 1111 | 229.8779 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | DEF |  | 96565727 | 4839 | 116.136 | 4.839 | 8.9 | 8.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16241197 | 1131 | 233.726 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 96570470 | 4743 | 113.832 | 4.743 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16242260 | 1063 | 224.1198 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | DEF |  | 96575115 | 4645 | 111.48 | 4.645 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16243415 | 1155 | 248.6545 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 133 |  | 96579878 | 4763 | 114.312 | 4.763 | 9 | 9 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16244522 | 1107 | 232.4165 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 131 |  | 96585887 | 6009 | 144.216 | 6.009 | 8.3 | 8.3 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16245750 | 1228 | 204.3601 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 18.4 | 131 |  | 96591002 | 5115 | 122.76 | 5.115 | 7.6 | 7.6 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16246964 | 1214 | 237.3412 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 6 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 133 |  | 96595020 | 4018 | 96.432 | 4.018 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16248170 | 1206 | 300.1493 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 131 |  | 96599172 | 4152 | 99.648 | 4.152 | 6.3 | 6.3 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16249354 | 1184 | 285.1638 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 129 |  | 96603320 | 4148 | 99.552 | 4.148 | 5.6 | 5.6 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16250571 | 1217 | 293.3944 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 130 |  | 96608326 | 5006 | 120.144 | 5.006 | 4.9 | 4.9 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16251796 | 1225 | 244.7064 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 129 |  | 96614088 | 5762 | 138.288 | 5.762 | 4.4 | 4.4 | 3B+1S | 0 | 1026 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16252914 | 1118 | 194.0299 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 132 |  | 96619836 | 5748 | 137.952 | 5.748 | 3.9 | 3.9 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16254064 | 1150 | 200.0696 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 128 |  | 96626348 | 6512 | 156.288 | 6.512 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16255308 | 1244 | 191.0319 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 130 |  | 96631866 | 5518 | 132.432 | 5.518 | 3 | 3 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16256436 | 1128 | 225.444 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 132 |  | 96637578 | 5712 | 137.088 | 5.712 | 2.6 | 2.6 | 3B+1S | 0 | 1016 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16257598 | 1162 | 197.479 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 96643498 | 5920 | 142.08 | 5.92 | 2.3 | 2.3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16258776 | 1178 | 198.9865 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 96649224 | 5726 | 137.424 | 5.726 | 1.9 | 1.9 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16259904 | 1128 | 196.9962 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 130 |  | 96654846 | 5622 | 134.928 | 5.622 | 1.6 | 1.6 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16261076 | 1172 | 208.4667 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 130 |  | 96660532 | 5686 | 136.464 | 5.686 | 1.4 | 1.4 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16262226 | 1150 | 202.2511 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 1 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 129 |  | 96665860 | 5328 | 127.872 | 5.328 | 1.7 | 1.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16263339 | 1113 | 208.8964 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | DEF |  | 96671348 | 5488 | 131.712 | 5.488 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16264445 | 1106 | 201.5306 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 125268 | 3006.432 | 125.268 | [13 empty] | 27720 | 221.2856 | [7 empty] | 0 | 0 | 1.0117 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:25 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 2, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 3
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-03 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27683 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96671348 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16264445 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 71 | 50 | 72 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 96676267 | 4919 | 118.056 | 4.919 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16265554 | 1109 | 225.4523 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 139 |  | 96681519 | 5252 | 126.048 | 5.252 | 4.5 | 4.5 | 3B | 0 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16266653 | 1099 | 209.2536 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 5 | 71 | 50 | 74 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 132 |  | 96686383 | 4864 | 116.736 | 4.864 | 5.9 | 5.9 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16267781 | 1128 | 231.9079 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 6 | 70 | 49.2958 | 74 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 141 |  | 96691260 | 4877 | 117.048 | 4.877 | 7.7 | 7.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16268899 | 1118 | 229.2393 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 130 |  | 96696164 | 4904 | 117.696 | 4.904 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16270017 | 1118 | 227.9772 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | 130 |  | 96701048 | 4884 | 117.216 | 4.884 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16271066 | 1049 | 214.783 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | 144 |  | 96706294 | 5246 | 125.904 | 5.246 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16272228 | 1162 | 221.5021 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | 132 |  | 96711738 | 5444 | 130.656 | 5.444 | 9 | 9 | 3B+1S | 1028 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16273412 | 1184 | 217.4871 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 132 |  | 96717410 | 5672 | 136.128 | 5.672 | 8.3 | 8.3 | 3B+1S | 1026 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16274650 | 1238 | 218.2652 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 96721840 | 4430 | 106.32 | 4.43 | 7.7 | 7.7 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16275868 | 1218 | 274.9436 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.14 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 132 |  | 96725926 | 4086 | 98.064 | 4.086 | 7.1 | 7.1 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16277022 | 1154 | 282.4278 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 131 |  | 96730002 | 4076 | 97.824 | 4.076 | 6.6 | 6.6 | 3B+1S | 1017 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16278184 | 1162 | 285.0834 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 19 | A ONG | 17.5 | 131 |  | 96735344 | 5342 | 128.208 | 5.342 | 6 | 6 | 3B+1S | 1017 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16279360 | 1176 | 220.1423 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 132 |  | 96740904 | 5560 | 133.44 | 5.56 | 5.5 | 5.5 | 3B+1S | 1016 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16280548 | 1188 | 213.6691 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 130 |  | 96747106 | 6202 | 148.848 | 6.202 | 5.1 | 5.1 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16281756 | 1208 | 194.7759 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 132 |  | 96752578 | 5472 | 131.328 | 5.472 | 4.6 | 4.6 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16282874 | 1118 | 204.3129 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 96758488 | 5910 | 141.84 | 5.91 | 4.2 | 4.2 | 3B+1S | 1016 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16284068 | 1194 | 189.1709 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 96764386 | 5898 | 141.552 | 5.898 | 3.7 | 3.7 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16285208 | 1140 | 202.4415 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 131 |  | 96770256 | 5870 | 140.88 | 5.87 | 3.3 | 3.3 | 3B+1S | 1015 | 0 | 1187 | 0 | 1188 | 1185 | N/A | N/A | N/A | 16286406 | 1198 | 204.0886 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 129 |  | 96776382 | 6126 | 147.024 | 6.126 | 2.9 | 2.9 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16287560 | 1154 | 188.3774 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 130 |  | 96782136 | 5754 | 138.096 | 5.754 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16288696 | 1136 | 197.4279 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 76 | 53.5211 | 71 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 96787882 | 5746 | 137.904 | 5.746 | 2.3 | 2.3 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16289890 | 1194 | 207.7967 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 2 | 68 | 47.8873 | 70 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 132 |  | 96793014 | 5132 | 123.168 | 5.132 | 3 | 3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16291004 | 1114 | 217.0694 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 2 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.5 | 144 |  | 96798042 | 5028 | 120.672 | 5.028 | 4.3 | 4.3 | 3B | 0 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16292128 | 1124 | 223.5481 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 126694 | 3040.656 | 126.694 | [13 empty] | 27683 | 218.5028 | [7 empty] | 0 | 0 | 1.0517 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:50 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 3, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 4
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / JONEL LLAGUNO
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-04 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27568 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96798042 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16292128 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 96803056 | 5014 | 120.336 | 5.014 | 5.5 | 5.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16293228 | 1100 | 219.3857 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 5 | 72 | 50.7042 | 73 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 96808014 | 4958 | 118.992 | 4.958 | 6.9 | 6.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16294355 | 1127 | 227.3094 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 7 | 71 | 50 | 75 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 145 |  | 96812739 | 4725 | 113.4 | 4.725 | 8.5 | 8.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16295478 | 1123 | 237.672 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A.ONG | 12.8 | 120 |  | 96817649 | 4910 | 117.84 | 4.91 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 0 | 1166 | 1185 | N/A | N/A | N/A | 16296549 | 1071 | 218.1263 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | 132 |  | 96822765 | 5116 | 122.784 | 5.116 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16297607 | 1058 | 206.8022 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 139 |  | 96828200 | 5435 | 130.44 | 5.435 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16298733 | 1126 | 207.1757 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.11 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 134 |  | 96833748 | 5548 | 133.152 | 5.548 | 9 | 9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16299921 | 1188 | 214.1312 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 131 |  | 96839170 | 5422 | 130.128 | 5.422 | 8.4 | 8.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16301113 | 1192 | 219.8451 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 129 |  | 96843805 | 4635 | 111.24 | 4.635 | 7.8 | 7.8 | 3B+1S | 0 | 1049 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16302310 | 1197 | 258.2524 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 132 |  | 96848298 | 4493 | 107.832 | 4.493 | 7.1 | 7.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16303514 | 1204 | 267.9724 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.2 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 129 |  | 96852742 | 4444 | 106.656 | 4.444 | 6.4 | 6.4 | 3B+1S | 0 | 1048 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16304710 | 1196 | 269.1269 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 127 |  | 96856958 | 4216 | 101.184 | 4.216 | 5.7 | 5.7 | 3B+1S | 0 | 1047 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16305899 | 1189 | 282.0209 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 129 |  | 96861259 | 4301 | 103.224 | 4.301 | 5.1 | 5.1 | 3B+1S | 0 | 1020 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16307082 | 1183 | 275.0523 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 134 |  | 96865834 | 4575 | 109.8 | 4.575 | 4.6 | 4.6 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16308330 | 1248 | 272.7869 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 73 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 130 |  | 96869935 | 4101 | 98.424 | 4.101 | 4.2 | 4.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16309428 | 1098 | 267.7396 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 96874256 | 4321 | 103.704 | 4.321 | 3.8 | 3.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16310544 | 1116 | 258.2735 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 131 |  | 96878744 | 4488 | 107.712 | 4.488 | 3.3 | 3.3 | 3B+1S | 0 | 1017 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16311750 | 1206 | 248.6631 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | 132 |  | 96883222 | 4478 | 107.472 | 4.478 | 2.9 | 2.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16312968 | 1218 | 269.3167 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.14 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 131 |  | 96887094 | 3872 | 92.928 | 3.872 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16314030 | 1062 | 274.2769 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 129 |  | 96891306 | 4212 | 101.088 | 4.212 | 2.2 | 2.2 | 3B+1S | 0 | 1014 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16315196 | 1166 | 276.8281 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 68 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | 132 |  | 96895312 | 4006 | 96.144 | 4.006 | 1.8 | 1.8 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16316334 | 1138 | 284.0739 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | DEF |  | 96899550 | 4238 | 101.712 | 4.238 | 1.5 | 1.5 | 3B+1S | 0 | 1003 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16317517 | 1183 | 279.1411 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 2 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A ONG | 11.9 | DEF |  | 96903594 | 4044 | 97.056 | 4.044 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16318618 | 1101 | 272.2552 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 138 |  | 96907480 | 3886 | 93.264 | 3.886 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16319696 | 1078 | 277.4061 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 109438 | 2626.512 | 109.438 | [13 empty] | 27568 | 251.9052 | [7 empty] | 0 | 0 | 1.11 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:30 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
BP3 STOPPED @ 4:00 AM DUE TO SHIFTING OF PUMP
- | BP2 STARTED @ 4:01 AM DUE TO SHIFTING OF PUMP
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 4, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 5
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY PROVIDENCIA / FIDEL RAMOS
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-05 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27542 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 96907480 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16319696 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 96911607 | 4127 | 99.048 | 4.127 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16320822 | 1126 | 272.8374 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 96915497 | 3890 | 93.36 | 3.89 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16321900 | 1078 | 277.1208 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 6 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 96919540 | 4043 | 97.032 | 4.043 | 6.8 | 6.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16323017 | 1117 | 276.28 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 12.8 | DEF |  | 96923510 | 3970 | 95.28 | 3.97 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16324170 | 1153 | 290.4282 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A.ONG | 13.1 | 128 |  | 96928218 | 4708 | 112.992 | 4.708 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16325233 | 1063 | 225.7859 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 4 | 2.8169 | 8 | 75 | 52.8169 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 13.1 | 140 |  | 96934014 | 5796 | 139.104 | 5.796 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16326344 | 1111 | 191.6839 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 132 |  | 96940230 | 6216 | 149.184 | 6.216 | 9 | 9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16327600 | 1256 | 202.0592 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 130 |  | 96944754 | 4524 | 108.576 | 4.524 | 8.5 | 8.5 | 3B+1S | 1017 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16328674 | 1074 | 237.4005 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 18.4 | 132 |  | 96949346 | 4592 | 110.208 | 4.592 | 7.9 | 7.9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16329834 | 1160 | 252.6132 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 131 |  | 96953948 | 4602 | 110.448 | 4.602 | 7.3 | 7.3 | 3B+1S | 1016 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16331046 | 1212 | 263.3638 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.06 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.7 | 132 |  | 96958264 | 4316 | 103.584 | 4.316 | 6.7 | 6.7 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16332222 | 1176 | 272.4745 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 128 |  | 96962644 | 4380 | 105.12 | 4.38 | 6.2 | 6.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16333414 | 1192 | 272.1461 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 19 | A ONG | 17.5 | 129 |  | 96966676 | 4032 | 96.768 | 4.032 | 5.7 | 5.7 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16334552 | 1138 | 282.2421 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 128 |  | 96970898 | 4222 | 101.328 | 4.222 | 5.2 | 5.2 | 3B+1S | 1018 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16335724 | 1172 | 277.5936 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | 128 |  | 96975178 | 4280 | 102.72 | 4.28 | 4.7 | 4.7 | 3B+1S | 1016 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16336888 | 1164 | 271.9626 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 96979696 | 4518 | 108.432 | 4.518 | 4.3 | 4.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16338070 | 1182 | 261.6202 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 96983928 | 4232 | 101.568 | 4.232 | 3.8 | 3.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16339220 | 1150 | 279.3006 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | 130 |  | 96988204 | 4276 | 102.624 | 4.276 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16340376 | 1156 | 268.9429 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 68 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 130 |  | 96992324 | 4120 | 98.88 | 4.12 | 3 | 3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16341518 | 1142 | 277.1845 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 68 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 129 |  | 96996794 | 4470 | 107.28 | 4.47 | 2.6 | 2.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16342716 | 1198 | 268.0089 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 68 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.1 | 128 |  | 97000888 | 4094 | 98.256 | 4.094 | 2.2 | 2.2 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16343848 | 1132 | 276.5022 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | 130 |  | 97005118 | 4230 | 101.52 | 4.23 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16345012 | 1164 | 275.1773 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 3 | 68 | 47.8873 | 70 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | 143 |  | 97009087 | 3969 | 95.256 | 3.969 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16346148 | 1136 | 286.2182 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 139 |  | 97013204 | 4117 | 98.808 | 4.117 | 3.3 | 3.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16347238 | 1090 | 264.7559 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 105724 | 2537.376 | 105.724 | [13 empty] | 27542 | 260.5085 | [7 empty] | 0 | 0 | 1.0517 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:13 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 5, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 6
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-06 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27627 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97013204 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16347238 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 4 | 68 | 47.8873 | 70 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | 144 |  | 97017516 | 4312 | 103.488 | 4.312 | 4.8 | 4.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16348348 | 1110 | 257.4212 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 5 | 71 | 50 | 71 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 144 |  | 97021687 | 4171 | 100.104 | 4.171 | 6.1 | 6.1 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16349458 | 1110 | 266.1232 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 6 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 143 |  | 97026003 | 4316 | 103.584 | 4.316 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16350574 | 1116 | 258.5728 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 8 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | 146 |  | 97030634 | 4631 | 111.144 | 4.631 | 9 | 9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16351682 | 1108 | 239.2572 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A.ONG | 13.1 | 129 |  | 97035554 | 4920 | 118.08 | 4.92 | 9.5 | 9.5 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16352767 | 1085 | 220.5285 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 128 |  | 97041254 | 5700 | 136.8 | 5.7 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16353887 | 1120 | 196.4912 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 132 |  | 97047374 | 6120 | 146.88 | 6.12 | 8.8 | 8.8 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16355083 | 1196 | 195.4248 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 132 |  | 97052880 | 5506 | 132.144 | 5.506 | 8.2 | 8.2 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16356288 | 1205 | 218.8522 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | 133 |  | 97057610 | 4730 | 113.52 | 4.73 | 7.6 | 7.6 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16357478 | 1190 | 251.5856 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | 131 |  | 97062233 | 4623 | 110.952 | 4.623 | 7 | 7 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16358673 | 1195 | 258.4902 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.11 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 4 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.7 | 131 |  | 97066694 | 4461 | 107.064 | 4.461 | 6.4 | 6.4 | 3B+1S | 0 | 1027 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16359872 | 1199 | 268.7738 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 130 |  | 97071180 | 4486 | 107.664 | 4.486 | 5.8 | 5.8 | 3B+1S | 0 | 1028 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16361060 | 1188 | 264.8239 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 131 |  | 97075679 | 4499 | 107.976 | 4.499 | 5.3 | 5.3 | 3B+1S | 0 | 1017 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16362231 | 1171 | 260.2801 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 131 |  | 97080368 | 4689 | 112.536 | 4.689 | 4.9 | 4.9 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16363404 | 1173 | 250.1599 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 132 |  | 97085642 | 5274 | 126.576 | 5.274 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16364572 | 1168 | 221.4638 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 131 |  | 97090593 | 4951 | 118.824 | 4.951 | 4.1 | 4.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16365727 | 1155 | 233.2862 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 1 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 131 |  | 97095558 | 4965 | 119.16 | 4.965 | 3.7 | 3.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16366887 | 1160 | 232.6284 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 131 |  | 97100496 | 4938 | 118.512 | 4.938 | 3.3 | 3.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16368054 | 1167 | 234.9129 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.13 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 97105275 | 4779 | 114.696 | 4.779 | 3 | 3 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16369216 | 1162 | 243.1471 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | 0 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | 129 |  | 97109577 | 4302 | 103.248 | 4.302 | 2.6 | 2.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16370377 | 1161 | 269.8745 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 129 |  | 97113892 | 4315 | 103.56 | 4.315 | 2.2 | 2.2 | 3B+1S | 0 | 1015 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16371537 | 1160 | 268.8297 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 131 |  | 97118235 | 4343 | 104.232 | 4.343 | 2 | 2 | 3B+1S | 0 | 1015 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16372660 | 1123 | 258.577 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 0 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 142 |  | 97122135 | 3900 | 93.6 | 3.9 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16373779 | 1119 | 286.9231 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 2 | 72 | 50.7042 | 74 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | 141 |  | 97125995 | 3860 | 92.64 | 3.86 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16374865 | 1086 | 281.3472 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 112791 | 2706.984 | 112.791 | [13 empty] | 27627 | 244.9398 | [7 empty] | 0 | 0 | 1.0533 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:10 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 6, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 7
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | PAUL G. LABIAN / REY PROVIDENCIA
| WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-07 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27696 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97125995 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16374865 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 145 |  | 97130244 | 4249 | 101.976 | 4.249 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16375989 | 1124 | 264.5328 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | 145 |  | 97134248 | 4004 | 96.096 | 4.004 | 5.9 | 5.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16377107 | 1118 | 279.2208 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 6 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 146 |  | 97138694 | 4446 | 106.704 | 4.446 | 7.2 | 7.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16378232 | 1125 | 253.0364 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 4 | 2.8169 | 7 | 68 | 47.8873 | 73 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 12.8 | 150 |  | 97142530 | 3836 | 92.064 | 3.836 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16379341 | 1109 | 289.1032 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A.ONG | 13.1 | 132 |  | 97147241 | 4711 | 113.064 | 4.711 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16380418 | 1077 | 228.6139 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 13.1 | 130 |  | 97152998 | 5757 | 138.168 | 5.757 | 9.4 | 9.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16381526 | 1108 | 192.4614 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 132 |  | 97158798 | 5800 | 139.2 | 5.8 | 8.9 | 8.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16382705 | 1179 | 203.2759 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 133 |  | 97164938 | 6140 | 147.36 | 6.14 | 8.3 | 8.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16383890 | 1185 | 192.9967 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 129 |  | 97170345 | 5407 | 129.768 | 5.407 | 7.7 | 7.7 | 3B+1S | 1047 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16385081 | 1191 | 220.27 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 132 |  | 97176225 | 5880 | 141.12 | 5.88 | 7.1 | 7.1 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16386312 | 1231 | 209.3537 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 132 |  | 97181490 | 5265 | 126.36 | 5.265 | 6.4 | 6.4 | 3B+1S | 1047 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16387521 | 1209 | 229.6296 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 134 |  | 97186433 | 4943 | 118.632 | 4.943 | 5.9 | 5.9 | 3B+1S | 1026 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16388713 | 1192 | 241.1491 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 132 |  | 97191091 | 4658 | 111.792 | 4.658 | 5.4 | 5.4 | 3B+1S | 1026 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16389874 | 1161 | 249.2486 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | 135 |  | 97195886 | 4795 | 115.08 | 4.795 | 4.9 | 4.9 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16391086 | 1212 | 252.7633 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | 135 |  | 97200904 | 5018 | 120.432 | 5.018 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16392218 | 1132 | 225.5879 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 135 |  | 97206424 | 5520 | 132.48 | 5.52 | 4.2 | 4.2 | 3B+1S | 1014 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16393398 | 1180 | 213.7681 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | 132 |  | 97211372 | 4948 | 118.752 | 4.948 | 3.8 | 3.8 | 3B+1S | 1016 | 0 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16394592 | 1194 | 238.4802 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 97216118 | 4746 | 113.904 | 4.746 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16395736 | 1144 | 251.5803 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | 129 |  | 97220964 | 4846 | 116.304 | 4.846 | 3.1 | 3.1 | 3B+1S | 1015 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16396862 | 1126 | 232.3566 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 130 |  | 97225736 | 4772 | 114.528 | 4.772 | 2.8 | 2.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16398072 | 1210 | 253.5624 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | 131 |  | 97230124 | 4388 | 105.312 | 4.388 | 2.4 | 2.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16399264 | 1192 | 271.65 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 130 |  | 97234747 | 4623 | 110.952 | 4.623 | 2.2 | 2.2 | 3b+1s | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16400366 | 1102 | 238.3734 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.19 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | 0 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | 144 |  | 97238715 | 3968 | 95.232 | 3.968 | 2.8 | 2.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16401450 | 1084 | 273.1855 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 2 | 73 | 51.4085 | 74 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | 140 |  | 97242745 | 4030 | 96.72 | 4.03 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16402561 | 1111 | 275.6824 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 116750 | 2802 | 116.75 | [13 empty] | 27696 | 237.2248 | [7 empty] | 0 | 0 | 1.0633 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:22 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 5:45 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 7, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 8
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | R.PROVIDENCIA/J. LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-08 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27572 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97242745 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16402561 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 3 | 73 | 51.4085 | 73 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.4 | 137 |  | 97247156 | 4411 | 105.864 | 4.411 | 5 | 5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16403667 | 1106 | 250.7368 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 4 | 73 | 51.4085 | 74 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 138 |  | 97251290 | 4134 | 99.216 | 4.134 | 6.4 | 6.4 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16404777 | 1110 | 268.5051 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 6 | 73 | 51.4085 | 75 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 142 |  | 97255794 | 4504 | 108.096 | 4.504 | 7.8 | 7.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16405874 | 1097 | 243.5613 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 8 | 70 | 49.2958 | 78 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | 149 |  | 97260168 | 4374 | 104.976 | 4.374 | 9.2 | 9.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16406983 | 1109 | 253.5437 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A.ONG | 13.1 | 130 |  | 97265305 | 5137 | 123.288 | 5.137 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16408051 | 1068 | 207.9034 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 13.1 | 138 |  | 97271068 | 5763 | 138.312 | 5.763 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16409184 | 1133 | 196.599 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 133 |  | 97276542 | 5474 | 131.376 | 5.474 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16410364 | 1180 | 215.5645 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | 131 |  | 97282187 | 5645 | 135.48 | 5.645 | 8.5 | 8.5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16411536 | 1172 | 207.6174 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 131 |  | 97287230 | 5043 | 121.032 | 5.043 | 7.8 | 7.8 | 3B+1S | 0 | 1057 | 1186 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16412741 | 1205 | 238.9451 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 130 |  | 97292066 | 4836 | 116.064 | 4.836 | 7.1 | 7.1 | 3B+1S | 0 | 1056 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16413941 | 1200 | 248.139 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.04 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 130 |  | 97296697 | 4631 | 111.144 | 4.631 | 6.5 | 6.5 | 3B+1S | 0 | 1037 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16415151 | 1210 | 261.2827 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | 131 |  | 97301182 | 4485 | 107.64 | 4.485 | 5.9 | 5.9 | 3B+1S | 0 | 1017 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16416324 | 1173 | 261.5385 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | 131 |  | 97305654 | 4472 | 107.328 | 4.472 | 5.4 | 5.4 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16417502 | 1178 | 263.4168 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | 126 |  | 97310170 | 4516 | 108.384 | 4.516 | 5 | 5 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16418680 | 1178 | 260.8503 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.92 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 133 |  | 97314502 | 4332 | 103.968 | 4.332 | 4.6 | 4.6 | 3B+1S | 0 | 1007 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16419838 | 1158 | 267.313 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 97319240 | 4738 | 113.712 | 4.738 | 4.3 | 4.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16421005 | 1167 | 246.3065 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 132 |  | 97324225 | 4985 | 119.64 | 4.985 | 3.8 | 3.8 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16422183 | 1178 | 234.1023 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 97328780 | 4555 | 109.32 | 4.555 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16423330 | 1147 | 258.6169 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 97333365 | 4585 | 110.04 | 4.585 | 3.2 | 3.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16424523 | 1193 | 260.1963 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 97337585 | 4220 | 101.28 | 4.22 | 2.8 | 2.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16425660 | 1137 | 269.4313 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 129 |  | 97342090 | 4505 | 108.12 | 4.505 | 2.5 | 2.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16426793 | 1133 | 251.4983 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 97346899 | 4809 | 115.416 | 4.809 | 2.4 | 2.4 | 3B+1S | 0 | 1003 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16427920 | 1127 | 234.3523 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.9 | DEF |  | 97351223 | 4324 | 103.776 | 4.324 | 3 | 3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16429008 | 1088 | 251.6189 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 97356275 | 5052 | 121.248 | 5.052 | 3.8 | 3.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16430133 | 1125 | 222.6841 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 113530 | 2724.72 | 113.53 | [13 empty] | 27572 | 242.8609 | [7 empty] | 0 | 0 | 0.99667 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:02 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 8, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. NOEL NERPIO OF SO. MAINTENANCE AND TEAM ARRIVE @ 3:00 PM TO CONDUCT WARM UP EXERCISE OF GENSETS 1 AND 2 WITHOUT LOAD FOR 5 MINUTES.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 9
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | REY PROVIDENCIA / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-09 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27233 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97356275 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16430133 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 4 | 2.8169 | 2 | 69 | 48.5915 | 70 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | 145 |  | 97360439 | 4164 | 99.936 | 4.164 | 5.2 | 5.2 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16431209 | 1076 | 258.4054 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 4 | 2.8169 | 3 | 71 | 50 | 73 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 144 |  | 97364953 | 4514 | 108.336 | 4.514 | 6.6 | 6.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16432307 | 1098 | 243.2432 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 143 |  | 97369897 | 4944 | 118.656 | 4.944 | 8 | 8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16433411 | 1104 | 223.301 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 97374505 | 4608 | 110.592 | 4.608 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16434519 | 1108 | 240.4514 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | DEF |  | 97379535 | 5030 | 120.72 | 5.03 | 9.5 | 9.5 | 3B | 0 | 0 | 1136 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16435607 | 1088 | 216.3022 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | DEF |  | 97384759 | 5224 | 125.376 | 5.224 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16436625 | 1018 | 194.8698 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.06 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 16.7 | 143 |  | 97390123 | 5364 | 128.736 | 5.364 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16437713 | 1088 | 202.8337 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 8 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 97395969 | 5846 | 140.304 | 5.846 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16438830 | 1117 | 191.0708 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | 133 |  | 97401899 | 5930 | 142.32 | 5.93 | 9 | 9 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16440019 | 1189 | 200.5059 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 97408237 | 6338 | 152.112 | 6.338 | 8.3 | 8.3 | 3B+1S | 1038 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16441229 | 1210 | 190.912 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.01 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 97414831 | 6594 | 158.256 | 6.594 | 7.7 | 7.7 | 3B+1S | 1036 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16442422 | 1193 | 180.9221 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 97420538 | 5707 | 136.968 | 5.707 | 7.2 | 7.2 | 3B+1S | 1017 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16443607 | 1185 | 207.6397 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 97425732 | 5194 | 124.656 | 5.194 | 6.6 | 6.6 | 3B+1S | 1016 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16444809 | 1202 | 231.4209 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | DEF |  | 97431990 | 6258 | 150.192 | 6.258 | 6.1 | 6.1 | 3B+1S | 1015 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16446192 | 1383 | 220.9971 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 97436500 | 4510 | 108.24 | 4.51 | 5.7 | 5.7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16447153 | 961 | 213.082 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 97441940 | 5440 | 130.56 | 5.44 | 5.3 | 5.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16448292 | 1139 | 209.375 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97447158 | 5218 | 125.232 | 5.218 | 5 | 5 | 3B+1S | 1005 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16449418 | 1126 | 218.2829 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97452550 | 5392 | 129.408 | 5.392 | 4.6 | 4.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16450617 | 1199 | 208.8279 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.77 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 97457880 | 5330 | 127.92 | 5.33 | 4.2 | 4.2 | 3B+1S | 1005 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16451774 | 1157 | 217.0732 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 97462570 | 4690 | 112.56 | 4.69 | 3.8 | 3.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16452915 | 1141 | 243.2836 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.1 | DEF |  | 97467670 | 5100 | 122.4 | 5.1 | 3.5 | 3.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16454060 | 1145 | 224.5098 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 97473382 | 5712 | 137.088 | 5.712 | 3.3 | 3.3 | 3B+1S | 1004 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16455193 | 1133 | 198.3543 | 100% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | DEF |  | 97478733 | 5351 | 128.424 | 5.351 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16456270 | 1077 | 201.2708 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | DEF |  | 97483895 | 5162 | 123.888 | 5.162 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16457366 | 1096 | 212.3208 | 0% | 0% | 100% | 100% | 0% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 127620 | 3062.88 | 127.62 | [13 empty] | 27233 | 213.3913 | [7 empty] | 0 | 0 | 0.95167 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:50 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 9, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 3.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 10
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-10 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26976 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97483895 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16457366 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 97488306 | 4411 | 105.864 | 4.411 | 5.8 | 5.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16458461 | 1095 | 248.243 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 97493114 | 4808 | 115.392 | 4.808 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16459542 | 1081 | 224.8336 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 97498050 | 4936 | 118.464 | 4.936 | 8.8 | 8.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16460651 | 1109 | 224.6759 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | DEF |  | 97502824 | 4774 | 114.576 | 4.774 | 9.5 | 9.5 | 3B | 0 | 0 | 1146 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16461731 | 1080 | 226.2254 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 97507483 | 4659 | 111.816 | 4.659 | 9.5 | 9.5 | 3B | 0 | 0 | 1126 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16462758 | 1027 | 220.4336 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | DEF |  | 97512545 | 5062 | 121.488 | 5.062 | 9.5 | 9.5 | 3B | 0 | 0 | 1096 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16463777 | 1019 | 201.3038 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.17 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | DEF |  | 97517543 | 4998 | 119.952 | 4.998 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16464785 | 1008 | 201.6807 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | DEF |  | 97522858 | 5315 | 127.56 | 5.315 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16465911 | 1126 | 211.8532 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | DEF |  | 97528431 | 5573 | 133.752 | 5.573 | 9.2 | 9.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16467070 | 1159 | 207.967 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 97534040 | 5609 | 134.616 | 5.609 | 8.8 | 8.8 | 3B+1S | 0 | 1017 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16468247 | 1177 | 209.8413 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 97540156 | 6116 | 146.784 | 6.116 | 8.2 | 8.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16469450 | 1203 | 196.6972 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 97545978 | 5822 | 139.728 | 5.822 | 7.6 | 7.6 | 3B+1S | 0 | 1017 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16470606 | 1156 | 198.5572 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 75 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 97551544 | 5566 | 133.584 | 5.566 | 7.1 | 7.1 | 3B+1S | 0 | 1017 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16471815 | 1209 | 217.2116 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 97557075 | 5531 | 132.744 | 5.531 | 6.5 | 6.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16473000 | 1185 | 214.247 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.77 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 97562690 | 5615 | 134.76 | 5.615 | 6.1 | 6.1 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16474153 | 1153 | 205.3428 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 4 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | DEF |  | 97568632 | 5942 | 142.608 | 5.942 | 5.7 | 5.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16475313 | 1160 | 195.2205 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 97574480 | 5848 | 140.352 | 5.848 | 5.3 | 5.3 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16476464 | 1151 | 198.3584 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 97580380 | 5900 | 141.6 | 5.9 | 4.9 | 4.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16477626 | 1162 | 195.0847 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 97586090 | 5710 | 137.04 | 5.71 | 4.6 | 4.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16478777 | 1151 | 201.5762 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 97591222 | 5132 | 123.168 | 5.132 | 4.2 | 4.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16479910 | 1133 | 220.7716 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 97596690 | 5468 | 131.232 | 5.468 | 3.7 | 3.7 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16481072 | 1162 | 212.5091 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 97602110 | 5420 | 130.08 | 5.42 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16482169 | 1097 | 202.3985 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | DEF |  | 97607067 | 4957 | 118.968 | 4.957 | 4.3 | 4.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16483286 | 1117 | 225.3379 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | DEF |  | 97612178 | 5111 | 122.664 | 5.111 | 5.1 | 5.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16484342 | 1056 | 206.6132 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 128283 | 3078.792 | 128.283 | [13 empty] | 26976 | 210.2851 | [7 empty] | 0 | 0 | 1.0067 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:45 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 8:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 10, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 3.5 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 11
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-11 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27090 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97612178 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16484342 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 97617225 | 5047 | 121.128 | 5.047 | 6.1 | 6.1 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16485427 | 1085 | 214.9792 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 6 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 97622125 | 4900 | 117.6 | 4.9 | 7.4 | 7.4 | 3B | 0 | 0 | 1188 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16486538 | 1111 | 226.7347 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 7 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 97626998 | 4873 | 116.952 | 4.873 | 8.8 | 8.8 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16487627 | 1089 | 223.4763 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | DEF |  | 97631630 | 4632 | 111.168 | 4.632 | 9.5 | 9.5 | 3B | 0 | 0 | 1145 | 1185 | 0 | 1185 | N/A | N/A | N/A | 16488689 | 1062 | 229.2746 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | DEF |  | 97635770 | 4140 | 99.36 | 4.14 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 1185 | 1156 | 0 | N/A | N/A | N/A | 16489715 | 1026 | 247.8261 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 13.1 | DEF |  | 97640494 | 4724 | 113.376 | 4.724 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16490817 | 1102 | 233.2769 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.09 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 97645246 | 4752 | 114.048 | 4.752 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16491908 | 1091 | 229.5875 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 9 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 97650547 | 5301 | 127.224 | 5.301 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 16493044 | 1136 | 214.2992 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | DEF |  | 97656089 | 5542 | 133.008 | 5.542 | 9 | 9 | 3B+1S | 1098 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16494215 | 1171 | 211.2956 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 97661182 | 5093 | 122.232 | 5.093 | 8.4 | 8.4 | 3B+1S | 1037 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16495442 | 1227 | 240.9189 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.01 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 6 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 97666872 | 5690 | 136.56 | 5.69 | 7.8 | 7.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16496682 | 1240 | 217.9262 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 97672070 | 5198 | 124.752 | 5.198 | 7.3 | 7.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16497799 | 1117 | 214.8903 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 97677767 | 5697 | 136.728 | 5.697 | 6.8 | 6.8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16498986 | 1187 | 208.3553 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | DEF |  | 97684140 | 6373 | 152.952 | 6.373 | 6.3 | 6.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16500240 | 1254 | 196.7676 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.84 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 59.8592 | 18 | A ONG | 16.9 | DEF |  | 97689770 | 5630 | 135.12 | 5.63 | 6.1 | 6.1 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16501335 | 1095 | 194.4938 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 4 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | DEF |  | 97695720 | 5950 | 142.8 | 5.95 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16502505 | 1170 | 196.6387 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | DEF |  | 97701440 | 5720 | 137.28 | 5.72 | 5.4 | 5.4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16503660 | 1155 | 204.5455 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97707347 | 5907 | 141.768 | 5.907 | 5 | 5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16504857 | 1197 | 195.5307 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.72 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 97713300 | 5953 | 142.872 | 5.953 | 4.6 | 4.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16506011 | 1154 | 193.8518 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 97718980 | 5680 | 136.32 | 5.68 | 4.2 | 4.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16507159 | 1148 | 202.1127 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 97724720 | 5740 | 137.76 | 5.74 | 3.9 | 3.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16508295 | 1136 | 197.9094 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 68 | 47.8873 | 73 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 12.6 | DEF |  | 97729712 | 4992 | 119.808 | 4.992 | 3.9 | 3.9 | 3B | 0 | 0 | 1016 | 1185 | 1147 | 0 | N/A | N/A | N/A | 16509230 | 935 | 187.2997 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.9 | DEF |  | 97735504 | 5792 | 139.008 | 5.792 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16510347 | 1117 | 192.8522 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 11.5 | DEF |  | 97740575 | 5071 | 121.704 | 5.071 | 5.4 | 5.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16511432 | 1085 | 213.9617 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 128397 | 3081.528 | 128.397 | [13 empty] | 27090 | 210.9862 | [7 empty] | 0 | 0 | 0.89833 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:20 AM WATER ELEVATION (9.5 M)
BP4 STOPPED @ 4:00 AM DUE TO SHIFTING OF PUMP
BP3 STARTED @ 4:01 AM DUE TO SHIFTING OF PUMP
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 11, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
Change operation advise as per SPM ENGR. JERICK AMBALOS of Control Center effective tonight June 11, 2018 target discharge pressure from 9:00 PM to 4:00 AM will be change from 83 psi to 68 psi only.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 12
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-12 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27305 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97740575 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16511432 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 5 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 97745450 | 4875 | 117 | 4.875 | 6.3 | 6.3 | 3B | 0 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16512524 | 1092 | 224 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 6 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 97750554 | 5104 | 122.496 | 5.104 | 7.7 | 7.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16513657 | 1133 | 221.9828 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 7 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 97755620 | 5066 | 121.584 | 5.066 | 9.1 | 9.1 | 3B | 0 | 0 | 1188 | 1185 | 1188 | 0 | N/A | N/A | N/A | 16514756 | 1099 | 216.9364 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | DEF |  | 97760547 | 4927 | 118.248 | 4.927 | 9.5 | 9.5 | 3B | 0 | 0 | 1147 | 1185 | 1147 | 0 | N/A | N/A | N/A | 16515824 | 1068 | 216.7648 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 97764826 | 4279 | 102.696 | 4.279 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16516890 | 1066 | 249.1236 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | DEF |  | 97768151 | 3325 | 79.8 | 3.325 | 9.5 | 9.5 | 3B | 0 | 0 | 1047 | 1185 | 1157 | 0 | N/A | N/A | N/A | 16517803 | 913 | 274.5865 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.96 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | DEF |  | 97772582 | 4431 | 106.344 | 4.431 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16518871 | 1068 | 241.0291 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | DEF |  | 97777737 | 5155 | 123.72 | 5.155 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16519993 | 1122 | 217.6528 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | DEF |  | 97782920 | 5183 | 124.392 | 5.183 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16521197 | 1204 | 232.2979 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 97788445 | 5525 | 132.6 | 5.525 | 8.5 | 8.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16522402 | 1205 | 218.0995 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.08 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 97794704 | 6259 | 150.216 | 6.259 | 7.9 | 7.9 | 3B+1S | 0 | 1056 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16523614 | 1212 | 193.6412 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 97800982 | 6278 | 150.672 | 6.278 | 7.2 | 7.2 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16524832 | 1218 | 194.0108 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 97806540 | 5558 | 133.392 | 5.558 | 6.5 | 6.5 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16526048 | 1216 | 218.7837 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 97812075 | 5535 | 132.84 | 5.535 | 6 | 6 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16527253 | 1205 | 217.7055 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | DEF |  | 97817765 | 5690 | 136.56 | 5.69 | 5.6 | 5.6 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16528415 | 1162 | 204.2179 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97823174 | 5409 | 129.816 | 5.409 | 5.2 | 5.2 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16529595 | 1180 | 218.1549 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97828930 | 5756 | 138.144 | 5.756 | 4.8 | 4.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16530780 | 1185 | 205.0035 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97834330 | 5400 | 129.6 | 5.4 | 4.4 | 4.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16531925 | 1145 | 219.4444 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 97839950 | 5620 | 134.88 | 5.62 | 3.9 | 3.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16533090 | 1165 | 207.2954 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 97844590 | 4640 | 111.36 | 4.64 | 3.5 | 3.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16534261 | 1171 | 252.3707 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 97849940 | 5350 | 128.4 | 5.35 | 3.2 | 3.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16535417 | 1156 | 216.0748 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 97855212 | 5272 | 126.528 | 5.272 | 2.9 | 2.9 | 3B+1S | 0 | 1006 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16536533 | 1116 | 211.6844 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 2 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | DEF |  | 97860768 | 5556 | 133.344 | 5.556 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16537644 | 1111 | 199.964 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 3 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.5 | DEF |  | 97865933 | 5165 | 123.96 | 5.165 | 4.2 | 4.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16538737 | 1093 | 211.6167 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 125358 | 3008.592 | 125.358 | [13 empty] | 27305 | 217.8162 | [7 empty] | 0 | 0 | 0.92833 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:05 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 12, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 13
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-13 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27542 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97865933 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16538737 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 5 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 97870790 | 4857 | 116.568 | 4.857 | 5.3 | 5.3 | 3B | 0 | 0 | 1186 | 1185 | 1188 | 0 | N/A | N/A | N/A | 16539859 | 1122 | 231.0068 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 6 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 97875851 | 5061 | 121.464 | 5.061 | 7 | 7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16540915 | 1056 | 208.6544 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 7 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 97880348 | 4497 | 107.928 | 4.497 | 8.2 | 8.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16542094 | 1179 | 262.1748 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A.ONG | 12.8 | DEF |  | 97885280 | 4932 | 118.368 | 4.932 | 9.5 | 9.5 | 3B | 0 | 0 | 1166 | 1185 | 1147 | 0 | N/A | N/A | N/A | 16543191 | 1097 | 222.425 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 9 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 97889487 | 4207 | 100.968 | 4.207 | 9.5 | 9.5 | 3B | 0 | 0 | 1170 | 1185 | 1147 | 0 | N/A | N/A | N/A | 16544215 | 1024 | 243.4039 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 9 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | DEF |  | 97894569 | 5082 | 121.968 | 5.082 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16545377 | 1162 | 228.6501 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.91 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 9 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 16.7 | DEF |  | 97899615 | 5046 | 121.104 | 5.046 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16546455 | 1078 | 213.6346 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | DEF |  | 97904547 | 4932 | 118.368 | 4.932 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16547645 | 1190 | 241.2814 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | DEF |  | 97910375 | 5828 | 139.872 | 5.828 | 8.5 | 8.5 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16548835 | 1190 | 204.1867 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.7 | DEF |  | 97916227 | 5852 | 140.448 | 5.852 | 7.9 | 7.9 | 3B+1S | 1047 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16550044 | 1209 | 206.596 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.02 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 97922482 | 6255 | 150.12 | 6.255 | 7.3 | 7.3 | 3B+1S | 1046 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16551249 | 1205 | 192.6459 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 97927735 | 5253 | 126.072 | 5.253 | 6.8 | 6.8 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16552449 | 1200 | 228.4409 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 97932827 | 5092 | 122.208 | 5.092 | 6.3 | 6.3 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16553620 | 1171 | 229.9686 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | DEF |  | 97938320 | 5493 | 131.832 | 5.493 | 5.8 | 5.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16554814 | 1194 | 217.3676 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.81 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 97943840 | 5520 | 132.48 | 5.52 | 5.5 | 5.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16555980 | 1166 | 211.2319 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 97949040 | 5200 | 124.8 | 5.2 | 5.2 | 5.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16557123 | 1143 | 219.8077 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97954765 | 5725 | 137.4 | 5.725 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16558294 | 1171 | 199.6507 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 97960540 | 5775 | 138.6 | 5.775 | 4.4 | 4.4 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16559493 | 1199 | 202.7706 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.7 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 97965920 | 5380 | 129.12 | 5.38 | 4 | 4 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16560614 | 1121 | 208.3643 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 97971206 | 5286 | 126.864 | 5.286 | 3.6 | 3.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16561770 | 1156 | 218.6909 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 97976570 | 5364 | 128.736 | 5.364 | 3.3 | 3.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16562924 | 1154 | 215.138 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 97981987 | 5417 | 130.008 | 5.417 | 3 | 3 | 3B+1S | 1004 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16564062 | 1138 | 210.0794 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 2 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | DEF |  | 97987340 | 5353 | 128.472 | 5.353 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16565170 | 1108 | 206.9867 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 137 |  | 97992615 | 5275 | 126.6 | 5.275 | 4.5 | 4.5 | 3B | 0 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16566279 | 1109 | 210.237 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 126682 | 3040.368 | 126.682 | [13 empty] | 27542 | 217.4105 | [7 empty] | 0 | 0 | 0.91167 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:45 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 13, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 14
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[16 empty] | 10pm - 6am | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-14 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27668 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 97992615 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16566279 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 7 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 141 |  | 97997595 | 4980 | 119.52 | 4.98 | 5.5 | 5.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16567382 | 1103 | 221.4859 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 7 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 140 |  | 98002517 | 4922 | 118.128 | 4.922 | 6.9 | 6.9 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16568492 | 1110 | 225.5181 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 8 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | 142 |  | 98007550 | 5033 | 120.792 | 5.033 | 8.3 | 8.3 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16569611 | 1119 | 222.3326 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 9 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | 119 |  | 98012630 | 5080 | 121.92 | 5.08 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1147 | 0 | N/A | N/A | N/A | 16570706 | 1095 | 215.5512 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 9 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | 128 |  | 98017305 | 4675 | 112.2 | 4.675 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1146 | 0 | N/A | N/A | N/A | 16571753 | 1047 | 223.9572 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 9 | 79 | 55.6338 | 76 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | 136 |  | 98021890 | 4585 | 110.04 | 4.585 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16572839 | 1086 | 236.8593 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.03 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 9 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | 135 |  | 98026764 | 4874 | 116.976 | 4.874 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16573975 | 1136 | 233.0735 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 8 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | 135 |  | 98031701 | 4937 | 118.488 | 4.937 | 9.1 | 9.1 | 3B+1S | 0 | 1017 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16575117 | 1142 | 231.3146 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 131 |  | 98037662 | 5961 | 143.064 | 5.961 | 8.5 | 8.5 | 3B+1S | 0 | 1067 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16576341 | 1224 | 205.3347 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 6 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 134 |  | 98044012 | 6350 | 152.4 | 6.35 | 7.9 | 7.9 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16577544 | 1203 | 189.4488 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.94 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 5 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 134 |  | 98050330 | 6318 | 151.632 | 6.318 | 7.3 | 7.3 | 3B+1S | 0 | 1038 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16578762 | 1218 | 192.7825 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 130 |  | 98056182 | 5852 | 140.448 | 5.852 | 6.7 | 6.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16579971 | 1209 | 206.596 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | 130 |  | 98061931 | 5749 | 137.976 | 5.749 | 6.2 | 6.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16581140 | 1169 | 203.3397 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | 131 |  | 98067749 | 5818 | 139.632 | 5.818 | 5.7 | 5.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16582350 | 1210 | 207.9752 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.07 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | 129 |  | 98073113 | 5364 | 128.736 | 5.364 | 5.3 | 5.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16583516 | 1166 | 217.3751 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | 131 |  | 98078510 | 5397 | 129.528 | 5.397 | 4.9 | 4.9 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16584699 | 1183 | 219.1958 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 128 |  | 98084174 | 5664 | 135.936 | 5.664 | 4.5 | 4.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16585883 | 1184 | 208.863 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | 130 |  | 98089941 | 5767 | 138.408 | 5.767 | 4 | 4 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16587053 | 1170 | 205.3061 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 128 |  | 98095701 | 5760 | 138.24 | 5.76 | 3.6 | 3.6 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16588229 | 1176 | 204.1667 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | 127 |  | 98101072 | 5371 | 128.904 | 5.371 | 3.2 | 3.2 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16589395 | 1166 | 217.0918 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | 127 |  | 98106758 | 5686 | 136.464 | 5.686 | 2.8 | 2.8 | 3B+1S | 0 | 1016 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16590558 | 1163 | 204.5375 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | 127 |  | 98112420 | 5662 | 135.888 | 5.662 | 2.5 | 2.5 | 3B+1S | 0 | 1015 | 1187 | 1185 | 1185 | 0 | N/A | N/A | N/A | 16591743 | 1185 | 209.29 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -1 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | 141 |  | 98117540 | 5120 | 122.88 | 5.12 | 3.1 | 3.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16592850 | 1107 | 216.2109 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | 139 |  | 98122545 | 5005 | 120.12 | 5.005 | 4.1 | 4.1 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16593947 | 1097 | 219.1808 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 129930 | 3118.32 | 129.93 | [13 empty] | 27668 | 212.9454 | [7 empty] | 0 | 0 | 0.99667 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:40 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 14, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 2.5 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 15
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | R.PROVIDENCIA/J. LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-15 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27569 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98122545 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16593947 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | 3 | 2.1127 | 4 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | 141 |  | 98127060 | 4515 | 108.36 | 4.515 | 5.6 | 5.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16595083 | 1136 | 251.6058 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | 3 | 2.1127 | 5 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | 140 |  | 98131900 | 4840 | 116.16 | 4.84 | 7 | 7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16596204 | 1121 | 231.6116 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | 3 | 2.1127 | 9 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | 142 |  | 98136650 | 4750 | 114 | 4.75 | 8.5 | 8.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16597325 | 1121 | 236 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | 119 |  | 98141135 | 4485 | 107.64 | 4.485 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1127 | 0 | N/A | N/A | N/A | 16598373 | 1048 | 233.6678 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | 3 | 2.1127 | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | 128 |  | 98145500 | 4365 | 104.76 | 4.365 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1116 | 0 | N/A | N/A | N/A | 16599430 | 1057 | 242.1535 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | 3 | 2.1127 | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | 139 |  | 98150336 | 4836 | 116.064 | 4.836 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16600551 | 1121 | 231.8031 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | 3 | 2.1127 | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | 143 |  | 98154790 | 4454 | 106.896 | 4.454 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16601592 | 1041 | 233.7225 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | 3 | 2.1127 | 8 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | 145 |  | 98159842 | 5052 | 121.248 | 5.052 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16602714 | 1122 | 222.0903 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | 3 | 2.1127 | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 18.4 | 132 |  | 98165166 | 5324 | 127.776 | 5.324 | 9.1 | 9.1 | 3B+1S | 1057 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16603912 | 1198 | 225.0188 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | 134 |  | 98170671 | 5505 | 132.12 | 5.505 | 8.4 | 8.4 | 3B+1S | 1058 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16605170 | 1258 | 228.5195 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.13 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | 135 |  | 98175211 | 4540 | 108.96 | 4.54 | 7.6 | 7.6 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16606379 | 1209 | 266.2996 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 5 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.3 | 132 |  | 98179778 | 4567 | 109.608 | 4.567 | 7.1 | 7.1 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16607579 | 1200 | 262.7545 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 19 | A ONG | 17.5 | DEF |  | 98184614 | 4836 | 116.064 | 4.836 | 6.5 | 6.5 | 3B+1S | 1017 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16608790 | 1211 | 250.4136 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 98189429 | 4815 | 115.56 | 4.815 | 6 | 6 | 3B+1S | 1005 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16610015 | 1225 | 254.4133 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | DEF |  | 98194160 | 4731 | 113.544 | 4.731 | 5.6 | 5.6 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16611162 | 1147 | 242.4435 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98199170 | 5010 | 120.24 | 5.01 | 5.1 | 5.1 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16612357 | 1195 | 238.523 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 98204020 | 4850 | 116.4 | 4.85 | 4.7 | 4.7 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16613505 | 1148 | 246.3918 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 98209711 | 5691 | 136.584 | 5.691 | 4.3 | 4.3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16614695 | 1190 | 201.722 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 98215303 | 5592 | 134.208 | 5.592 | 3.9 | 3.9 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16615846 | 1151 | 205.8298 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 98222099 | 6796 | 163.104 | 6.796 | 3.5 | 3.5 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16617016 | 1170 | 172.1601 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 98226580 | 4481 | 107.544 | 4.481 | 3.2 | 3.2 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16618166 | 1150 | 256.6391 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -2 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 12.6 | DEF |  | 98232112 | 5532 | 132.768 | 5.532 | 3 | 3 | 3B+1S | 1006 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16619324 | 1158 | 209.3275 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.9 | DEF |  | 98237225 | 5113 | 122.712 | 5.113 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16620411 | 1087 | 212.5953 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A ONG | 11.5 | DEF |  | 98242615 | 5390 | 129.36 | 5.39 | 4.6 | 4.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16621516 | 1105 | 205.0093 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 120070 | 2881.68 | 120.07 | [13 empty] | 27569 | 229.6077 | [7 empty] | 0 | 0 | 1.0183 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:40 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 15, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. NOEL NERPIO OF SO. MAINTENANCE AND TEAM ARRIVE @ 3:00 PM TO CONDUCT WARM UP EXERCISE OF GENSETS 1 AND 2 WITHOUT LOAD FOR 5 MINUTES.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 16
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | A.RAYALA II /J. LLAGUNO
| WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[16 empty] | 10pm - 6am | PAUL G. LABIAN / REY PROVIDENCIA
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-16 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27695 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98242615 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16621516 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 4 | 68 | 47.8873 | 66 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | DEF |  | 98247441 | 4826 | 115.824 | 4.826 | 5.7 | 5.7 | 3B | 0 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16622654 | 1138 | 235.8061 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 5 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 98252514 | 5073 | 121.752 | 5.073 | 7.5 | 7.5 | 3B | 0 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 16623725 | 1071 | 211.1177 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 6 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 98257386 | 4872 | 116.928 | 4.872 | 8.6 | 8.6 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16624886 | 1161 | 238.3005 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | DEF |  | 98261933 | 4547 | 109.128 | 4.547 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1147 | 0 | N/A | N/A | N/A | 16625971 | 1085 | 238.6189 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A.ONG | 13.1 | DEF |  | 98265991 | 4058 | 97.392 | 4.058 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1146 | 0 | N/A | N/A | N/A | 16626998 | 1027 | 253.0803 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | DEF |  | 98270701 | 4710 | 113.04 | 4.71 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16628119 | 1121 | 238.0042 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 55.6338 | 57.0423 | 58.4623 | 19 | A ONG | 16.7 | DEF |  | 98275619 | 4918 | 118.032 | 4.918 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16629228 | 1109 | 225.4982 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 17.3 | DEF |  | 98280621 | 5002 | 120.048 | 5.002 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16630351 | 1123 | 224.5102 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 18.4 | DEF |  | 98285881 | 5260 | 126.24 | 5.26 | 8.9 | 8.9 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16631578 | 1227 | 233.27 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 7 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 98291870 | 5989 | 143.736 | 5.989 | 8.2 | 8.2 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16632810 | 1232 | 205.7105 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 6 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.7 | DEF |  | 98296813 | 4943 | 118.632 | 4.943 | 7.5 | 7.5 | 3B+1S | 0 | 1057 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16634016 | 1206 | 243.9814 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 6 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 98301638 | 4825 | 115.8 | 4.825 | 6.8 | 6.8 | 3B+1S | 0 | 1047 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16635228 | 1212 | 251.1917 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 98306826 | 5188 | 124.512 | 5.188 | 6.1 | 6.1 | 3B+1S | 0 | 1037 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16636459 | 1231 | 237.2783 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 98311936 | 5110 | 122.64 | 5.11 | 5.5 | 5.5 | 3B+1S | 0 | 1036 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16637606 | 1147 | 224.4618 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 98316984 | 5048 | 121.152 | 5.048 | 5 | 5 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16638742 | 1136 | 225.0396 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98323058 | 6074 | 145.776 | 6.074 | 4.4 | 4.4 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16639998 | 1256 | 206.783 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98328646 | 5588 | 134.112 | 5.588 | 3.8 | 3.8 | 3B+1S | 0 | 1036 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16641178 | 1180 | 224.7674 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98334402 | 5756 | 138.144 | 5.756 | 3.3 | 3.3 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16642346 | 1168 | 205.0035 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98340302 | 5900 | 141.6 | 5.9 | 2.9 | 2.9 | 3B+1S | 0 | 1027 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 16643490 | 1144 | 193.8983 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98346014 | 5712 | 137.088 | 5.712 | 2.5 | 2.5 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16644660 | 1170 | 204.8319 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 98352048 | 6034 | 144.816 | 6.034 | 2.2 | 2.2 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16645878 | 1218 | 201.8561 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 77 | 54.2254 | 70 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 98357407 | 5359 | 128.616 | 5.359 | 1.9 | 1.9 | 3B+1S | 0 | 1026 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16647006 | 1128 | 210.487 | 0% | 100% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 98362750 | 5343 | 128.232 | 5.343 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16648089 | 1083 | 202.6951 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | DEF |  | 98368173 | 5423 | 130.152 | 5.423 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 16649211 | 1122 | 206.8966 | 0% | 0% | 100% | 100% | 100% | 0% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 125558 | 3013.392 | 125.558 | [13 empty] | 27695 | 220.5754 | [7 empty] | 0 | 0 | 1.01 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:25 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 16, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 17
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-17 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27605 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98368173 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16649211 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.4 | DEF |  | 98373143 | 4970 | 119.28 | 4.97 | 4.4 | 4.4 | 3B | 0 | 0 | 1186 | 1185 | 1186 | 0 | N/A | N/A | N/A | 16650301 | 1090 | 219.3159 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 98378051 | 4908 | 117.792 | 4.908 | 5.5 | 5.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16651412 | 1111 | 226.3651 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.75 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | DEF |  | 98382954 | 4903 | 117.672 | 4.903 | 6.7 | 6.7 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16652509 | 1097 | 223.7406 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 71 | 50 | 76 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 12.8 | DEF |  | 98387586 | 4632 | 111.168 | 4.632 | 8.2 | 8.2 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16653629 | 1120 | 241.7962 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 98392170 | 4584 | 110.016 | 4.584 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | 0 | N/A | N/A | N/A | 16654721 | 1092 | 238.2199 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 9 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 13.1 | DEF |  | 98396915 | 4745 | 113.88 | 4.745 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 1167 | 0 | N/A | N/A | N/A | 16655791 | 1070 | 225.5005 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.89 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 57.0423 | 58.4507 | 59.8707 | 19 | A ONG | 16.7 | DEF |  | 98401759 | 4844 | 116.256 | 4.844 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1167 | 0 | N/A | N/A | N/A | 16656890 | 1099 | 226.8786 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 17.3 | DEF |  | 98406719 | 4960 | 119.04 | 4.96 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16658010 | 1120 | 225.8065 | 0% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 18.4 | DEF |  | 98411857 | 5138 | 123.312 | 5.138 | 9 | 9 | 3B+1S | 1042 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16659211 | 1201 | 233.7485 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 98417008 | 5151 | 123.624 | 5.151 | 8.3 | 8.3 | 3B+1S | 1042 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16660426 | 1215 | 235.8765 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 0.99 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 98421522 | 4514 | 108.336 | 4.514 | 7.7 | 7.7 | 3B+1S | 1042 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16661633 | 1207 | 267.3903 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 98426114 | 4592 | 110.208 | 4.592 | 7 | 7 | 3B+1S | 1042 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16662891 | 1258 | 273.9547 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 77 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 98430468 | 4354 | 104.496 | 4.354 | 6.3 | 6.3 | 3B+1S | 1042 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16664055 | 1164 | 267.3404 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 98434874 | 4406 | 105.744 | 4.406 | 5.8 | 5.8 | 3B+1S | 1017 | 0 | 1187 | 1185 | 11186 | 0 | N/A | N/A | N/A | 16665172 | 1117 | 253.5179 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.9 | DEF |  | 98439614 | 4740 | 113.76 | 4.74 | 5.3 | 5.3 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 16666404 | 1232 | 259.9156 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 70 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98444486 | 4872 | 116.928 | 4.872 | 4.8 | 4.8 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16667592 | 1188 | 243.8424 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98449674 | 5188 | 124.512 | 5.188 | 4.4 | 4.4 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16668764 | 1172 | 228.99 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98454952 | 5278 | 126.672 | 5.278 | 3.9 | 3.9 | 3B+1S | 1016 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16669982 | 1218 | 222.0538 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98460644 | 5692 | 136.608 | 5.692 | 3.5 | 3.5 | 3B+1S | 1016 | 0 | 1188 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16671084 | 1102 | 193.6051 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98466802 | 6158 | 147.792 | 6.158 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16672304 | 1220 | 198.1163 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 98472222 | 5420 | 130.08 | 5.42 | 2.9 | 2.9 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16673416 | 1112 | 205.1661 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 77 | 54.2254 | 70 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 98477921 | 5699 | 136.776 | 5.699 | 2.6 | 2.6 | 3B+1S | 1016 | 0 | 1186 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16674583 | 1167 | 204.7728 | 100% | 0% | 100% | 100% | 100% | 0% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 2 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | DEF |  | 98483375 | 5454 | 130.896 | 5.454 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16675716 | 1133 | 207.7374 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | DEF |  | 98488375 | 5000 | 120 | 5 | 4.5 | 4.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16676816 | 1100 | 220 | 0% | 0% | 100% | 100% | 100% | 30% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 120202 | 2884.848 | 120.202 | [13 empty] | 27605 | 229.6551 | [7 empty] | 0 | 0 | 0.97167 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:38 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 8:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 17, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 18
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-18 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27658 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98488375 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16676816 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 4 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 98493343 | 4968 | 119.232 | 4.968 | 5.7 | 5.7 | 3B | 0 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 16677940 | 1124 | 226.248 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 6 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 98498276 | 4933 | 118.392 | 4.933 | 7.2 | 7.2 | 3B | 0 | 0 | 1187 | 1185 | 1188 | 0 | N/A | N/A | N/A | 16679065 | 1125 | 228.0559 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 7 | 73 | 51.4085 | 74 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 98503233 | 4957 | 118.968 | 4.957 | 8.7 | 8.7 | 3B | 0 | 0 | 1187 | 1185 | 1186 | 0 | N/A | N/A | N/A | 16680171 | 1106 | 223.1188 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 98507649 | 4416 | 105.984 | 4.416 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 1187 | 0 | N/A | N/A | N/A | 16681265 | 1094 | 247.7355 | 0% | 0% | 100% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 81 | 57.0423 | 80 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | DEF |  | 98511369 | 3720 | 89.28 | 3.72 | 9.5 | 9.5 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16682337 | 1072 | 288.172 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | DEF |  | 98516320 | 4951 | 118.824 | 4.951 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16683465 | 1128 | 227.8328 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.07 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | DEF |  | 98521100 | 4780 | 114.72 | 4.78 | 9 | 9 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16684659 | 1194 | 249.7908 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 98526808 | 5708 | 136.992 | 5.708 | 8.4 | 8.4 | 3B+1S | 0 | 1027 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16685846 | 1187 | 207.9537 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 98531717 | 4909 | 117.816 | 4.909 | 7.8 | 7.8 | 3B+1S | 0 | 1029 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16687045 | 1199 | 244.2453 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 98535824 | 4107 | 98.568 | 4.107 | 7.2 | 7.2 | 3B+1S | 0 | 1036 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16688254 | 1209 | 294.3755 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.96 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 98539612 | 3788 | 90.912 | 3.788 | 6.6 | 6.6 | 3B+1S | 0 | 1027 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16689471 | 1217 | 321.2777 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 98543310 | 3698 | 88.752 | 3.698 | 6 | 6 | 3B+1S | 0 | 1027 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16690651 | 1180 | 319.0914 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 98547578 | 4268 | 102.432 | 4.268 | 5.4 | 5.4 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16691827 | 1176 | 275.5389 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | DEF |  | 98552014 | 4436 | 106.464 | 4.436 | 5 | 5 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16692966 | 1139 | 256.7628 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 3 | 77 | 54.2254 | 72 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | DEF |  | 98557228 | 5214 | 125.136 | 5.214 | 4.6 | 4.6 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16694164 | 1198 | 229.766 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 3 | 78 | 54.9296 | 73 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 16.7 | DEF |  | 98563046 | 5818 | 139.632 | 5.818 | 4.3 | 4.3 | 3B+1S | 0 | 1014 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16695298 | 1134 | 194.9123 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 2 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98568654 | 5608 | 134.592 | 5.608 | 3.8 | 3.8 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16696454 | 1156 | 202.2111 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98574368 | 5714 | 137.136 | 5.714 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16697632 | 1178 | 202.3101 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.08 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 98580356 | 5988 | 143.712 | 5.988 | 3 | 3 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16698808 | 1176 | 196.3928 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 98585824 | 5468 | 131.232 | 5.468 | 2.7 | 2.7 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16699934 | 1126 | 205.9254 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 98591508 | 5684 | 136.416 | 5.684 | 2.4 | 2.4 | 3B+1S | 0 | 1014 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16701088 | 1154 | 203.026 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 70 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | DEF |  | 98597270 | 5762 | 138.288 | 5.762 | 2.1 | 2.1 | 3B+1S | 0 | 1005 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16702269 | 1181 | 204.9636 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 98602433 | 5163 | 123.912 | 5.163 | 2.6 | 2.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16703366 | 1097 | 212.4734 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | DEF |  | 98607790 | 5357 | 128.568 | 5.357 | 3.5 | 3.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16704474 | 1108 | 206.8322 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 119415 | 2865.96 | 119.415 | [13 empty] | 27658 | 231.6124 | [7 empty] | 0 | 0 | 1.015 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:20 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
BP2 STOPPED @ 4:00 AM DUE TO SHIFTING OF PUMP
- | BP4 STARTED @4:01 AM DUE TO SHIFTING OF PUMP
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 18, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
WATER SAMPLING / CENTRAL LAB. Res. Chl. 0.94 mg/l BY MR. RALPH RAMOS ARRIVE @ 1:02 PM
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2- STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 19
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-19 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27745 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98607790 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16704474 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 68 | 47.8873 | 69 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | DEF |  | 98612656 | 4866 | 116.784 | 4.866 | 4.9 | 4.9 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16705581 | 1107 | 227.4969 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 98617546 | 4890 | 117.36 | 4.89 | 6.4 | 6.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16706646 | 1065 | 217.7914 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 6 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 98622273 | 4727 | 113.448 | 4.727 | 8 | 8 | 3B | 0 | 0 | 1187 | 0 | 1188 | 1185 | N/A | N/A | N/A | 16707809 | 1163 | 246.0334 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | DEF |  | 98627356 | 5083 | 121.992 | 5.083 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16708923 | 1114 | 219.1619 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 98631958 | 4602 | 110.448 | 4.602 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16710004 | 1081 | 234.8979 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | DEF |  | 98637671 | 5713 | 137.112 | 5.713 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16711170 | 1166 | 204.0959 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 7 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | DEF |  | 98643107 | 5436 | 130.464 | 5.436 | 8.7 | 8.7 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16712379 | 1209 | 222.4062 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 98648932 | 5825 | 139.8 | 5.825 | 8 | 8 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16713581 | 1202 | 206.3519 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 98653213 | 4281 | 102.744 | 4.281 | 7.3 | 7.3 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16714803 | 1222 | 285.4473 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 98657083 | 3870 | 92.88 | 3.87 | 6.6 | 6.6 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16716022 | 1219 | 314.9871 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 98660708 | 3625 | 87 | 3.625 | 6 | 6 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16717194 | 1172 | 323.3103 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 98664510 | 3802 | 91.248 | 3.802 | 5.4 | 5.4 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16718394 | 1200 | 315.6234 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 98668429 | 3919 | 94.056 | 3.919 | 4.8 | 4.8 | 3B+1S | 1035 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16719574 | 1180 | 301.0972 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 98672802 | 4373 | 104.952 | 4.373 | 4.3 | 4.3 | 3B+1S | 1016 | 0 | 1186 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16720732 | 1158 | 264.8068 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 3 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | DEF |  | 98677346 | 4544 | 109.056 | 4.544 | 3.9 | 3.9 | 3B+1S | 1015 | 0 | 1186 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16721870 | 1138 | 250.4401 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 72 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98682604 | 5258 | 126.192 | 5.258 | 3.6 | 3.6 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16723020 | 1150 | 218.7143 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98688426 | 5822 | 139.728 | 5.822 | 3.2 | 3.2 | 3B+1S | 1015 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16724188 | 1168 | 197.5266 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 98694124 | 5698 | 136.752 | 5.698 | 2.9 | 2.9 | 3B+1S | 1017 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16725372 | 1184 | 204.9842 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 68 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 98699952 | 5828 | 139.872 | 5.828 | 2.6 | 2.6 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16726528 | 1156 | 198.3528 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 66 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 98705496 | 5544 | 133.056 | 5.544 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16727678 | 1150 | 207.4315 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 64 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 98711160 | 5664 | 135.936 | 5.664 | 1.9 | 1.9 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16728836 | 1158 | 204.4492 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 68 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | DEF |  | 98717007 | 5847 | 140.328 | 5.847 | 1.6 | 1.6 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16730012 | 1176 | 201.1288 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.1 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 1 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | DEF |  | 98722210 | 5203 | 124.872 | 5.203 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16731093 | 1081 | 207.7648 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | DEF |  | 98727512 | 5302 | 127.248 | 5.302 | 3.2 | 3.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16732219 | 1126 | 212.3727 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 119722 | 2873.328 | 119.722 | [13 empty] | 27745 | 231.7452 | [7 empty] | 0 | 0 | 1.02 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:43 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 19, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 20
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
[16 empty] | 10pm - 6am | PAUL G. LABIAN / JONEL LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-20 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26760 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98727512 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16732219 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 68 | 47.8873 | 67 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A.ONG | 11.4 | DEF |  | 98732268 | 4756 | 114.144 | 4.756 | 4.6 | 4.6 | 3B | 0 | 0 | 1188 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16733329 | 1110 | 233.3894 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 5 | 70 | 49.2958 | 69 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 98737178 | 4910 | 117.84 | 4.91 | 6 | 6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16734454 | 1125 | 229.1242 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.91 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 6 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | DEF |  | 98741758 | 4580 | 109.92 | 4.58 | 7.4 | 7.4 | 3B | 0 | 0 | 1187 | 0 | 1188 | 1185 | N/A | N/A | N/A | 16735558 | 1104 | 241.048 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 8 | 70 | 49.2958 | 72 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | DEF |  | 98746477 | 4719 | 113.256 | 4.719 | 9.1 | 9.1 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16736684 | 1126 | 238.6099 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 80 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A.ONG | 13.1 | DEF |  | 98750999 | 4522 | 108.528 | 4.522 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16737744 | 1060 | 234.4096 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | DEF |  | 98757036 | 6037 | 144.888 | 6.037 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16738926 | 1182 | 195.7926 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 7 | 78 | 54.9296 | 79 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 98762719 | 5683 | 136.392 | 5.683 | 8.9 | 8.9 | 3B+1S | 0 | 1027 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16740102 | 1176 | 206.933 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 98768426 | 5707 | 136.968 | 5.707 | 8.2 | 8.2 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16741304 | 1202 | 210.6185 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 98773184 | 4758 | 114.192 | 4.758 | 7.6 | 7.6 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16742480 | 1176 | 247.1627 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 98777017 | 3833 | 91.992 | 3.833 | 6.8 | 6.8 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16743229 | 749 | 195.4083 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | DEF |  | 98780849 | 3832 | 91.968 | 3.832 | 6.1 | 6.1 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16743979 | 750 | 195.7203 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 98784563 | 3714 | 89.136 | 3.714 | 5.5 | 5.5 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16745175 | 1196 | 322.0248 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 98788422 | 3859 | 92.616 | 3.859 | 4.9 | 4.9 | 3B+1S | 0 | 1046 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16746390 | 1215 | 314.8484 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | DEF |  | 98792527 | 4105 | 98.52 | 4.105 | 4.3 | 4.3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16747542 | 1152 | 280.6334 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.12 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 98796904 | 4377 | 105.048 | 4.377 | 3.9 | 3.9 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16748672 | 1130 | 258.1677 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98801860 | 4956 | 118.944 | 4.956 | 3.5 | 3.5 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16749839 | 1167 | 235.4722 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98807068 | 5208 | 124.992 | 5.208 | 3.3 | 3.3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16751007 | 1168 | 224.0783 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 2 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98812810 | 5742 | 137.808 | 5.742 | 3 | 3 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16752160 | 1153 | 203.4134 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.97 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98818806 | 5996 | 143.904 | 5.996 | 2.7 | 2.7 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16753327 | 1167 | 194.6298 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98824637 | 5831 | 139.944 | 5.831 | 2.4 | 2.4 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16754481 | 1154 | 197.9077 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 98830776 | 6139 | 147.336 | 6.139 | 2.1 | 2.1 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16755642 | 1161 | 189.1187 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 1 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 98836593 | 5817 | 139.608 | 5.817 | 1.9 | 1.9 | 3B+1S | 0 | 1015 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16756763 | 1121 | 192.711 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 1 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | DEF |  | 98842033 | 5440 | 130.56 | 5.44 | 2.5 | 2.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16757882 | 1119 | 205.6985 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 98846952 | 4919 | 118.056 | 4.919 | 3.4 | 3.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16758979 | 1097 | 223.0128 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 119440 | 2866.56 | 119.44 | [13 empty] | 26760 | 224.0455 | [7 empty] | 0 | 0 | 0.99667 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:05 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
MAINTENACE TEAM LEAD BY BUNDA GERARDO ARRIVE @ 8:05AM FOR GENSET WARM UP WITH LOAD 400 LITTERS
NOG @ 9:00AM
GENSET 2 FTO @ 9:54AM
RNOM @ 9:55AM
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 20, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2- STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 21
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
[16 empty] | 10pm - 6am | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-21 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27658 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98846952 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16758979 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 70 | 49.2958 | 71 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 98851908 | 4956 | 118.944 | 4.956 | 5 | 5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16760118 | 1139 | 229.8224 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A.ONG | 11.2 | DEF |  | 98856358 | 4450 | 106.8 | 4.45 | 6.5 | 6.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16761224 | 1106 | 248.5393 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 7 | 72 | 50.7042 | 76 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 98861049 | 4691 | 112.584 | 4.691 | 8.1 | 8.1 | 3B | 0 | 0 | 1188 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16762342 | 1118 | 238.3287 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 8 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 98865730 | 4681 | 112.344 | 4.681 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16763446 | 1104 | 235.847 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 98870203 | 4473 | 107.352 | 4.473 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16764502 | 1056 | 236.0832 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | DEF |  | 98876078 | 5875 | 141 | 5.875 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16765704 | 1202 | 204.5957 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 16.7 | DEF |  | 98881930 | 5852 | 140.448 | 5.852 | 8.9 | 8.9 | 3B+1S | 1027 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16766872 | 1168 | 199.5899 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 98887694 | 5764 | 138.336 | 5.764 | 8.2 | 8.2 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16768059 | 1187 | 205.9334 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 98892387 | 4693 | 112.632 | 4.693 | 7.5 | 7.5 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16769280 | 1221 | 260.1747 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 98896540 | 4153 | 99.672 | 4.153 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16770470 | 1190 | 286.5399 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 98900481 | 3941 | 94.584 | 3.941 | 6.2 | 6.2 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16771690 | 1220 | 309.5661 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 98904159 | 3678 | 88.272 | 3.678 | 5.6 | 5.6 | 3B+1S | 1047 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16772847 | 1157 | 314.5731 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 76 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 98908111 | 3952 | 94.848 | 3.952 | 5 | 5 | 3B+1S | 1039 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16774037 | 1190 | 301.1134 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | DEF |  | 98912408 | 4297 | 103.128 | 4.297 | 4.6 | 4.6 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16775175 | 1138 | 264.8359 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 98917218 | 4810 | 115.44 | 4.81 | 4.2 | 4.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16776340 | 1165 | 242.2037 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 2 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 98922149 | 4931 | 118.344 | 4.931 | 3.8 | 3.8 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16777504 | 1164 | 236.0576 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98927341 | 5192 | 124.608 | 5.192 | 3.4 | 3.4 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16778671 | 1167 | 224.1911 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 98932837 | 5496 | 131.904 | 5.496 | 3.1 | 3.1 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16779841 | 1170 | 212.3362 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.01 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98938399 | 5562 | 133.488 | 5.562 | 2.8 | 2.8 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16780986 | 1145 | 205.8612 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 98944133 | 5734 | 137.616 | 5.734 | 2.5 | 2.5 | 3B+1S | 1015 | 0 | 1187 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16782149 | 1163 | 202.8253 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 98950024 | 5891 | 141.384 | 5.891 | 2.2 | 2.2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16783302 | 1153 | 195.7223 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 98955786 | 5762 | 138.288 | 5.762 | 2 | 2 | 3B+1S | 1015 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16784416 | 1114 | 193.3356 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 98960813 | 5027 | 120.648 | 5.027 | 2.6 | 2.6 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16785506 | 1090 | 216.8291 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 98966319 | 5506 | 132.144 | 5.506 | 3.6 | 3.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16786637 | 1131 | 205.4123 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 119367 | 2864.808 | 119.367 | [13 empty] | 27658 | 231.7056 | [7 empty] | 0 | 0 | 1.0017 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:40 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 21, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 9:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL

## JUN 22
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
[16 empty] | 10pm - 6am | R.PROVIDENCIA/J. LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-22 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27464 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 98966319 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16786637 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.4 | DEF |  | 98971206 | 4887 | 117.288 | 4.887 | 4.6 | 4.6 | 3B | 0 | 0 | 1186 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16787723 | 1086 | 222.2222 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 5 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 98976059 | 4853 | 116.472 | 4.853 | 6.1 | 6.1 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16788837 | 1114 | 229.5487 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 6 | 73 | 51.4085 | 75 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 98980692 | 4633 | 111.192 | 4.633 | 7.6 | 7.6 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16789969 | 1132 | 244.3341 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 8 | 72 | 50.7042 | 74 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 12.8 | DEF |  | 98985506 | 4814 | 115.536 | 4.814 | 9.1 | 9.1 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16791065 | 1096 | 227.6693 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 98989740 | 4234 | 101.616 | 4.234 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16792128 | 1063 | 251.0628 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | DEF |  | 98995221 | 5481 | 131.544 | 5.481 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16793315 | 1187 | 216.5663 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 80 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 16.7 | DEF |  | 99001016 | 5795 | 139.08 | 5.795 | 8.9 | 8.9 | 3B+1S | 0 | 1037 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16794486 | 1171 | 202.0708 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 99006170 | 5154 | 123.696 | 5.154 | 8.2 | 8.2 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16795670 | 1184 | 229.7245 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 79 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 99009965 | 3795 | 91.08 | 3.795 | 7.6 | 7.6 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16796781 | 1111 | 292.7536 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 78 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.7 | DEF |  | 99013655 | 3690 | 88.56 | 3.69 | 6.9 | 6.9 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16798082 | 1301 | 352.5745 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99017468 | 3813 | 91.512 | 3.813 | 6.2 | 6.2 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16799283 | 1201 | 314.9751 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 99021372 | 3904 | 93.696 | 3.904 | 5.6 | 5.6 | 3B+1S | 0 | 1047 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16800498 | 1215 | 311.2193 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 77 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 99025067 | 3695 | 88.68 | 3.695 | 5 | 5 | 3B+1S | 0 | 1037 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16801649 | 1151 | 311.502 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 74 | 52.1127 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 17.3 | DEF |  | 99029315 | 4248 | 101.952 | 4.248 | 4.4 | 4.4 | 3B+1S | 0 | 1028 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16802822 | 1173 | 276.1299 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 74 | 52.1127 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | DEF |  | 99034147 | 4832 | 115.968 | 4.832 | 3.8 | 3.8 | 3B+1S | 0 | 1018 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16803991 | 1169 | 241.9288 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99039061 | 4914 | 117.936 | 4.914 | 3.4 | 3.4 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16805132 | 1141 | 232.1937 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99044035 | 4974 | 119.376 | 4.974 | 3 | 3 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16806291 | 1159 | 229.3928 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99049331 | 5296 | 127.104 | 5.296 | 2.6 | 2.6 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16807482 | 1191 | 218.8444 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 74 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99054741 | 5410 | 129.84 | 5.41 | 2.3 | 2.3 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16808619 | 1137 | 210.1664 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99059681 | 4940 | 118.56 | 4.94 | 2 | 2 | 3B+1S | 0 | 1016 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16809701 | 1082 | 219.0283 | 0% | 100% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 1 | 71 | 50 | 73 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.1 | DEF |  | 99065586 | 5905 | 141.72 | 5.905 | 1.8 | 1.8 | 3B | 0 | 0 | 1178 | 0 | 1178 | 1185 | N/A | N/A | N/A | 16810900 | 1199 | 203.0483 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | DEF |  | 99070820 | 5234 | 125.616 | 5.234 | 1.8 | 1.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16811958 | 1058 | 202.1399 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.96 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 2 | 68 | 47.8873 | 67 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | DEF |  | 99076010 | 5190 | 124.56 | 5.19 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16813005 | 1047 | 201.7341 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | DEF |  | 99080232 | 4222 | 101.328 | 4.222 | 4.4 | 4.4 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16814101 | 1096 | 259.5926 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 113913 | 2733.912 | 113.913 | [13 empty] | 27464 | 241.0963 | [7 empty] | 0 | 0 | 0.99333 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 3:01 AM TO 5:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:03 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 22, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2- STOPPED @ 8:35 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 23
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | FIDEL RAMOS / JONEL LLAGUNO
[16 empty] | 10pm - 6am | REY PROVIDENCIA / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-23 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26875 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99080232 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16814101 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 99084746 | 4514 | 108.336 | 4.514 | 6.2 | 6.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16815297 | 1196 | 264.9535 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 69 | 48.5915 | 69 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.2 | DEF |  | 99089193 | 4447 | 106.728 | 4.447 | 7.8 | 7.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16816448 | 1151 | 258.8262 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 1.04 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 99093539 | 4346 | 104.304 | 4.346 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16817578 | 1130 | 260.0092 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 70 | 49.2958 | 70 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 12.8 | DEF |  | 99097175 | 3636 | 87.264 | 3.636 | 9.5 | 9.5 | 2B | 0 | 0 | 0 | 0 | 1036 | 1185 | N/A | N/A | N/A | 16818235 | 657 | 180.6931 | 0% | 0% | 0% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 99100876 | 3701 | 88.824 | 3.701 | 9.5 | 9.5 | 3B | 0 | 0 | 1137 | 0 | 1147 | 1185 | N/A | N/A | N/A | 16819148 | 913 | 246.6901 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 80 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | DEF |  | 99104629 | 3753 | 90.072 | 3.753 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16820148 | 1000 | 266.4535 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 16.7 | DEF |  | 99109572 | 4943 | 118.632 | 4.943 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16821328 | 1180 | 238.7214 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 8 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 99114218 | 4646 | 111.504 | 4.646 | 9.1 | 9.1 | 3B+1S | 1017 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16822478 | 1150 | 247.5248 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 99118905 | 4687 | 112.488 | 4.687 | 8.4 | 8.4 | 3B+1S | 1099 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16823709 | 1231 | 262.6413 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99122814 | 3909 | 93.816 | 3.909 | 7.6 | 7.6 | 3B+1S | 1098 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16824919 | 1210 | 309.5421 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.97 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | DEF |  | 99126634 | 3820 | 91.68 | 3.82 | 6.8 | 6.8 | 3B+1S | 1068 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16826139 | 1220 | 319.3717 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 4 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.3 | DEF |  | 99130379 | 3745 | 89.88 | 3.745 | 5.9 | 5.9 | 3B+1S | 1118 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16827351 | 1212 | 323.6315 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 3 | 68 | 47.8873 | 66 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 19 | A ONG | 17.5 | DEF |  | 99133770 | 3391 | 81.384 | 3.391 | 5.1 | 5.1 | 3B+1S | 1048 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16828529 | 1178 | 347.3902 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 2 | 68 | 47.8873 | 64 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 17.3 | DEF |  | 99137756 | 3986 | 95.664 | 3.986 | 4.2 | 4.2 | 3B+1S | 1045 | 0 | 1186 | 0 | 1186 | 1185 | N/A | N/A | N/A | 16829698 | 1169 | 293.2765 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 1 | 68 | 47.8873 | 65 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.9 | DEF |  | 99141674 | 3918 | 94.032 | 3.918 | 3.3 | 3.3 | 3B+1S | 1016 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16830833 | 1135 | 289.6886 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 2 | 71 | 50 | 68 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.7 | DEF |  | 99145571 | 3897 | 93.528 | 3.897 | 2.8 | 2.8 | 3B+1S | 1017 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16831982 | 1149 | 294.8422 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 1 | 72 | 50.7042 | 68 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 18 | A ONG | 16.7 | DEF |  | 99150295 | 4724 | 113.376 | 4.724 | 2.4 | 2.4 | 3B+1S | 1005 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16833143 | 1161 | 243.2261 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 0 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.7 | DEF |  | 99155887 | 5592 | 134.208 | 5.592 | 2.1 | 2.1 | 3B+1S | 1006 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16834304 | 1161 | 207.618 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | -2 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 18 | A ONG | 16.6 | DEF |  | 99161596 | 5709 | 137.016 | 5.709 | 1.8 | 1.8 | 3B+1S | 1006 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16835441 | 1137 | 199.1592 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -3 | 75 | 52.8169 | 71 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 99167325 | 5729 | 137.496 | 5.729 | 1.5 | 1.5 | 3B+1S | 1006 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16836629 | 1188 | 207.366 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 99172785 | 5460 | 131.04 | 5.46 | 1.4 | 1.4 | 3B | 1105 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16837717 | 1088 | 199.2674 | 100% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | DEF |  | 99177681 | 4896 | 117.504 | 4.896 | 1.5 | 1.5 | 3B | 0 | 0 | 1148 | 0 | 1147 | 1185 | N/A | N/A | N/A | 16838770 | 1053 | 215.0735 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 99183015 | 5334 | 128.016 | 5.334 | 2.2 | 2.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16839872 | 1102 | 206.5992 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 99187808 | 4793 | 115.032 | 4.793 | 3.2 | 3.2 | 3B | 0 | 0 | 1167 | 0 | 1167 | 1185 | N/A | N/A | N/A | 16840976 | 1104 | 230.3359 | 0% | 0% | 100% | 0% | 100% | 100% | 30% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 107576 | 2581.824 | 107.576 | [13 empty] | 26875 | 249.8234 | [7 empty] | 0 | 0 | 1.0117 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
XCV2 - CLOSED @ 2:51 AM WATER ELEVATION (9.5 M)
BP1 STOPPED @ 3:00 AM TO MEET THE TARGET DISCHARGE 70 PSI.
TARGET DISCHARGE PRESSURE SET TO 70 PSI @ 3:00 AM TO 4:00 AM AS PER SCHEDULE
BP1 STARTED @ 4:00 AM TO MEET THE TARGET DISCHARGE 83 PSI.
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 5:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 23, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 8:25 PM DUE TO PARAMETER CAPACITY OF 1.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)
ENGR. ADRIAN ECHON AND SOUTH MAINTENANCE TEAM ARRIVE @ 11:10 PM TO CONDUCT REGREASING OF DRIVE COUPLING OF BP2 AND SP1&SP2.

## JUN 24
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | JONEL V. LLAGUNO / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-24 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27197 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99187808 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16840976 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | DEF |  | 99192495 | 4687 | 112.488 | 4.687 | 4.7 | 4.7 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16842091 | 1115 | 237.892 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 3 | 73 | 51.4085 | 72 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 99197530 | 5035 | 120.84 | 5.035 | 6.2 | 6.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16843229 | 1138 | 226.0179 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A.ONG | 11.2 | DEF |  | 99201585 | 4055 | 97.32 | 4.055 | 7.8 | 7.8 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16844354 | 1125 | 277.4353 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 99206216 | 4631 | 111.144 | 4.631 | 9.2 | 9.2 | 3B | 0 | 0 | 1187 | 0 | 1187 | 1185 | N/A | N/A | N/A | 16845525 | 1171 | 252.8612 | 0% | 0% | 100% | 0% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A.ONG | 13.1 | DEF |  | 99210012 | 3796 | 91.104 | 3.796 | 9.5 | 9.5 | 3B | 0 | 0 | 1117 | 0 | 1117 | 1185 | N/A | N/A | N/A | 16846527 | 1002 | 263.9621 | 0% | 0% | 100% | 0% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 56.338 | 57.7465 | 59.1665 | 19 | A ONG | 13.1 | DEF |  | 99214729 | 4717 | 113.208 | 4.717 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16847549 | 1022 | 216.6631 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 99218861 | 4132 | 99.168 | 4.132 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16848657 | 1108 | 268.151 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 17.3 | DEF |  | 99223481 | 4620 | 110.88 | 4.62 | 9.1 | 9.1 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16849784 | 1127 | 243.9394 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 99227735 | 4254 | 102.096 | 4.254 | 8.5 | 8.5 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16850960 | 1176 | 276.4457 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99232369 | 4634 | 111.216 | 4.634 | 7.8 | 7.8 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16852193 | 1233 | 266.0768 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.92 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | DEF |  | 99236703 | 4334 | 104.016 | 4.334 | 7 | 7 | 3B+1S | 0 | 1048 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16853386 | 1193 | 275.2653 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 4 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 53.5327 | 19 | A ONG | 17.3 | DEF |  | 99241117 | 4414 | 105.936 | 4.414 | 6.3 | 6.3 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16854590 | 1204 | 272.7685 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 3 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 19 | A ONG | 17.5 | DEF |  | 99245521 | 4404 | 105.696 | 4.404 | 5.6 | 5.6 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16855762 | 1172 | 266.1217 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 17.3 | DEF |  | 99249970 | 4449 | 106.776 | 4.449 | 5.2 | 5.2 | 3B+1S | 0 | 1046 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16856978 | 1216 | 273.3198 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | DEF |  | 99254460 | 4490 | 107.76 | 4.49 | 4.5 | 4.5 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16858140 | 1162 | 258.7973 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99258985 | 4525 | 108.6 | 4.525 | 4 | 4 | 3B+1S | 0 | 1047 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16859346 | 1206 | 266.5193 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | -2 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99263670 | 4685 | 112.44 | 4.685 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16860478 | 1132 | 257.4173 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99268295 | 4625 | 111 | 4.625 | 3.2 | 3.2 | 3B+1S | 0 | 1006 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16861638 | 1160 | 244.7568 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.94 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99273345 | 5050 | 121.2 | 5.05 | 2.9 | 2.9 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16862768 | 1130 | 223.7624 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -5 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99278315 | 4970 | 119.28 | 4.97 | 2.6 | 2.6 | 3B+1S | 0 | 1006 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16863888 | 1120 | 225.3521 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -5 | 71 | 50 | 68 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 18 | A ONG | 16.1 | DEF |  | 99283880 | 5565 | 133.56 | 5.565 | 2.4 | 2.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16865008 | 1120 | 201.2579 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 14 | A ONG | 12.6 | DEF |  | 99289172 | 5292 | 127.008 | 5.292 | 2.8 | 2.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16866137 | 1129 | 213.3409 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 68 | 47.8873 | 65 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 11.9 | DEF |  | 99293915 | 4743 | 113.832 | 4.743 | 3.2 | 3.2 | 3B | 0 | 0 | 0 | 1185 | 1056 | 1185 | N/A | N/A | N/A | 16867189 | 1052 | 221.8005 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 71 | 50 | 68 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.5 | DEF |  | 99297810 | 3895 | 93.48 | 3.895 | 4.3 | 4.3 | 3B | 0 | 0 | 0 | 1185 | 1045 | 1185 | N/A | N/A | N/A | 16868173 | 984 | 252.6316 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 110002 | 2640.048 | 110.002 | [13 empty] | 27197 | 247.241 | [7 empty] | 0 | 0 | 0.96333 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 72 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 6:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:11 AM WATER ELEVATION (9.5 M)
BP1 STOPPED @ 6:00 AM DUE TO SHIFTING OF PUMP
- | BP2 STARTED @6:01 AM DUE TO SHIFTING OF PUMP
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 24, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 8:30 PM DUE TO PARAMETER CAPACITY OF 2.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 9:01 PM (30%)
ENGR. ADRIAN ECHON AND SOUTH MAINTENANCE TEAM ARRIVE @ 10:54 PM TO CONDUCT REGREASING AND DRIVE COUPLING OF BP1 AND BP4.

## JUN 25
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | JONEL V. LLAGUNO / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-25 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 26598 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99297810 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16868173 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 71 | 50 | 68 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 99301765 | 3955 | 94.92 | 3.955 | 4.7 | 4.7 | 2B | 0 | 0 | 0 | 1185 | 1098 | 0 | N/A | N/A | N/A | 16868941 | 768 | 194.1846 | 0% | 0% | 0% | 100% | 100% | 0% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 3 | 71 | 50 | 68 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 99305590 | 3825 | 91.8 | 3.825 | 5.4 | 5.4 | 3B | 0 | 0 | 0 | 1185 | 1025 | 1185 | N/A | N/A | N/A | 16869875 | 934 | 244.183 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 4 | 70 | 70 | 67 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 99309188 | 3598 | 86.352 | 3.598 | 6.8 | 6.8 | 3B | 0 | 0 | 0 | 1185 | 1007 | 1185 | N/A | N/A | N/A | 16870884 | 1009 | 280.4336 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 5 | 69 | 48.5915 | 66 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 12.8 | DEF |  | 99312665 | 3477 | 83.448 | 3.477 | 8.4 | 8.4 | 3B | 0 | 0 | 0 | 1185 | 1005 | 1185 | N/A | N/A | N/A | 16871865 | 981 | 282.1398 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 6 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 99316685 | 4020 | 96.48 | 4.02 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16872896 | 1031 | 256.4677 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 7 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 13.1 | DEF |  | 99321186 | 4501 | 108.024 | 4.501 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16874028 | 1132 | 251.4997 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.94 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 99325435 | 4249 | 101.976 | 4.249 | 9.1 | 9.1 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16875169 | 1141 | 268.5338 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 99330417 | 4982 | 119.568 | 4.982 | 8.5 | 8.5 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16876365 | 1196 | 240.0642 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 7 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 99334978 | 4561 | 109.464 | 4.561 | 8 | 8 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16877529 | 1164 | 255.2072 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99339805 | 4827 | 115.848 | 4.827 | 7.4 | 7.4 | 3B+1S | 1017 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16878757 | 1228 | 254.4023 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.06 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99344104 | 4299 | 103.176 | 4.299 | 6.9 | 6.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16879912 | 1155 | 268.6671 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 99349125 | 5021 | 120.504 | 5.021 | 6.3 | 6.3 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16881085 | 1173 | 233.6188 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 99354335 | 5210 | 125.04 | 5.21 | 5.9 | 5.9 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16882239 | 1154 | 221.4971 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 2 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | DEF |  | 99359130 | 4795 | 115.08 | 4.795 | 5.5 | 5.5 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16883409 | 1170 | 244.0042 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | DEF |  | 99363540 | 4410 | 105.84 | 4.41 | 5.1 | 5.1 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16884565 | 1156 | 262.1315 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 2 | 77 | 54.2254 | 75 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | DEF |  | 99367935 | 4395 | 105.48 | 4.395 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16885723 | 1158 | 263.4812 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99372708 | 4773 | 114.552 | 4.773 | 4.5 | 4.5 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16886874 | 1151 | 242.6147 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99378021 | 5313 | 127.512 | 5.313 | 4.1 | 4.1 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16888048 | 1174 | 216.6384 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.7 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 99383250 | 5229 | 125.496 | 5.229 | 3.7 | 3.7 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16889182 | 1134 | 216.8675 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -1 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99388708 | 5458 | 130.992 | 5.458 | 3.4 | 3.4 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16890331 | 1149 | 210.5167 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -1 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.1 | DEF |  | 99394000 | 5292 | 127.008 | 5.292 | 3.1 | 3.1 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16891468 | 1137 | 214.8526 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -1 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 14 | A ONG | 12.6 | DEF |  | 99399385 | 5385 | 129.24 | 5.385 | 2.9 | 2.9 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16892654 | 1186 | 220.2414 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.89 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | DEF |  | 99403920 | 4535 | 108.84 | 4.535 | 3.5 | 3.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16893702 | 1048 | 231.0915 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 73 | 51.4085 | 71 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | DEF |  | 99408295 | 4375 | 105 | 4.375 | 4.5 | 4.5 |  | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16894771 | 1069 | 244.3429 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 110485 | 2651.64 | 110.485 | [13 empty] | 26598 | 240.7386 | [7 empty] | 0 | 0 | 0.91667 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 72 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 6:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:35 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
- | SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 25, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.9 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 26
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | JONEL V. LLAGUNO / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-26 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27425 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99408295 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16894771 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 72 | 50.7042 | 70 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.4 | DEF |  | 99412490 | 4195 | 100.68 | 4.195 | 5.6 | 5.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16895874 | 1103 | 262.9321 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 99416549 | 4059 | 97.416 | 4.059 | 6.8 | 6.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16896963 | 1089 | 268.2927 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 75 | 70 | 71 | Automatic - Pressure Setting | 47.8873 | 49.2958 | 53.5211 | 14 | A.ONG | 11.2 | DEF |  | 99420285 | 3736 | 89.664 | 3.736 | 7.9 | 7.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16898057 | 1094 | 292.8266 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 12.8 | DEF |  | 99424030 | 3745 | 89.88 | 3.745 | 9.1 | 9.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16899151 | 1094 | 292.1228 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 78 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A.ONG | 13.1 | DEF |  | 99427966 | 3936 | 94.464 | 3.936 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16900229 | 1078 | 273.8821 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 78 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | DEF |  | 99432899 | 4933 | 118.392 | 4.933 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16901344 | 1115 | 226.0288 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 7 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 99438058 | 5159 | 123.816 | 5.159 | 8.9 | 8.9 | 3B+1S | 0 | 1027 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16902552 | 1208 | 234.1539 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 99443280 | 5222 | 125.328 | 5.222 | 8.3 | 8.3 | 3B+1S | 0 | 1030 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16903741 | 1189 | 227.6905 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 99448345 | 5065 | 121.56 | 5.065 | 7.6 | 7.6 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16904934 | 1193 | 235.538 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99453285 | 4940 | 118.56 | 4.94 | 6.9 | 6.9 | 3B+1S | 0 | 1037 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16906130 | 1196 | 242.1053 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.08 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99458080 | 4795 | 115.08 | 4.795 | 6.3 | 6.3 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16907316 | 1186 | 247.341 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 99462876 | 4796 | 115.104 | 4.796 | 5.7 | 5.7 | 3B+1S | 0 | 1036 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16908509 | 1193 | 248.749 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 99468140 | 5264 | 126.336 | 5.264 | 5.3 | 5.3 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16909668 | 1159 | 220.1748 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 4 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | DEF |  | 99473136 | 4996 | 119.904 | 4.996 | 4.8 | 4.8 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16910839 | 1171 | 234.3875 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.93 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 4 | 78 | 54.9296 | 76 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 18 | A ONG | 16.9 | DEF |  | 99477960 | 4824 | 115.776 | 4.824 | 4.5 | 4.5 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16911995 | 1156 | 239.6352 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | DEF |  | 99482235 | 4275 | 102.6 | 4.275 | 4.3 | 4.3 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16913063 | 1068 | 249.8246 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99487540 | 5305 | 127.32 | 5.305 | 3.8 | 3.8 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16914287 | 1224 | 201.3195 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99492165 | 4625 | 111 | 4.625 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16915438 | 1151 | 264.6486 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 0 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 99497190 | 5025 | 120.6 | 5.025 | 3.2 | 3.2 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16916581 | 1143 | 227.4627 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99502400 | 5210 | 125.04 | 5.21 | 2.9 | 2.9 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16917727 | 1146 | 219.9616 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 99507090 | 4690 | 112.56 | 4.69 | 2.6 | 2.6 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16918857 | 1130 | 240.9382 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 99512144 | 5054 | 121.296 | 5.054 | 2.4 | 2.4 | 3B+1S | 0 | 1005 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16920014 | 1157 | 228.9276 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 1 | 71 | 50 | 68 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 99517377 | 5233 | 125.592 | 5.233 | 3.1 | 3.1 | 3B | 0 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 16921113 | 1099 | 210.0134 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.5 | DEF |  | 99522274 | 4897 | 117.528 | 4.897 | 4 | 4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16922196 | 1083 | 221.1558 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 113979 | 2735.496 | 113.979 | [13 empty] | 27425 | 240.6145 | [7 empty] | 0 | 0 | 1.0067 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 72 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 6:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:10 AM WATER ELEVATION (9.5 M)
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 26, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2- STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.4 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 27
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
[16 empty] | 10pm - 6am | JONEL V. LLAGUNO / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-27 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27478 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99522274 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16922196 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 70 | 49.2958 | 67 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 99526875 | 4601 | 110.424 | 4.601 | 5.1 | 5.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16923294 | 1098 | 238.6438 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 4 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A.ONG | 11.2 | DEF |  | 99531130 | 4255 | 102.12 | 4.255 | 6.6 | 6.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16924416 | 1122 | 263.6898 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 73 | 70 | 69 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 99534970 | 3840 | 92.16 | 3.84 | 8.1 | 8.1 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16925507 | 1091 | 284.1146 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 7 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 99538630 | 3660 | 87.84 | 3.66 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16926550 | 1043 | 284.9727 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 79 | 76 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A.ONG | 13.1 | DEF |  | 99542590 | 3960 | 95.04 | 3.96 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1188 | 1185 | N/A | N/A | N/A | 16927689 | 1139 | 287.6263 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 9 | 79 | 55.6338 | 77 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | DEF |  | 99547164 | 4574 | 109.776 | 4.574 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16928798 | 1109 | 242.4574 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.98 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 16.7 | DEF |  | 99551835 | 4671 | 112.104 | 4.671 | 8.8 | 8.8 | 3B+1S | 1016 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 16930025 | 1227 | 262.6846 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 99556482 | 4647 | 111.528 | 4.647 | 8.1 | 8.1 | 3B+1S | 1048 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 16931212 | 1187 | 255.4336 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 99561013 | 4531 | 108.744 | 4.531 | 7.4 | 7.4 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16932400 | 1188 | 262.1938 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99565692 | 4679 | 112.296 | 4.679 | 6.8 | 6.8 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16933599 | 1199 | 256.2513 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.07 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.7 | DEF |  | 99570061 | 4369 | 104.856 | 4.369 | 6.2 | 6.2 | 3B+1S | 1017 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16934782 | 1183 | 270.7713 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.3 | DEF |  | 99574354 | 4293 | 103.032 | 4.293 | 5.6 | 5.6 | 3B+1S | 1037 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16935967 | 1185 | 276.0307 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 99578597 | 4243 | 101.832 | 4.243 | 5.1 | 5.1 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16937118 | 1151 | 271.2703 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | DEF |  | 99582840 | 4243 | 101.832 | 4.243 | 4.7 | 4.7 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16938285 | 1167 | 275.0412 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.78 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | -1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 99587180 | 4340 | 104.16 | 4.34 | 4.4 | 4.4 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16939475 | 1190 | 274.1935 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | -1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 99591460 | 4280 | 102.72 | 4.28 | 4 | 4 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16940603 | 1128 | 263.5514 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | -1 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99596265 | 4805 | 115.32 | 4.805 | 3.7 | 3.7 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16941793 | 1190 | 234.7555 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99600800 | 4535 | 108.84 | 4.535 | 3.4 | 3.4 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16942925 | 1132 | 262.4035 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.8 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99605640 | 4840 | 116.16 | 4.84 | 3.1 | 3.1 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16944080 | 1155 | 238.6364 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99610970 | 5330 | 127.92 | 5.33 | 2.8 | 2.8 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16945215 | 1135 | 212.9456 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -2 | 74 | 52.1127 | 71 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 99615895 | 4925 | 118.2 | 4.925 | 2.5 | 2.5 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16946341 | 1126 | 228.6294 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -1 | 76 | 53.5211 | 73 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 99620575 | 4680 | 112.32 | 4.68 | 2.3 | 2.3 | 3B+1S | 1005 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 16947457 | 1116 | 238.4615 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 0 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A ONG | 11.9 | DEF |  | 99625430 | 4855 | 116.52 | 4.855 | 2.9 | 2.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16948573 | 1116 | 229.8661 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 77 | 54.2254 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 11.5 | DEF |  | 99629897 | 4467 | 107.208 | 4.467 | 3.8 | 3.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16949674 | 1101 | 246.4741 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 107623 | 2582.952 | 107.623 | [13 empty] | 27478 | 255.3172 | [7 empty] | 0 | 0 | 0.935 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 72 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:55 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 27, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 28
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | REY PROVIDENCIA / FIDEL RAMOS
[16 empty] | 10pm - 6am | JONEL V. LLAGUNO / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-28 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27459 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99629897 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16949674 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.4 | DEF |  | 99633665 | 3768 | 90.432 | 3.768 | 5 | 5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16950752 | 1078 | 286.0934 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 3 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.2 | DEF |  | 99637532 | 3867 | 92.808 | 3.867 | 6.4 | 6.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16951821 | 1069 | 276.4417 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 5 | 73 | 70 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 99641195 | 3663 | 87.912 | 3.663 | 7.9 | 7.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16952976 | 1155 | 315.3153 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 83 | 58.4507 | 80 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 59.1549 | 14 | A.ONG | 12.8 | DEF |  | 99645149 | 3954 | 94.896 | 3.954 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16954065 | 1089 | 275.4173 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 8 | 79 | 76 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A.ONG | 13.1 | DEF |  | 99649170 | 4021 | 96.504 | 4.021 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16955154 | 1089 | 270.8282 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 13.1 | DEF |  | 99653470 | 4300 | 103.2 | 4.3 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16956225 | 1071 | 249.0698 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.99 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 7 | 78 | 54.9296 | 78 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 99658637 | 5167 | 124.008 | 5.167 | 9 | 9 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16957454 | 1229 | 237.8556 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 99663514 | 4877 | 117.048 | 4.877 | 8.4 | 8.4 | 3B+1S | 0 | 1018 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 16958635 | 1181 | 242.1571 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 99667803 | 4289 | 102.936 | 4.289 | 7.8 | 7.8 | 3B+1S | 0 | 1017 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16959821 | 1186 | 276.5213 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99671870 | 4067 | 97.608 | 4.067 | 7.2 | 7.2 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16961001 | 1180 | 290.1402 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.06 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99675933 | 4063 | 97.512 | 4.063 | 6.7 | 6.7 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16962173 | 1172 | 288.4568 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 99680196 | 4263 | 102.312 | 4.263 | 6.1 | 6.1 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16963358 | 1185 | 277.9733 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 3 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 19 | A ONG | 17.5 | DEF |  | 99684542 | 4346 | 104.304 | 4.346 | 5.6 | 5.6 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16964523 | 1165 | 268.0626 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 17.3 | DEF |  | 99689135 | 4593 | 110.232 | 4.593 | 5.2 | 5.2 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16965698 | 1175 | 255.8241 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.95 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 3 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 18 | A ONG | 16.9 | DEF |  | 99693370 | 4235 | 101.64 | 4.235 | 4.8 | 4.8 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16966845 | 1147 | 270.8383 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 2 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.7 | DEF |  | 99697795 | 4425 | 106.2 | 4.425 | 4.5 | 4.5 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16968008 | 1163 | 262.8249 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | 2 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 99702183 | 4388 | 105.312 | 4.388 | 4 | 4 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16969168 | 1160 | 265.041 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | 2 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99706582 | 4399 | 105.576 | 4.399 | 3.5 | 3.5 | 3B+1S | 0 | 1015 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16970347 | 1179 | 263.6963 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99711524 | 4942 | 118.608 | 4.942 | 3.2 | 3.2 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16971488 | 1141 | 230.8782 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | 1 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99716718 | 5194 | 124.656 | 5.194 | 2.8 | 2.8 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16972644 | 1156 | 222.5645 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | 0 | 74 | 52.1127 | 73 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 99721911 | 5193 | 124.632 | 5.193 | 2.4 | 2.4 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16973801 | 1157 | 222.7999 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -2 | 66 | 46.4789 | 64 | Automatic - Pressure Setting | 42.9577 | 44.3662 | 48.5915 | 14 | A ONG | 12.6 | DEF |  | 99726845 | 4934 | 118.416 | 4.934 | 2.1 | 2.1 | 3B+1S | 0 | 1016 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16974956 | 1155 | 234.09 | 0% | 100% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.05 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | 1 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A ONG | 11.9 | DEF |  | 99731651 | 4806 | 115.344 | 4.806 | 2.8 | 2.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16976048 | 1092 | 227.216 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | 2 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 47.1831 | 48.5915 | 52.8169 | 14 | A ONG | 11.5 | DEF |  | 99736455 | 4804 | 115.296 | 4.804 | 3.6 | 3.6 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16977133 | 1085 | 225.8535 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 106558 | 2557.392 | 106.558 | [13 empty] | 27459 | 257.6906 | [7 empty] | 0 | 0 | 1.0217 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 72 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:50 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 6:01 AM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 28, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. NOEL NERPIO AND SOUTH MAINTENANCE TEAM ARRIVE @ 3:27 PM TO CONDUCT WARM UP EXSERCISE OF GENSET 1 AND 2 WITHOUT LOAD FOR 5 MINUTES.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2- STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.1 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)

## JUN 29
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | R.PROVIDENCIA / J. LLAGUNO
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-29 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27569 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99736455 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 16977133 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 3 | 70 | 49.2958 | 68 | Automatic - Pressure Setting | 44.3662 | 45.7746 | 50 | 14 | A.ONG | 11.4 | DEF |  | 99740433 | 3978 | 95.472 | 3.978 | 4.8 | 4.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16978242 | 1109 | 278.7833 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 3 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 99744516 | 4083 | 97.992 | 4.083 | 6.4 | 6.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16979315 | 1073 | 262.797 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.98 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 4 | 72 | 70 | 69 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A.ONG | 11.2 | DEF |  | 99748329 | 3813 | 91.512 | 3.813 | 8 | 8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16980415 | 1100 | 288.4868 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 82 | 57.7465 | 80 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 58.4507 | 14 | A.ONG | 12.8 | DEF |  | 99751830 | 3501 | 84.024 | 3.501 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1186 | 1185 | N/A | N/A | N/A | 16981575 | 1160 | 331.3339 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 79 | 76 | 77 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A.ONG | 13.1 | DEF |  | 99755670 | 3840 | 92.16 | 3.84 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16982679 | 1104 | 287.5 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 13.1 | DEF |  | 99760463 | 4793 | 115.032 | 4.793 | 9.5 | 9.5 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16983774 | 1095 | 228.4582 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.12 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 78 | 54.9296 | 77 | Automatic - Pressure Setting | 53.5211 | 54.9296 | 56.3496 | 19 | A ONG | 16.7 | DEF |  | 99765348 | 4885 | 117.24 | 4.885 | 8.9 | 8.9 | 3B+1S | 1017 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16984969 | 1195 | 244.6264 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 99769951 | 4603 | 110.472 | 4.603 | 8.3 | 8.3 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16986159 | 1190 | 258.527 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 77 | 54.2254 | 76 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 18.4 | DEF |  | 99774550 | 4599 | 110.376 | 4.599 | 7.6 | 7.6 | 3B+1S | 1046 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16987376 | 1217 | 264.6227 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | DEF | #VALUE! | 5 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99778693 | 4143 | 99.432 | 4.143 | 6.9 | 6.9 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16988547 | 1171 | 282.6454 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | DEF | #VALUE! | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99782819 | 4126 | 99.024 | 4.126 | 6.2 | 6.2 | 3B+1S | 1047 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16989744 | 1197 | 290.1115 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | DEF | #VALUE! | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 99787082 | 4263 | 102.312 | 4.263 | 5.7 | 5.7 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16990914 | 1170 | 274.4546 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | DEF | #VALUE! | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 99791550 | 4468 | 107.232 | 4.468 | 5.2 | 5.2 | 3B+1S | 1016 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16992102 | 1188 | 265.8908 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 17.3 | DEF |  | 99795940 | 4390 | 105.36 | 4.39 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16993283 | 1181 | 269.0205 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.87 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A ONG | 16.9 | DEF |  | 99800155 | 4215 | 101.16 | 4.215 | 4.8 | 4.8 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16994457 | 1174 | 278.5291 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | DEF | #VALUE! | 0 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 18 | A ONG | 16.7 | DEF |  | 99804340 | 4185 | 100.44 | 4.185 | 4.1 | 4.1 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16995591 | 1134 | 270.9677 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99808418 | 4078 | 97.872 | 4.078 | 3.7 | 3.7 | 3B+1S | 1006 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16996733 | 1142 | 278.0775 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.7 | DEF |  | 99812995 | 4577 | 109.848 | 4.577 | 3.4 | 3.4 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16997923 | 1190 | 249.5084 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 0.83 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | DEF | #VALUE! | -2 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 18 | A ONG | 16.6 | DEF |  | 99817470 | 4475 | 107.4 | 4.475 | 3.2 | 3.2 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 16999060 | 1137 | 254.0782 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | DEF | #VALUE! | -4 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99822056 | 4586 | 110.064 | 4.586 | 2.9 | 2.9 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17000206 | 1146 | 249.891 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | DEF | #VALUE! | -5 | 74 | 52.1127 | 70 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 99826925 | 4869 | 116.856 | 4.869 | 2.6 | 2.6 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17001332 | 1126 | 231.259 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | DEF | #VALUE! | -5 | 76 | 53.5211 | 74 | Automatic - Pressure Setting | 50 | 51.4085 | 55.6338 | 14 | A ONG | 12.6 | DEF |  | 99832175 | 5250 | 126 | 5.25 | 2.3 | 2.3 | 3B+1S | 1005 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17002525 | 1193 | 227.2381 | 100% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | DEF | #VALUE! | -5 | 69 | 48.5915 | 67 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A ONG | 11.9 | DEF |  | 99836840 | 4665 | 111.96 | 4.665 | 2.9 | 2.9 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17003575 | 1050 | 225.0804 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | DEF | #VALUE! | -2 | 69 | 48.5915 | 66 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A ONG | 11.5 | DEF |  | 99841390 | 4550 | 109.2 | 4.55 | 4.4 | 4.4 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17004702 | 1127 | 247.6923 | 0% | 0% | 0% | 100% | 100% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 104935 | 2518.44 | 104.935 | [13 empty] | 27569 | 262.7245 | [7 empty] | 0 | 0 | 0.975 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 72 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 4:00 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 6:01 AM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 29, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1- STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.3 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (20%)

## JUN 30
ENGINEER / OPERATOR ON DUTY
| BDOM DAILY OPERATION REPORT | [14 empty] | 6am - 2pm | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
| WATER NETWORK | [14 empty] | 2pm - 10pm | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
[16 empty] | 10pm - 6am | REY PROVIDENCIA / PAUL G. LABIAN
| LOCATION: |  | Villamor Pump Station and Reservoir | [9 empty] | 2014-02-16
| DATE |  | UNIT | [5 empty] | OPERATIONAL STATUS | Min | Target | Max |  |  |  | Suction Line (900mm) | Discharge Line (1600mm) |  |  |  |  | Reservoir MIN/MAX (m) |  | Operational Pumps | Green |  | Orange |  | RED |  | MIN SPEED (RPM) |  | MULTIPLIER | Totalizer KWHR | Max KwHr | Max KwHr/ML | VALVE SETTING | [5 empty] | RESERVOIR REFILL |  |  | Res. Chl.
| 2018-06-29 |  | m of H2O | [6 empty] | m of H2O | [5 empty] | MLD | MLD | m3 | m3 | MLD | ML | 1.3m - 10m |  | 3B+2S | 0 |  | >0 to <1185 |  | 1185 |  | 800 |  |  | 27439 |  |  | 0% - 100% | 0% - 100% | 0% - 100% | 0% - 100% |  | 0% - 100% | 0% - 100% | m3 | m3 | 0.3 - 1.5 |  | PLANT STATUS
| Time |  | Suction |  |  | Discharge |  |  | Plant Status | Pressure Requirement |  |  | Change in Pressure Setting / Requirement | Instructed By: | i2o pressure | Suction Flow Rate | Discharge Flow Rate | Total Production | Hourly Production (1600mm) |  |  | Reservoir Level A | Reservoir Level B | No of units in operation | Motor Speed (RPM) | [7 empty] | Power Consumption Meralco rdg | Power Consumption ATS rdg (KWHr) | Hourly Energy Consumption (KWHr) | Hourly KWHr per Production KWHr/ML | MOV 1 SP1 | MOV 2 SP2 | MOV 3 BP1 | MOV 4 BP2 | MOV 5 BP3 | MOV 6 BP4 | Reservoir Inlet XCVI | Totalizer Reading | Reservoir Hourly Refill XCV4 | Chlorine Residual | Hourly Remarks | Details | Code | SOUTH BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading | psi | (m) | Gauge Reading |  | (m) | (m) | (m) | m of H2O |  | m of H2O |  |  | 99841390 |  |  |  | (m) | (m) |  | SP1 | SP2 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 |  | 17004702 |  |  | DVO | DVO | DVO | DVO | DVO | DVO | DVO |  |  | mg /l |  | Automatic - i2O | AI | REY L. PROVIDENCIA / GEORGE O. HERNANDEZ
| 48:00 | 1:00 | DEF | #VALUE! | 2 | 69 | 48.5915 | 67 | Automatic - Pressure Setting | 43.662 | 45.0704 | 49.2958 | 14 | A.ONG | 11.4 | DEF |  | 99845305 | 3915 | 93.96 | 3.915 | 5.8 | 5.8 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17005790 | 1088 | 277.9055 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Automatic - Pressure Setting | AP | PAUL G. LABIAN / ARMAN R. RAYALA II
| 49:00 | 2:00 | DEF | #VALUE! | 3 | 71 | 50 | 69 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A.ONG | 11.2 | DEF |  | 99849134 | 3829 | 91.896 | 3.829 | 7.3 | 7.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17006841 | 1051 | 274.4842 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Manual Operation | MO | PAUL G. LABIAN / GEORGE O. HERNANDEZ
| 50:00 | 3:00 | DEF | #VALUE! | 4 | 73 | 51.4085 | 70 | Automatic - Pressure Setting | 46.4789 | 47.8873 | 52.1127 | 14 | A.ONG | 11.2 | DEF |  | 99852780 | 3646 | 87.504 | 3.646 | 8.3 | 8.3 | 3B | 0 | 0 | 0 | 1185 | 1187 | 1185 | N/A | N/A | N/A | 17008003 | 1162 | 318.7054 | 0% | 0% | 0% | 100% | 100% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Scheduled Shutdown | SS | PAUL G. LABIAN / REY PROVIDENCIA
| 51:00 | 4:00 | DEF | #VALUE! | 6 | 81 | 57.0423 | 78 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 14 | A.ONG | 12.8 | DEF |  | 99856779 | 3999 | 95.976 | 3.999 | 9.5 | 9.5 | 3B | 0 | 0 | 1167 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17009118 | 1115 | 278.8197 | 0% | 0% | 100% | 100% | 0% | 100% | 80% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Start Up Error | SU | PAUL G. LABIAN / FIDEL A. RAMOS
| 52:00 | 5:00 | DEF | #VALUE! | 7 | 81 | 57.0423 | 79 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 57.7465 | 18 | A.ONG | 13.1 | DEF |  | 99861052 | 4273 | 102.552 | 4.273 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17010124 | 1006 | 235.4318 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Shutdown Error | SE | PAUL G. LABIAN / JONEL LLAGUNO
| 53:00 | 6:00 | DEF | #VALUE! | 8 | 79 | 55.6338 | 79 | Automatic - Pressure Setting | 54.2254 | 55.6338 | 57.0538 | 19 | A ONG | 13.1 | DEF |  | 99866004 | 4952 | 118.848 | 4.952 | 9.5 | 9.5 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17011284 | 1160 | 234.2488 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.97 | Normal operation schedule | Error - General | E | PAUL G. LABIAN / DYAN ELVIN CAPIÑA
| 54:00 | 7:00 | DEF | #VALUE! | 8 | 80 | 56.338 | 79 | Automatic - Pressure Setting | 54.9296 | 56.338 | 57.758 | 19 | A ONG | 16.7 | DEF |  | 99871024 | 5020 | 120.48 | 5.02 | 9.3 | 9.3 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17012386 | 1102 | 219.5219 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Power Interruption | PI | ARMAN R. RAYALA II / FIDEL A. RAMOS
| 55:00 | 8:00 | DEF | #VALUE! | 7 | 77 | 54.2254 | 77 | Automatic - Pressure Setting | 52.8169 | 54.2254 | 55.6454 | 19 | A ONG | 17.3 | DEF |  | 99876237 | 5213 | 125.112 | 5.213 | 8.7 | 8.7 | 3B+1S | 0 | 1016 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17013577 | 1191 | 228.4673 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Water Interruption | WI | ARMAN R. RAYALA II / REY PROVIDENCIA
| 56:00 | 9:00 | DEF | #VALUE! | 6 | 76 | 53.5211 | 76 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 18.4 | DEF |  | 99880742 | 4505 | 108.12 | 4.505 | 8.1 | 8.1 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17014754 | 1177 | 261.2653 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | Equipment Maintenance | EM | R.PROVIDENCIA / J. LLAGUNO
| 57:00 | 10:00 | 3 | 2.1127 | 5 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99885361 | 4619 | 110.856 | 4.619 | 7.4 | 7.4 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17015983 | 1229 | 266.0749 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / FIDEL A. RAMOS
| 58:00 | 11:00 | 3 | 2.1127 | 4 | 76 | 53.5211 | 75 | Automatic - Pressure Setting | 52.1127 | 53.5211 | 54.9411 | 19 | A ONG | 17.7 | DEF |  | 99889897 | 4536 | 108.864 | 4.536 | 6.7 | 6.7 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17017197 | 1214 | 267.6367 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule |  |  | GEORGE O. HERNANDEZ / ARMAN R. RAYALA II
| 59:00 | 12:00 | 3 | 2.1127 | 4 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 54.2369 | 19 | A ONG | 17.3 | DEF |  | 99894401 | 4504 | 108.096 | 4.504 | 6 | 6 | 3B+1S | 0 | 1048 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17018372 | 1175 | 260.8792 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Normal operation schedule | UNITS |  | GEORGE O. HERNANDEZ / PAUL G. LABIAN
| 60:00 | 13:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 74 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 19 | A ONG | 17.5 | DEF |  | 99899006 | 4605 | 110.52 | 4.605 | 5.3 | 5.3 | 3B+1S | 0 | 1046 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17019585 | 1213 | 263.4093 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | PRESSURE | Atmospheric Pressure | FIDEL RAMOS / ARMAN R. RAYALA II
| 61:00 | 14:00 | 3 | 2.1127 | 3 | 75 | 52.8169 | 72 | Automatic - Pressure Setting | 51.4085 | 52.8169 | 57.0423 | 18 | A ONG | 17.3 | DEF |  | 99903497 | 4491 | 107.784 | 4.491 | 4.7 | 4.7 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17020777 | 1192 | 265.4197 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 0.88 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | 14.7 | REY L. PROVIDENCIA / ARMAN R. RAYALA II
| 62:00 | 15:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 50.7042 | 52.1127 | 56.338 | 18 | A ONG | 16.9 | DEF |  | 99907642 | 4145 | 99.48 | 4.145 | 4.4 | 4.4 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17021900 | 1123 | 270.9288 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | psi | 10.36 | A.RAYALA II /J. LLAGUNO
| 63:00 | 16:00 | 3 | 2.1127 | 0 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99912030 | 4388 | 105.312 | 4.388 | 3.9 | 3.9 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17023049 | 1149 | 261.8505 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | bar | 1.0132 | REY PROVIDENCIA / PAUL G. LABIAN
| 64:00 | 17:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99916410 | 4380 | 105.12 | 4.38 | 3.5 | 3.5 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17024224 | 1175 | 262.3288 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | atm | 1 | R.PROVIDENCIA/J. LLAGUNO
| 65:00 | 18:00 | 3 | 2.1127 | -1 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.7 | DEF |  | 99920850 | 4440 | 106.56 | 4.44 | 3.1 | 3.1 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17025370 | 1146 | 264.6396 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.03 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | kPA | 101.325 | JONEL V. LLAGUNO / PAUL G. LABIAN
| 66:00 | 19:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99925565 | 4715 | 113.16 | 4.715 | 2.8 | 2.8 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17026531 | 1161 | 246.2354 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | FIDEL RAMOS / JONEL LLAGUNO
| 67:00 | 20:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.6 | DEF |  | 99930690 | 5125 | 123 | 5.125 | 2.5 | 2.5 | 3B+1S | 0 | 1006 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17027660 | 1129 | 220.2927 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | Convert Pressure (Enter Unit and Value) |  | REY PROVIDENCIA / FIDEL RAMOS
| 68:00 | 21:00 | 3 | 2.1127 | -3 | 74 | 52.1127 | 72 | Automatic - Pressure Setting | 48.5915 | 50 | 54.2254 | 18 | A ONG | 16.1 | DEF |  | 99936185 | 5495 | 131.88 | 5.495 | 2.2 | 2.2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17028805 | 1145 | 208.3712 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | m of H2O | psi | R.PROVIDENCIA / DYAN ELVIN CAPIÑA
| 69:00 | 22:00 | 3 | 2.1127 | -3 | 75 | 52.8169 | 73 | Automatic - Pressure Setting | 49.2958 | 50.7042 | 54.9296 | 14 | A ONG | 12.6 | DEF |  | 99941501 | 5316 | 127.584 | 5.316 | 2 | 2 | 3B+1S | 0 | 1005 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17029950 | 1145 | 215.3875 | 0% | 100% | 100% | 100% | 0% | 100% | 0% |  | 0 | 1.02 | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | 1 | 1.4189 | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 70:00 | 23:00 | 3 | 2.1127 | -2 | 71 | 50 | 70 | Automatic - Pressure Setting | 45.0704 | 46.4789 | 50.7042 | 14 | A ONG | 11.9 | DEF |  | 99946663 | 5162 | 123.888 | 5.162 | 2.3 | 2.3 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17031054 | 1104 | 213.8706 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) |  |  | GEORGE HERNANDEZ / JONEL LLAGUNO
| 71:00 | 24:00 | 3 | 2.1127 | 0 | 72 | 50.7042 | 71 | Automatic - Pressure Setting | 45.7746 | 47.1831 | 51.4085 | 14 | A ONG | 11.5 | DEF |  | 99951744 | 5081 | 121.944 | 5.081 | 2.9 | 2.9 | 3B | 0 | 0 | 1187 | 1185 | 0 | 1185 | N/A | N/A | N/A | 17032141 | 1087 | 213.9343 | 0% | 0% | 100% | 100% | 0% | 100% | 0% |  | 0 |  | Additional 3psi to normal target discharge pressure as request OF Engr. Edmundo Llagas Jr (SPM) | FLOW | MLD | ARMAN R. RAYALA II / DYAN ELVIN A. CAPIÑA
[13 empty] | TOTAL | [5 empty] | 110354 | 2648.496 | 110.354 | [13 empty] | 27439 | 248.6453 | [7 empty] | 0 | 0 | 0.96833 |  | MLD | 1 | FIDEL RAMOS / DYAN ELVIN CAPIÑA
[48 empty] | m3/hr | 41.67
| NOTABLE REMARKS FOR THE DAY : | [46 empty] | Liter/sec | 11.575
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
Target Discharge Pressure set to 83 psi @ 12:01 am as per request of Engr. FRANCES MORLA (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 12:01 AM TO 3:01 AM AS PER SCHEDULE
Change operation advise as per Sir. Alvin Cruz effective SEPTEMBER 7, 2016 target pressure for 12:01 MN to 3:01 AM will be changed from 75 psi to 83 psi only. This was requested by Sir. GIGI effective until further notice.
FLOW METER DEFFECTIVE AS OF JULY 18, 2017
RESERVOIR REFILL TOTALIZER READING DEFFECTIVE AS OF JULY 18, 2017
XCV2- INCREASE OPENING @ 12:01 AM (80%)
TARGET DISCHARGE PRESSURE SET TO 72 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
XCV2 - CLOSED @ 3:20 AM WATER ELEVATION (9.5 M)
BP3 STOPPED @ 3:30 AM DUE TO SHIFTING OF PUMP
BP1 STARTED @ 3:31 AM DUE TO SHIFTING OF PUMP
- | TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 AM TO 6:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( JUNE 30, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2- STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV2 -OPENED @ 10:01 PM (30%)