## 1
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-01
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 6879083 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1723169 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-01 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 68 | 47.8873 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6882855 |  |  |  | 3772 | 3.772 | 90.528 | a41: 90.528; a42: 5.6; a43: 5.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1724263; a109: 1094; a111: 1094 | 1094 | 290.0318 |  |  | Manual Operation | MO
2018-10-01 | 49:00 | 2:00 | 4 | 2.8169 | 3 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6887085 |  |  |  | 4230 | 4.23 | 101.52 | a41: 101.52; a42: 7; a43: 7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1725376; a109: 1113; a111: 1113 | 1113 | 263.1206 | 1.05 |  | Scheduled Shutdown | SS
2018-10-01 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6891360 |  |  |  | 4275 | 4.275 | 102.6 | a41: 102.6; a42: 8.4; a43: 8.4; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1726477; a109: 1101; a111: 1101 | 1101 | 257.5439 |  |  | Start Up Error | SU
2018-10-01 | 51:00 | 4:00 | 4 | 2.8169 | 6 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6896129 |  |  |  | 4769 | 4.769 | 114.456 | a41: 114.456; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1727539; a109: 1062; a111: 1062 | 1062 | 222.6882 |  |  | Shutdown Error | SE
2018-10-01 | 52:00 | 5:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6900905 |  |  |  | 4776 | 4.776 | 114.624 | a41: 114.624; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1728690; a109: 1151; a111: 1151 | 1151 | 240.9966 |  |  | Error - General | E
2018-10-01 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6905488 |  |  |  | 4583 | 4.583 | 109.992 | a41: 109.992; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1729817; a109: 1127; a111: 1127 | 1127 | 245.9088 | 0.96 |  | Power Interruption | PI
2018-10-01 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6910364 |  |  |  | 4876 | 4.876 | 117.024 | a41: 117.024; a42: 8.9; a43: 8.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1730959; a109: 1142; a111: 1142 | 1142 | 234.2084 |  |  | Water Interruption | WI
2018-10-01 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6915140 |  |  |  | 4776 | 4.776 | 114.624 | a41: 114.624; a42: 8.3; a43: 8.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1732165; a109: 1206; a111: 1206 | 1206 | 252.5126 |  |  | Equipment Maintenance | EM
2018-10-01 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6919468 |  |  |  | 4328 | 4.328 | 103.872 | a41: 103.872; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: DEF; a107: 1733342; a109: 1177; a111: 1177 | 1177 | 271.9501
2018-10-01 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6923914 |  |  |  | 4446 | 4.446 | 106.704 | a41: 106.704; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1734536; a109: 1194; a111: 1194 | 1194 | 268.556 | 1.08
2018-10-01 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6928440 |  |  |  | 4526 | 4.526 | 108.624 | a41: 108.624; a42: 6.5; a43: 6.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1735741; a109: 1205; a111: 1205 | 1205 | 266.2395 |  |  | UNITS
2018-10-01 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6932625 |  |  |  | 4185 | 4.185 | 100.44 | a41: 100.44; a42: 5.9; a43: 5.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1736918; a109: 1177; a111: 1177 | 1177 | 281.2425 |  |  | PRESSURE | Atmospheric Pressure
2018-10-01 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6936876 |  |  |  | 4251 | 4.251 | 102.024 | a41: 102.024; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1738108; a109: 1190; a111: 1190 | 1190 | 279.9341 |  |  | m of H2O | 14.7
2018-10-01 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6940948 |  |  |  | 4072 | 4.072 | 97.728 | a41: 97.728; a42: 4.9; a43: 4.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: DEF; a107: 1739258; a109: 1150; a111: 1150 | 1150 | 282.4165 | 1.13 |  | psi | 10.36
2018-10-01 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 75 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6945206 |  |  |  | 4258 | 4.258 | 102.192 | a41: 102.192; a42: 4.4; a43: 4.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1740431; a109: 1173; a111: 1173 | 1173 | 275.4814 |  |  | bar | 1.0132
2018-10-01 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6949452 |  |  |  | 4246 | 4.246 | 101.904 | a41: 101.904; a42: 4; a43: 4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1741585; a109: 1154; a111: 1154 | 1154 | 271.7852 |  |  | atm | 1
2018-10-01 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6953817 |  |  |  | 4365 | 4.365 | 104.76 | a41: 104.76; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1742741; a109: 1156; a111: 1156 | 1156 | 264.8339 |  |  | kPA | 101.325
2018-10-01 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6958086 |  |  |  | 4269 | 4.269 | 102.456 | a41: 102.456; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1743899; a109: 1158; a111: 1158 | 1158 | 271.2579 | 1.01
2018-10-01 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6962195 |  |  |  | 4109 | 4.109 | 98.616 | a41: 98.616; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: DEF; a107: 1745040; a109: 1141; a111: 1141 | 1141 | 277.6831 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-01 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 69 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6966399 |  |  |  | 4204 | 4.204 | 100.896 | a41: 100.896; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1746214; a109: 1174; a111: 1174 | 1174 | 279.2578 |  |  | m of H2O | psi
2018-10-01 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 69 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6970557 |  |  |  | 4158 | 4.158 | 99.792 | a41: 99.792; a42: 2.4; a43: 2.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1747356; a109: 1142; a111: 1142 | 1142 | 274.6513 |  |  | 1 | 1.4189
2018-10-01 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 69 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6974796 |  |  |  | 4239 | 4.239 | 101.736 | a41: 101.736; a42: 2.1; a43: 2.1; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1748480; a109: 1124; a111: 1124 | 1124 | 265.1569 | 1.16
2018-10-01 | 70:00 | 23:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6979032 |  |  |  | 4236 | 4.236 | 101.664 | a41: 101.664; a42: 2.5; a43: 2.5; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1749624; a109: 1144; a111: 1144 | 1144 | 270.0661 |  |  | FLOW | MLD
2018-10-01 | 71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6983378 |  |  |  | 4346 | 4.346 | 104.304 | a41: 104.304; a42: 3.1; a43: 3.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1750722; a109: 1098; a111: 1098 | 1098 | 252.6461 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.1667 | 74.1667 | 52.23 | 71.75 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 104295 | 104.295 | 104.295 | a42: 5.6375; a43: 5.6375; a106: 0; a109: 27553; a111: 27553 | 27553 | 264.1833 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | REY PROVIDENCIA / J. LLAGUNO
| 2pm - 10pm | P.LABIAN / D. E. CAPIÑA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR Posadas Influence area.
Target Discharge Pressure set to 75 psi @ 12:01 AM as per request of Engr. Frances Morla (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4 - CLOSED @ 3:50 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
MR. JIMMY AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 8:52 AM TO CONDUCT MONTHLY PREVENTIVE MAINTENANCE OF PUMP AND MOTOR.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( OCT. 1, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
MR. NOEL NERPIO AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 4:35 PM FOR QUARTERLY & SEMI-ANNUAL PREVENTIVE MAINTENANCE.
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.1 ELEVATION LEVEL.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
MR. ERNESTO MONZON AND SOUTH MAINTENANCE TEAM ARRIVE @ 11:26 PM TO CONDUCT PREVENTIVE MAINTENANCE OFFLINE

## 2
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-02
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 0 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1750722 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-02 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 71 | 50 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6987111 |  |  |  | 6987111 | 6987.111 | 167690.664 | a41: 167690.664; a42: 4.2; a43: 4.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1751780; a109: 1058; a111: 1058 | 1058 | 0.15142 |  |  | Manual Operation | MO
2018-10-02 | 49:00 | 2:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 6991478 |  |  |  | 4367 | 4.367 | 104.808 | a41: 104.808; a42: 5.3; a43: 5.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1752916; a109: 1136; a111: 1136 | 1136 | 260.1328 | 1.1 |  | Scheduled Shutdown | SS
2018-10-02 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6995400 |  |  |  | 3922 | 3.922 | 94.128 | a41: 94.128; a42: 6.9; a43: 6.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1754020; a109: 1104; a111: 1104 | 1104 | 281.489 |  |  | Start Up Error | SU
2018-10-02 | 51:00 | 4:00 | 4 | 2.8169 | 6 | 69 | 48.5915 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 6999532 |  |  |  | 4132 | 4.132 | 99.168 | a41: 99.168; a42: 8.5; a43: 8.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1755128; a109: 1108; a111: 1108 | 1108 | 268.151 |  |  | Shutdown Error | SE
2018-10-02 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7003778 |  |  |  | 4246 | 4.246 | 101.904 | a41: 101.904; a42: 9.5; a43: 9.5; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1756196; a109: 1068; a111: 1068 | 1068 | 251.5309 |  |  | Error - General | E
2018-10-02 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 70 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7008727 |  |  |  | 4949 | 4.949 | 118.776 | a41: 118.776; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1757360; a109: 1164; a111: 1164 | 1164 | 235.199 | 1.13 |  | Power Interruption | PI
2018-10-02 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 69 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7013980 |  |  |  | 5253 | 5.253 | 126.072 | a41: 126.072; a42: 8.9; a43: 8.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: DEF; a107: 1758537; a109: 1177; a111: 1177 | 1177 | 224.0624 |  |  | Water Interruption | WI
2018-10-02 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 69 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7019074 |  |  |  | 5094 | 5.094 | 122.256 | a41: 122.256; a42: 8.1; a43: 8.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: DEF; a107: 1759770; a109: 1233; a111: 1233 | 1233 | 242.0495 |  |  | Equipment Maintenance | EM
2018-10-02 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 68 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7023703 |  |  |  | 4629 | 4.629 | 111.096 | a41: 111.096; a42: 7.4; a43: 7.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: DEF; a107: 1760981; a109: 1211; a111: 1211 | 1211 | 261.6116
2018-10-02 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 68 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7028205 |  |  |  | 4502 | 4.502 | 108.048 | a41: 108.048; a42: 6.8; a43: 6.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: DEF; a107: 1762185; a109: 1204; a111: 1204 | 1204 | 267.4367 | 1.15
2018-10-02 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 67 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7032840 |  |  |  | 4635 | 4.635 | 111.24 | a41: 111.24; a42: 6.2; a43: 6.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1763363; a109: 1178; a111: 1178 | 1178 | 254.1532 |  |  | UNITS
2018-10-02 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 67 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7037415 |  |  |  | 4575 | 4.575 | 109.8 | a41: 109.8; a42: 5.6; a43: 5.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1764521; a109: 1158; a111: 1158 | 1158 | 253.1148 |  |  | PRESSURE | Atmospheric Pressure
2018-10-02 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 66 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7041980 |  |  |  | 4565 | 4.565 | 109.56 | a41: 109.56; a42: 5.1; a43: 5.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1765724; a109: 1203; a111: 1203 | 1203 | 263.5268 |  |  | m of H2O | 14.7
2018-10-02 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 69 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7046239 |  |  |  | 4259 | 4.259 | 102.216 | a41: 102.216; a42: 4.7; a43: 4.7; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: DEF; a107: 1766854; a109: 1130; a111: 1130 | 1130 | 265.3205 | 1.08 |  | psi | 10.36
2018-10-02 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 70 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7050543 |  |  |  | 4304 | 4.304 | 103.296 | a41: 103.296; a42: 4.2; a43: 4.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: DEF; a107: 1767998; a109: 1144; a111: 1144 | 1144 | 265.7993 |  |  | bar | 1.0132
2018-10-02 | 63:00 | 16:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7055476 |  |  |  | 4933 | 4.933 | 118.392 | a41: 118.392; a42: 3.8; a43: 3.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: DEF; a107: 1769154; a109: 1156; a111: 1156 | 1156 | 234.3402 |  |  | atm | 1
2018-10-02 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7060379 |  |  |  | 4903 | 4.903 | 117.672 | a41: 117.672; a42: 3.5; a43: 3.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: DEF; a107: 1770310; a109: 1156; a111: 1156 | 1156 | 235.774 |  |  | kPA | 101.325
2018-10-02 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7065267 |  |  |  | 4888 | 4.888 | 117.312 | a41: 117.312; a42: 3.2; a43: 3.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: DEF; a107: 1771453; a109: 1143; a111: 1143 | 1143 | 233.838 | 1.01
2018-10-02 | 66:00 | 19:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 68 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7069847 |  |  |  | 4580 | 4.58 | 109.92 | a41: 109.92; a42: 2.9; a43: 2.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: DEF; a107: 1772595; a109: 1142; a111: 1142 | 1142 | 249.345 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-02 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 69 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7074203 |  |  |  | 4356 | 4.356 | 104.544 | a41: 104.544; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: DEF; a107: 1773764; a109: 1169; a111: 1169 | 1169 | 268.3655 |  |  | m of H2O | psi
2018-10-02 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 69 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7078571 |  |  |  | 4368 | 4.368 | 104.832 | a41: 104.832; a42: 2.2; a43: 2.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: DEF; a107: 1774888; a109: 1124; a111: 1124 | 1124 | 257.326 |  |  | 1 | 1.4189
2018-10-02 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7083134 |  |  |  | 4563 | 4.563 | 109.512 | a41: 109.512; a42: 2; a43: 2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1776010; a109: 1122; a111: 1122 | 1122 | 245.8909 | 1.18
2018-10-02 | 70:00 | 23:00 | 4 | 2.8169 | 1 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7086858 |  |  |  | 3724 | 3.724 | 89.376 | a41: 89.376; a42: 2.9; a43: 2.9; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1777126; a109: 1116; a111: 1116 | 1116 | 299.6778 |  |  | FLOW | MLD
2018-10-02 | 71:00 | 24:00 | 4 | 2.8169 | 2 | 73 | 2 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7091096 |  |  |  | 4238 | 4.238 | 101.712 | a41: 101.712; a42: 4.1; a43: 4.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1778236; a109: 1110; a111: 1110 | 1110 | 261.916 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.5833 | 74.0417 | 50.0833 | 68.5417 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 7091096 | 7091.096 | 7091.096 | a42: 5.3333; a43: 5.3333; a106: 0; a109: 27514; a111: 27514 | 27514 | 3.8801 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | REY PROVIDENCIA / A.RAYALA II
| 2pm - 10pm | P.LABIAN / D. E. CAPIÑA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
Additional 3 psi to target discharge pressure from 12:01 AM to 5:01 AM as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR Posadas Influence area.
Target Discharge Pressure set to 75 psi @ 12:01 AM as per request of Engr. Frances Morla (SPM-South)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (22%)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
XCV4 - CLOSED @ 4:24 AM WATER ELEVATION (9.5 M)
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
Additional 3 psi to target discharge pressure from 12:01 PM to 5:01 PM ( OCT. 2, 2018) as per request of Engr. Frances Morla (SPM-South), due to shifting of WSR and Posadas Influence area.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 8:01 PM TO 10:01 PM AS PER SCHEDULE
SP2 - STOPPED @ 9:40 PM DUE TO PARAMETER CAPACITY OF 2.1 ELEVATION LEVEL.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (17%)

## 3
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-03
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7091096 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1778236 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-03 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 68 | 47.8873 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7095128 |  |  |  | 4032 | 4.032 | 96.768 | a41: 96.768; a42: 5.7; a43: 5.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1779354; a109: 1118; a111: 1118 | 1118 | 277.2817 |  |  | Manual Operation | MO
2018-10-03 | 49:00 | 2:00 | 4 | 2.8169 | 4 | 70 | 49.2958 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7099186 |  |  |  | 4058 | 4.058 | 97.392 | a41: 97.392; a42: 7.3; a43: 7.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1780460; a109: 1106; a111: 1106 | 1106 | 272.5481 | 1.12 |  | Scheduled Shutdown | SS
2018-10-03 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7103588 |  |  |  | 4402 | 4.402 | 105.648 | a41: 105.648; a42: 9; a43: 9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1781564; a109: 1104; a111: 1104 | 1104 | 250.7951 |  |  | Start Up Error | SU
2018-10-03 | 51:00 | 4:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7107856 |  |  |  | 4268 | 4.268 | 102.432 | a41: 102.432; a42: 9.6; a43: 9.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1782636; a109: 1072; a111: 1072 | 1072 | 251.1715 |  |  | Shutdown Error | SE
2018-10-03 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7112624 |  |  |  | 4768 | 4.768 | 114.432 | a41: 114.432; a42: 9.6; a43: 9.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1783724; a109: 1088; a111: 1088 | 1088 | 228.1879 |  |  | Error - General | E
2018-10-03 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 69 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7117609 |  |  |  | 4985 | 4.985 | 119.64 | a41: 119.64; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1784880; a109: 1156; a111: 1156 | 1156 | 231.8957 | 1.15 |  | Power Interruption | PI
2018-10-03 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 69 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7123143 |  |  |  | 5534 | 5.534 | 132.816 | a41: 132.816; a42: 8.8; a43: 8.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1786093; a109: 1213; a111: 1213 | 1213 | 219.1905 |  |  | Water Interruption | WI
2018-10-03 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 68 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7127975 |  |  |  | 4832 | 4.832 | 115.968 | a41: 115.968; a42: 8.2; a43: 8.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1787291; a109: 1198; a111: 1198 | 1198 | 247.9305 |  |  | Equipment Maintenance | EM
2018-10-03 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 68 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7132499 |  |  |  | 4524 | 4.524 | 108.576 | a41: 108.576; a42: 7.5; a43: 7.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1788474; a109: 1183; a111: 1183 | 1183 | 261.4943
2018-10-03 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 67 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7137155 |  |  |  | 4656 | 4.656 | 111.744 | a41: 111.744; a42: 6.9; a43: 6.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: DEF; a107: 1789687; a109: 1213; a111: 1213 | 1213 | 260.5241 | 1.17
2018-10-03 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 73 | 67 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7141532 |  |  |  | 4377 | 4.377 | 105.048 | a41: 105.048; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: DEF; a107: 1790851; a109: 1164; a111: 1164 | 1164 | 265.9356 |  |  | UNITS
2018-10-03 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 66 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7145843 |  |  |  | 4311 | 4.311 | 103.464 | a41: 103.464; a42: 5.6; a43: 5.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: DEF; a107: 1792042; a109: 1191; a111: 1191 | 1191 | 276.27 |  |  | PRESSURE | Atmospheric Pressure
2018-10-03 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 66 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7150113 |  |  |  | 4270 | 4.27 | 102.48 | a41: 102.48; a42: 5; a43: 5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1793232; a109: 1190; a111: 1190 | 1190 | 278.6885 |  |  | m of H2O | 14.7
2018-10-03 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7154338 |  |  |  | 4225 | 4.225 | 101.4 | a41: 101.4; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: DEF; a107: 1794390; a109: 1158; a111: 1158 | 1158 | 274.0828 | 0.99 |  | psi | 10.36
2018-10-03 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7158661 |  |  |  | 4323 | 4.323 | 103.752 | a41: 103.752; a42: 4; a43: 4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1795563; a109: 1173; a111: 1173 | 1173 | 271.3393 |  |  | bar | 1.0132
2018-10-03 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7162956 |  |  |  | 4295 | 4.295 | 103.08 | a41: 103.08; a42: 3.6; a43: 3.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1796744; a109: 1181; a111: 1181 | 1181 | 274.9709 |  |  | atm | 1
2018-10-03 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7167126 |  |  |  | 4170 | 4.17 | 100.08 | a41: 100.08; a42: 3.2; a43: 3.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1017; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.46%; a89: 0%; a96: DEF; a107: 1797883; a109: 1139; a111: 1139 | 1139 | 273.1415 |  |  | kPA | 101.325
2018-10-03 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7171299 |  |  |  | 4173 | 4.173 | 100.152 | a41: 100.152; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1799042; a109: 1159; a111: 1159 | 1159 | 277.7378 | 1.07
2018-10-03 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7175483 |  |  |  | 4184 | 4.184 | 100.416 | a41: 100.416; a42: 2.4; a43: 2.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1800203; a109: 1161; a111: 1161 | 1161 | 277.4857 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-03 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 71 | 50 | 68 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7179687 |  |  |  | 4204 | 4.204 | 100.896 | a41: 100.896; a42: 2; a43: 2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1801385; a109: 1182; a111: 1182 | 1182 | 281.1608 |  |  | m of H2O | psi
2018-10-03 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 71 | 50 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7183615 |  |  |  | 3928 | 3.928 | 94.272 | a41: 94.272; a42: 2; a43: 2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1802451; a109: 1066; a111: 1066 | 1066 | 271.3849 |  |  | 1 | 1.4189
2018-10-03 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7187778 |  |  |  | 4163 | 4.163 | 99.912 | a41: 99.912; a42: 2; a43: 2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1803546; a109: 1095; a111: 1095 | 1095 | 263.0315 | 1.22
2018-10-03 | 70:00 | 23:00 | 4 | 2.8169 | 0 | 68 | 47.8873 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7191266 |  |  |  | 3488 | 3.488 | 83.712 | a41: 83.712; a42: 2.9; a43: 2.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1804618; a109: 1072; a111: 1072 | 1072 | 307.3394 |  |  | FLOW | MLD
2018-10-03 | 71:00 | 24:00 | 4 | 2.8169 | 1 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7195178 |  |  |  | 3912 | 3.912 | 93.888 | a41: 93.888; a42: 4; a43: 4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1805732; a109: 1114; a111: 1114 | 1114 | 284.7648 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.5 | 72.9583 | 52.2201 | 68.6667 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 104082 | 104.082 | 104.082 | a42: 5.5167; a43: 5.5167; a106: 0; a109: 27496; a111: 27496 | 27496 | 264.1763 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA / D. E. CAPIÑA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
Target Discharge Pressure set to 75 psi @ 12:01 AM
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (22%)
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 3:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4 - CLOSED @ 3:12 AM WATER ELEVATION (9.6 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 12:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 72PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 72PSI
SP2 - STOPPED @ 8:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL.
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 8:01 PM TO 12:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (17%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 68PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 70PSI

## 4
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-04
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7195178 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1805732 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-04 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7199464 |  |  |  | 4286 | 4.286 | 102.864 | a41: 102.864; a42: 5.2; a43: 5.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1806836; a109: 1104; a111: 1104 | 1104 | 257.5828 |  |  | Manual Operation | MO
2018-10-04 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7204080 |  |  |  | 4616 | 4.616 | 110.784 | a41: 110.784; a42: 6.2; a43: 6.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1807928; a109: 1092; a111: 1092 | 1092 | 236.5685 | 1.1 |  | Scheduled Shutdown | SS
2018-10-04 | 50:00 | 3:00 | 4 | 2.8169 | 6 | 70 | 49.2958 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7208686 |  |  |  | 4606 | 4.606 | 110.544 | a41: 110.544; a42: 7.8; a43: 7.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1809040; a109: 1112; a111: 1112 | 1112 | 241.4242 |  |  | Start Up Error | SU
2018-10-04 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7213132 |  |  |  | 4446 | 4.446 | 106.704 | a41: 106.704; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1810120; a109: 1080; a111: 1080 | 1080 | 242.915 |  |  | Shutdown Error | SE
2018-10-04 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7217846 |  |  |  | 4714 | 4.714 | 113.136 | a41: 113.136; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1811238; a109: 1118; a111: 1118 | 1118 | 237.1659 |  |  | Error - General | E
2018-10-04 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7222618 |  |  |  | 4772 | 4.772 | 114.528 | a41: 114.528; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1812336; a109: 1098; a111: 1098 | 1098 | 230.0922 | 1.18 |  | Power Interruption | PI
2018-10-04 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7228039 |  |  |  | 5421 | 5.421 | 130.104 | a41: 130.104; a42: 8.9; a43: 8.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1813577; a109: 1241; a111: 1241 | 1241 | 228.9246 |  |  | Water Interruption | WI
2018-10-04 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7233309 |  |  |  | 5270 | 5.27 | 126.48 | a41: 126.48; a42: 8.2; a43: 8.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1814784; a109: 1207; a111: 1207 | 1207 | 229.0323 |  |  | Equipment Maintenance | EM
2018-10-04 | 56:00 | 9:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7238227 |  |  |  | 4918 | 4.918 | 118.032 | a41: 118.032; a42: 7.6; a43: 7.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1815988; a109: 1204; a111: 1204 | 1204 | 244.815
2018-10-04 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7242847 |  |  |  | 4620 | 4.62 | 110.88 | a41: 110.88; a42: 6.9; a43: 6.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1817170; a109: 1182; a111: 1182 | 1182 | 255.8442 | 1.2
2018-10-04 | 58:00 | 11:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7247251 |  |  |  | 4404 | 4.404 | 105.696 | a41: 105.696; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1818335; a109: 1165; a111: 1165 | 1165 | 264.5322 |  |  | UNITS
2018-10-04 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7251752 |  |  |  | 4501 | 4.501 | 108.024 | a41: 108.024; a42: 5.7; a43: 5.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1819564; a109: 1229; a111: 1229 | 1229 | 273.0504 |  |  | PRESSURE | Atmospheric Pressure
2018-10-04 | 60:00 | 13:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7256059 |  |  |  | 4307 | 4.307 | 103.368 | a41: 103.368; a42: 5.1; a43: 5.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1820739; a109: 1175; a111: 1175 | 1175 | 272.8117 |  |  | m of H2O | 14.7
2018-10-04 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7260268 |  |  |  | 4209 | 4.209 | 101.016 | a41: 101.016; a42: 4.6; a43: 4.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1821882; a109: 1143; a111: 1143 | 1143 | 271.5609 | 1.15 |  | psi | 10.36
2018-10-04 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 70 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7264754 |  |  |  | 4486 | 4.486 | 107.664 | a41: 107.664; a42: 4.1; a43: 4.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1017; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.46%; a96: DEF; a107: 1823052; a109: 1170; a111: 1170 | 1170 | 260.8114 |  |  | bar | 1.0132
2018-10-04 | 63:00 | 16:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7269318 |  |  |  | 4564 | 4.564 | 109.536 | a41: 109.536; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: DEF; a107: 1824218; a109: 1166; a111: 1166 | 1166 | 255.4777 |  |  | atm | 1
2018-10-04 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7273643 |  |  |  | 4325 | 4.325 | 103.8 | a41: 103.8; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: DEF; a107: 1825366; a109: 1148; a111: 1148 | 1148 | 265.4335 |  |  | kPA | 101.325
2018-10-04 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7277993 |  |  |  | 4350 | 4.35 | 104.4 | a41: 104.4; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1826531; a109: 1165; a111: 1165 | 1165 | 267.8161 | 1.03
2018-10-04 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 68 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7282427 |  |  |  | 4434 | 4.434 | 106.416 | a41: 106.416; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1827713; a109: 1182; a111: 1182 | 1182 | 266.5765 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-04 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 69 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7286710 |  |  |  | 4283 | 4.283 | 102.792 | a41: 102.792; a42: 2.1; a43: 2.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1828871; a109: 1158; a111: 1158 | 1158 | 270.3712 |  |  | m of H2O | psi
2018-10-04 | 68:00 | 21:00 | 4 | 2.8169 | -3 | 72 | 50.7042 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7290760 |  |  |  | 4050 | 4.05 | 97.2 | a41: 97.2; a42: 2; a43: 2; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1829949; a109: 1078; a111: 1078 | 1078 | 266.1728 |  |  | 1 | 1.4189
2018-10-04 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7294994 |  |  |  | 4234 | 4.234 | 101.616 | a41: 101.616; a42: 2; a43: 2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1831044; a109: 1095; a111: 1095 | 1095 | 258.6207 | 1.16
2018-10-04 | 70:00 | 23:00 | 4 | 2.8169 | 1 | 68 | 47.8873 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7298458 |  |  |  | 3464 | 3.464 | 83.136 | a41: 83.136; a42: 3.1; a43: 3.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1832142; a109: 1098; a111: 1098 | 1098 | 316.9746 |  |  | FLOW | MLD
2018-10-04 | 71:00 | 24:00 | 4 | 2.8169 | 2 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7302510 |  |  |  | 4052 | 4.052 | 97.248 | a41: 97.248; a42: 4.6; a43: 4.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1833286; a109: 1144; a111: 1144 | 1144 | 282.3297 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.9583 | 73.9583 | 52.0833 | 71.0833 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 107332 | 107.332 | 107.332 | a42: 5.475; a43: 5.475; a106: 0; a109: 27554; a111: 27554 | 27554 | 256.7175 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | PAUL LABIAN / REY PROVIDENCIA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (22%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 70PSI
XCV4 - CLOSED @ 3:50 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 81PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 77PSI
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 78PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
SP2 - STOPPED @ 8:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 12:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (17%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 68PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI

## 5
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-05
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7302510 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1833286 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-05 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7306444 |  |  |  | 3934 | 3.934 | 94.416 | a41: 94.416; a42: 5.8; a43: 5.8; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1834392; a109: 1106; a111: 1106 | 1106 | 281.1388 |  |  | Manual Operation | MO
2018-10-05 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7310322 |  |  |  | 3878 | 3.878 | 93.072 | a41: 93.072; a42: 7.2; a43: 7.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1835500; a109: 1108; a111: 1108 | 1108 | 285.7143 | 1.1 |  | Scheduled Shutdown | SS
2018-10-05 | 50:00 | 3:00 | 4 | 2.8169 | 7 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7314334 |  |  |  | 4012 | 4.012 | 96.288 | a41: 96.288; a42: 8.5; a43: 8.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1836609; a109: 1109; a111: 1109 | 1109 | 276.4207 |  |  | Start Up Error | SU
2018-10-05 | 51:00 | 4:00 | 4 | 2.8169 | 9 | 81 | 57.0423 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7318752 |  |  |  | 4418 | 4.418 | 106.032 | a41: 106.032; a42: 9.8; a43: 9.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1837730; a109: 1121; a111: 1121 | 1121 | 253.7347 |  |  | Shutdown Error | SE
2018-10-05 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 77 | 54.2254 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7323038 |  |  |  | 4286 | 4.286 | 102.864 | a41: 102.864; a42: 9.8; a43: 9.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1838784; a109: 1054; a111: 1054 | 1054 | 245.9169 |  |  | Error - General | E
2018-10-05 | 53:00 | 6:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7327976 |  |  |  | 4938 | 4.938 | 118.512 | a41: 118.512; a42: 9.8; a43: 9.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1839904; a109: 1120; a111: 1120 | 1120 | 226.8125 | 1.16 |  | Power Interruption | PI
2018-10-05 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7333169 |  |  |  | 5193 | 5.193 | 124.632 | a41: 124.632; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1841097; a109: 1193; a111: 1193 | 1193 | 229.7323 |  |  | Water Interruption | WI
2018-10-05 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7337959 |  |  |  | 4790 | 4.79 | 114.96 | a41: 114.96; a42: 8.6; a43: 8.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1842283; a109: 1186; a111: 1186 | 1186 | 247.5992 |  |  | Equipment Maintenance | EM
2018-10-05 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7342493 |  |  |  | 4534 | 4.534 | 108.816 | a41: 108.816; a42: 8; a43: 8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1028; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.39%; a89: 0%; a96: DEF; a107: 1843471; a109: 1188; a111: 1188 | 1188 | 262.0203
2018-10-05 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7346926 |  |  |  | 4433 | 4.433 | 106.392 | a41: 106.392; a42: 7.3; a43: 7.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: DEF; a107: 1844668; a109: 1197; a111: 1197 | 1197 | 270.0203 | 1.21
2018-10-05 | 58:00 | 11:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7351339 |  |  |  | 4413 | 4.413 | 105.912 | a41: 105.912; a42: 6.7; a43: 6.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: DEF; a107: 1845860; a109: 1192; a111: 1192 | 1192 | 270.111 |  |  | UNITS
2018-10-05 | 59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7355630 |  |  |  | 4291 | 4.291 | 102.984 | a41: 102.984; a42: 6.1; a43: 6.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1028; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.39%; a89: 0%; a96: DEF; a107: 1847038; a109: 1178; a111: 1178 | 1178 | 274.5281 |  |  | PRESSURE | Atmospheric Pressure
2018-10-05 | 60:00 | 13:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7359924 |  |  |  | 4294 | 4.294 | 103.056 | a41: 103.056; a42: 5.5; a43: 5.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: DEF; a107: 1848216; a109: 1178; a111: 1178 | 1178 | 274.3363 |  |  | m of H2O | 14.7
2018-10-05 | 61:00 | 14:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7364200 |  |  |  | 4276 | 4.276 | 102.624 | a41: 102.624; a42: 5; a43: 5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1849399; a109: 1183; a111: 1183 | 1183 | 276.6604 | 1.13 |  | psi | 10.36
2018-10-05 | 62:00 | 15:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7368369 |  |  |  | 4169 | 4.169 | 100.056 | a41: 100.056; a42: 4.6; a43: 4.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: DEF; a107: 1850540; a109: 1141; a111: 1141 | 1141 | 273.6867 |  |  | bar | 1.0132
2018-10-05 | 63:00 | 16:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7372803 |  |  |  | 4434 | 4.434 | 106.416 | a41: 106.416; a42: 4.2; a43: 4.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1851713; a109: 1173; a111: 1173 | 1173 | 264.5467 |  |  | atm | 1
2018-10-05 | 64:00 | 17:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7377264 |  |  |  | 4461 | 4.461 | 107.064 | a41: 107.064; a42: 3.8; a43: 3.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1852886; a109: 1173; a111: 1173 | 1173 | 262.9455 |  |  | kPA | 101.325
2018-10-05 | 65:00 | 18:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7381700 |  |  |  | 4436 | 4.436 | 106.464 | a41: 106.464; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: DEF; a107: 1854026; a109: 1140; a111: 1140 | 1140 | 256.9883 | 0.96
2018-10-05 | 66:00 | 19:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7386360 |  |  |  | 4660 | 4.66 | 111.84 | a41: 111.84; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1855209; a109: 1183; a111: 1183 | 1183 | 253.8627 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-05 | 67:00 | 20:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 69 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7390817 |  |  |  | 4457 | 4.457 | 106.968 | a41: 106.968; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1856378; a109: 1169; a111: 1169 | 1169 | 262.284 |  |  | m of H2O | psi
2018-10-05 | 68:00 | 21:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 70 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7395442 |  |  |  | 4625 | 4.625 | 111 | a41: 111; a42: 2.4; a43: 2.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: DEF; a107: 1857531; a109: 1153; a111: 1153 | 1153 | 249.2973 |  |  | 1 | 1.4189
2018-10-05 | 69:00 | 22:00 | 4 | 2.8169 | -3 | 75 | 52.8169 | 72 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7400235 |  |  |  | 4793 | 4.793 | 115.032 | a41: 115.032; a42: 2.1; a43: 2.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: DEF; a107: 1858698; a109: 1167; a111: 1167 | 1167 | 243.4801 | 1.08
2018-10-05 | 70:00 | 23:00 | 4 | 2.8169 | -1 | 70 | 49.2958 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7404603 |  |  |  | 4368 | 4.368 | 104.832 | a41: 104.832; a42: 2..6; a43: 2..6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1859807; a109: 1109; a111: 1109 | 1109 | 253.8919 |  |  | FLOW | MLD
2018-10-05 | 71:00 | 24:00 | 4 | 2.8169 | 1 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7408666 |  |  |  | 4063 | 4.063 | 97.512 | a41: 97.512; a42: 3.7; a43: 3.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1860909; a109: 1102; a111: 1102 | 1102 | 271.2282 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.9167 | 74.2917 | 52.3181 | 72.125 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 106156 | 106.156 | 106.156 | a42: 5.9652; a43: 5.9652; a106: 0; a109: 27623; a111: 27623 | 27623 | 260.2114 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | D.E. CAPIÑA / J. LLAGUNO
| 2pm - 10pm | P.LABIAN / A. RAYALA II
| 10pm - 6am | REY PROVIDENCIA/ GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (22%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
XCV4 - CLOSED @ 3:50 AM WATER ELEVATION (9.8 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 81PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 77PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 80 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.1 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:00 PM AS PER SCHEDULE/ ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:00 PM AS PER SCHEDULE/ ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:00 AM AS PER SCHEDULE/ ACTUAL READING 71PSI

## 6
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-06
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7408666 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1860909 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-06 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 68 | 47.8873 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7412499 |  |  |  | 3833 | 3.833 | 91.992 | a41: 91.992; a42: 5.4; a43: 5.4; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1862023; a109: 1114; a111: 1114 | 1114 | 290.634 |  |  | Manual Operation | MO
2018-10-06 | 49:00 | 2:00 | 4 | 2.8169 | 4 | 68 | 47.8873 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7416414 |  |  |  | 3915 | 3.915 | 93.96 | a41: 93.96; a42: 7.2; a43: 7.2; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1863155; a109: 1132; a111: 1132 | 1132 | 289.1443 | 0.98 |  | Scheduled Shutdown | SS
2018-10-06 | 50:00 | 3:00 | 4 | 2.8169 | 6 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7420344 |  |  |  | 3930 | 3.93 | 94.32 | a41: 94.32; a42: 9; a43: 9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1864260; a109: 1105; a111: 1105 | 1105 | 281.1705 |  |  | Start Up Error | SU
2018-10-06 | 51:00 | 4:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7424388 |  |  |  | 4044 | 4.044 | 97.056 | a41: 97.056; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1865281; a109: 1021; a111: 1021 | 1021 | 252.4728 |  |  | Shutdown Error | SE
2018-10-06 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7428490 |  |  |  | 4102 | 4.102 | 98.448 | a41: 98.448; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1866350; a109: 1069; a111: 1069 | 1069 | 260.6046 |  |  | Error - General | E
2018-10-06 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 79 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7433115 |  |  |  | 4625 | 4.625 | 111 | a41: 111; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1867490; a109: 1140; a111: 1140 | 1140 | 246.4865 | 1.03 |  | Power Interruption | PI
2018-10-06 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 79 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7437811 |  |  |  | 4696 | 4.696 | 112.704 | a41: 112.704; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1017; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.46%; a96: DEF; a107: 1868603; a109: 1113; a111: 1113 | 1113 | 237.0102 |  |  | Water Interruption | WI
2018-10-06 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7442756 |  |  |  | 4945 | 4.945 | 118.68 | a41: 118.68; a42: 8.8; a43: 8.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1869814; a109: 1211; a111: 1211 | 1211 | 244.8938 |  |  | Equipment Maintenance | EM
2018-10-06 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7447366 |  |  |  | 4610 | 4.61 | 110.64 | a41: 110.64; a42: 8.1; a43: 8.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1871005; a109: 1191; a111: 1191 | 1191 | 258.3514
2018-10-06 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7451938 |  |  |  | 4572 | 4.572 | 109.728 | a41: 109.728; a42: 7.4; a43: 7.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1872198; a109: 1193; a111: 1193 | 1193 | 260.9361 | 1.1
2018-10-06 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7456275 |  |  |  | 4337 | 4.337 | 104.088 | a41: 104.088; a42: 6.8; a43: 6.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1873410; a109: 1212; a111: 1212 | 1212 | 279.4558 |  |  | UNITS
2018-10-06 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7460326 |  |  |  | 4051 | 4.051 | 97.224 | a41: 97.224; a42: 6.1; a43: 6.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1874600; a109: 1190; a111: 1190 | 1190 | 293.7546 |  |  | PRESSURE | Atmospheric Pressure
2018-10-06 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 75 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7464562 |  |  |  | 4236 | 4.236 | 101.664 | a41: 101.664; a42: 5.5; a43: 5.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1875788; a109: 1188; a111: 1188 | 1188 | 280.4533 |  |  | m of H2O | 14.7
2018-10-06 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7468685 |  |  |  | 4123 | 4.123 | 98.952 | a41: 98.952; a42: 4.9; a43: 4.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1876934; a109: 1146; a111: 1146 | 1146 | 277.9529 | 1.12 |  | psi | 10.36
2018-10-06 | 62:00 | 15:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7472737 |  |  |  | 4052 | 4.052 | 97.248 | a41: 97.248; a42: 4.4; a43: 4.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: DEF; a107: 1878096; a109: 1162; a111: 1162 | 1162 | 286.772 |  |  | bar | 1.0132
2018-10-06 | 63:00 | 16:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7477052 |  |  |  | 4315 | 4.315 | 103.56 | a41: 103.56; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: DEF; a107: 1879276; a109: 1180; a111: 1180 | 1180 | 273.4647 |  |  | atm | 1
2018-10-06 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7481327 |  |  |  | 4275 | 4.275 | 102.6 | a41: 102.6; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1880440; a109: 1164; a111: 1164 | 1164 | 272.2807 |  |  | kPA | 101.325
2018-10-06 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7485785 |  |  |  | 4458 | 4.458 | 106.992 | a41: 106.992; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 1881624; a109: 1184; a111: 1184 | 1184 | 265.59 | 1.05
2018-10-06 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7490018 |  |  |  | 4233 | 4.233 | 101.592 | a41: 101.592; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 1882793; a109: 1169; a111: 1169 | 1169 | 276.1635 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-06 | 67:00 | 20:00 | 4 | 2.8169 | -2 | 70 | 49.2958 | 67 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7494217 |  |  |  | 4199 | 4.199 | 100.776 | a41: 100.776; a42: 2; a43: 2; a47: 3B; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1883924; a109: 1131; a111: 1131 | 1131 | 269.3498 |  |  | m of H2O | psi
2018-10-06 | 68:00 | 21:00 | 4 | 2.8169 | -3 | 71 | 50 | 69 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7498259 |  |  |  | 4042 | 4.042 | 97.008 | a41: 97.008; a42: 2; a43: 2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1885008; a109: 1084; a111: 1084 | 1084 | 268.1841 |  |  | 1 | 1.4189
2018-10-06 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 69 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7502844 |  |  |  | 4585 | 4.585 | 110.04 | a41: 110.04; a42: 2; a43: 2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1886130; a109: 1122; a111: 1122 | 1122 | 244.711 | 1.14
2018-10-06 | 70:00 | 23:00 | 4 | 2.8169 | 0 | 69 | 48.5915 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7506548 |  |  |  | 3704 | 3.704 | 88.896 | a41: 88.896; a42: 2.8; a43: 2.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1887206; a109: 1076; a111: 1076 | 1076 | 290.4968 |  |  | FLOW | MLD
2018-10-06 | 71:00 | 24:00 | 4 | 2.8169 | 1 | 71 | 50 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7510606 |  |  |  | 4058 | 4.058 | 97.392 | a41: 97.392; a42: 3.8; a43: 3.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 1888314; a109: 1108; a111: 1108 | 1108 | 273.0409 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.5 | 73.5 | 51.7606 | 72.5417 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 101940 | 101.94 | 101.94 | a42: 5.6667; a43: 5.6667; a106: 0; a109: 27405; a111: 27405 | 27405 | 268.8346 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | D.E. CAPIÑA / A.RAYALA II
| 2pm - 10pm | P. LABIAN / J. LLAGUNO
| 10pm - 6am | FIDEL RAMOS / REY PROVIDENCIA
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (22%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 68PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
XCV4 - CLOSED @ 3:16 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 80PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 79 PSI
SP2 - STARTED @ 6:40 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @11:01 AM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @12:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL.
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 70PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (14%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 69PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI

## 7
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-07
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7510606 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1888314 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-07 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7514412 |  |  |  | 3806 | 3.806 | 91.344 | a41: 91.344; a42: 4.8; a43: 4.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1889410; a109: 1096; a111: 1096 | 1096 | 287.9664 |  |  | Manual Operation | MO
2018-10-07 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7518254 |  |  |  | 3842 | 3.842 | 92.208 | a41: 92.208; a42: 6.2; a43: 6.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1890536; a109: 1126; a111: 1126 | 1126 | 293.0765 | 1.1 |  | Scheduled Shutdown | SS
2018-10-07 | 50:00 | 3:00 | 4 | 2.8169 | 7 | 71 | 50 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7522532 |  |  |  | 4278 | 4.278 | 102.672 | a41: 102.672; a42: 7.6; a43: 7.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1891626; a109: 1090; a111: 1090 | 1090 | 254.792 |  |  | Start Up Error | SU
2018-10-07 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 71 | 50 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7526834 |  |  |  | 4302 | 4.302 | 103.248 | a41: 103.248; a42: 9.1; a43: 9.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1892740; a109: 1114; a111: 1114 | 1114 | 258.9493 |  |  | Shutdown Error | SE
2018-10-07 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7530942 |  |  |  | 4108 | 4.108 | 98.592 | a41: 98.592; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1893796; a109: 1056; a111: 1056 | 1056 | 257.0594 |  |  | Error - General | E
2018-10-07 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7535466 |  |  |  | 4524 | 4.524 | 108.576 | a41: 108.576; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1894932; a109: 1136; a111: 1136 | 1136 | 251.1052 | 1.18 |  | Power Interruption | PI
2018-10-07 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7540131 |  |  |  | 4665 | 4.665 | 111.96 | a41: 111.96; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1896054; a109: 1122; a111: 1122 | 1122 | 240.5145 |  |  | Water Interruption | WI
2018-10-07 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7545021 |  |  |  | 4890 | 4.89 | 117.36 | a41: 117.36; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 1897214; a109: 1160; a111: 1160 | 1160 | 237.2188 |  |  | Equipment Maintenance | EM
2018-10-07 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7549858 |  |  |  | 4837 | 4.837 | 116.088 | a41: 116.088; a42: 8.5; a43: 8.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 1898455; a109: 1241; a111: 1241 | 1241 | 256.564
2018-10-07 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7554438 |  |  |  | 4580 | 4.58 | 109.92 | a41: 109.92; a42: 7.8; a43: 7.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 1899645; a109: 1190; a111: 1190 | 1190 | 259.8253 | 1.2
2018-10-07 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7558792 |  |  |  | 4354 | 4.354 | 104.496 | a41: 104.496; a42: 7.1; a43: 7.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 1900839; a109: 1194; a111: 1194 | 1194 | 274.2306 |  |  | UNITS
2018-10-07 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7563067 |  |  |  | 4275 | 4.275 | 102.6 | a41: 102.6; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 1902033; a109: 1194; a111: 1194 | 1194 | 279.2982 |  |  | PRESSURE | Atmospheric Pressure
2018-10-07 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7567173 |  |  |  | 4106 | 4.106 | 98.544 | a41: 98.544; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 1903220; a109: 1187; a111: 1187 | 1187 | 289.0891 |  |  | m of H2O | 14.7
2018-10-07 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7571253 |  |  |  | 4080 | 4.08 | 97.92 | a41: 97.92; a42: 5.2; a43: 5.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 1904358; a109: 1138; a111: 1138 | 1138 | 278.9216 | 1.19 |  | psi | 10.36
2018-10-07 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7575602 |  |  |  | 4349 | 4.349 | 104.376 | a41: 104.376; a42: 4.6; a43: 4.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 1905557; a109: 1199; a111: 1199 | 1199 | 275.6956 |  |  | bar | 1.0132
2018-10-07 | 63:00 | 16:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7579915 |  |  |  | 4313 | 4.313 | 103.512 | a41: 103.512; a42: 4; a43: 4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 1906731; a109: 1174; a111: 1174 | 1174 | 272.2003 |  |  | atm | 1
2018-10-07 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7584192 |  |  |  | 4277 | 4.277 | 102.648 | a41: 102.648; a42: 3.5; a43: 3.5; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1017; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.46%; a89: 0%; a96: 0%; a107: 1907896; a109: 1165; a111: 1165 | 1165 | 272.3872 |  |  | kPA | 101.325
2018-10-07 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7588418 |  |  |  | 4226 | 4.226 | 101.424 | a41: 101.424; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 1909059; a109: 1163; a111: 1163 | 1163 | 275.2011 | 1.09
2018-10-07 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7592872 |  |  |  | 4454 | 4.454 | 106.896 | a41: 106.896; a42: 2.6; a43: 2.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 1910228; a109: 1169; a111: 1169 | 1169 | 262.4607 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-07 | 67:00 | 20:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 69 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7597172 |  |  |  | 4300 | 4.3 | 103.2 | a41: 103.2; a42: 2.1; a43: 2.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 1911399; a109: 1171; a111: 1171 | 1171 | 272.3256 |  |  | m of H2O | psi
2018-10-07 | 68:00 | 21:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 70 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7601422 |  |  |  | 4250 | 4.25 | 102 | a41: 102; a42: 1.8; a43: 1.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1025; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.13%; a89: 0%; a96: 0%; a107: 1912555; a109: 1156; a111: 1156 | 1156 | 272 |  |  | 1 | 1.4189
2018-10-07 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 70 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7606044 |  |  |  | 4622 | 4.622 | 110.928 | a41: 110.928; a42: 1.5; a43: 1.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1025; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.13%; a89: 0%; a96: 0%; a107: 1913738; a109: 1183; a111: 1183 | 1183 | 255.9498 | 1.16
2018-10-07 | 70:00 | 23:00 | 4 | 2.8169 | 1 | 68 | 47.8873 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7609422 |  |  |  | 3378 | 3.378 | 81.072 | a41: 81.072; a42: 2.4; a43: 2.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1914822; a109: 1084; a111: 1084 | 1084 | 320.8999 |  |  | FLOW | MLD
2018-10-07 | 71:00 | 24:00 | 4 | 2.8169 | 2 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7613568 |  |  |  | 4146 | 4.146 | 99.504 | a41: 99.504; a42: 3.7; a43: 3.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1915964; a109: 1142; a111: 1142 | 1142 | 275.4462 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.7083 | 73.7083 | 51.9073 | 72.0833 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 102962 | 102.962 | 102.962 | a42: 5.6417; a43: 5.6417; a106: 0; a109: 27650; a111: 27650 | 27650 | 268.5457 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | P. LABIAN / D. E. CAPIÑA
| 10pm - 6am | FIDEL RAMOS / REY PROVIDENCIA
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (22%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI
XCV4 - CLOSED @ 4:38 AM WATER ELEVATION (9.5 M)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 81PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 81 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 78 PSI
SP1 - STARTED @ 7:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 76PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 68PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI

## 8
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-08
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7613568 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1915964 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-08 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 7617236 |  |  |  | 3668 | 3.668 | 88.032 | a41: 88.032; a42: 5; a43: 5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1917036; a109: 1072; a111: 1072 | 1072 | 292.2574 |  |  | Manual Operation | MO
2018-10-08 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7621222 |  |  |  | 3986 | 3.986 | 95.664 | a41: 95.664; a42: 6.3; a43: 6.3; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1918148; a109: 1112; a111: 1112 | 1112 | 278.9764 | 1.17 |  | Scheduled Shutdown | SS
2018-10-08 | 50:00 | 3:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7625246 |  |  |  | 4024 | 4.024 | 96.576 | a41: 96.576; a42: 7.5; a43: 7.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1919264; a109: 1116; a111: 1116 | 1116 | 277.336 |  |  | Start Up Error | SU
2018-10-08 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 73 | 51.4085 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7629360 |  |  |  | 4114 | 4.114 | 98.736 | a41: 98.736; a42: 8.8; a43: 8.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1920392; a109: 1128; a111: 1128 | 1128 | 274.1857 |  |  | Shutdown Error | SE
2018-10-08 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7633518 |  |  |  | 4158 | 4.158 | 99.792 | a41: 99.792; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1921458; a109: 1066; a111: 1066 | 1066 | 256.3733 |  |  | Error - General | E
2018-10-08 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7638109 |  |  |  | 4591 | 4.591 | 110.184 | a41: 110.184; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1922567; a109: 1109; a111: 1109 | 1109 | 241.5596 | 1.15 |  | Power Interruption | PI
2018-10-08 | 54:00 | 7:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7643351 |  |  |  | 5242 | 5.242 | 125.808 | a41: 125.808; a42: 8.9; a43: 8.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 1923791; a109: 1224; a111: 1224 | 1224 | 233.4987 |  |  | Water Interruption | WI
2018-10-08 | 55:00 | 8:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7648421 |  |  |  | 5070 | 5.07 | 121.68 | a41: 121.68; a42: 8.3; a43: 8.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 1925002; a109: 1211; a111: 1211 | 1211 | 238.856 |  |  | Equipment Maintenance | EM
2018-10-08 | 56:00 | 9:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7652986 |  |  |  | 4565 | 4.565 | 109.56 | a41: 109.56; a42: 7.6; a43: 7.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1046; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.9%; a96: 0%; a107: 1926176; a109: 1174; a111: 1174 | 1174 | 257.1742
2018-10-08 | 57:00 | 10:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7657280 |  |  |  | 4294 | 4.294 | 103.056 | a41: 103.056; a42: 6.9; a43: 6.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 1927402; a109: 1226; a111: 1226 | 1226 | 285.5147 | 1.1
2018-10-08 | 58:00 | 11:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7661550 |  |  |  | 4270 | 4.27 | 102.48 | a41: 102.48; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 1928615; a109: 1213; a111: 1213 | 1213 | 284.0749 |  |  | UNITS
2018-10-08 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 71 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7665570 |  |  |  | 4020 | 4.02 | 96.48 | a41: 96.48; a42: 5.7; a43: 5.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 1929766; a109: 1151; a111: 1151 | 1151 | 286.3184 |  |  | PRESSURE | Atmospheric Pressure
2018-10-08 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7669788 |  |  |  | 4218 | 4.218 | 101.232 | a41: 101.232; a42: 5.1; a43: 5.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 1930939; a109: 1173; a111: 1173 | 1173 | 278.0939 |  |  | m of H2O | 14.7
2018-10-08 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 71 | 50 | 70 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7673535 |  |  |  | 3747 | 3.747 | 89.928 | a41: 89.928; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1017; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.46%; a96: 0%; a107: 1932160; a109: 1221; a111: 1221 | 1221 | 325.8607 | 1.17 |  | psi | 10.36
2018-10-08 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 71 | 50 | 70 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7677203 |  |  |  | 3668 | 3.668 | 88.032 | a41: 88.032; a42: 3.8; a43: 3.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1933296; a109: 1136; a111: 1136 | 1136 | 309.7056 |  |  | bar | 1.0132
2018-10-08 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7681530 |  |  |  | 4327 | 4.327 | 103.848 | a41: 103.848; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1934459; a109: 1163; a111: 1163 | 1163 | 268.7774 |  |  | atm | 1
2018-10-08 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7685832 |  |  |  | 4302 | 4.302 | 103.248 | a41: 103.248; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1935624; a109: 1165; a111: 1165 | 1165 | 270.8043 |  |  | kPA | 101.325
2018-10-08 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7690191 |  |  |  | 4359 | 4.359 | 104.616 | a41: 104.616; a42: 2.6; a43: 2.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1936801; a109: 1177; a111: 1177 | 1177 | 270.0161 | 1.14
2018-10-08 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7694464 |  |  |  | 4273 | 4.273 | 102.552 | a41: 102.552; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 1937953; a109: 1152; a111: 1152 | 1152 | 269.5998 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-08 | 67:00 | 20:00 | 4 | 2.8169 | -2 | 72 | 50.7042 | 71 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7698588 |  |  |  | 4124 | 4.124 | 98.976 | a41: 98.976; a42: 1.9; a43: 1.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 1939114; a109: 1161; a111: 1161 | 1161 | 281.5228 |  |  | m of H2O | psi
2018-10-08 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 72 | 50.7042 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7702615 |  |  |  | 4027 | 4.027 | 96.648 | a41: 96.648; a42: 1.6; a43: 1.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 1940268; a109: 1154; a111: 1154 | 1154 | 286.5657 |  |  | 1 | 1.4189
2018-10-08 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7706780 |  |  |  | 4165 | 4.165 | 99.96 | a41: 99.96; a42: 1.4; a43: 1.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1941427; a109: 1159; a111: 1159 | 1159 | 278.2713 | 0.8
2018-10-08 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7710605 |  |  |  | 3825 | 3.825 | 91.8 | a41: 91.8; a42: 1.8; a43: 1.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1942492; a109: 1065; a111: 1065 | 1065 | 278.4314 |  |  | FLOW | MLD
2018-10-08 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7714333 |  |  |  | 3728 | 3.728 | 89.472 | a41: 89.472; a42: 3; a43: 3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1943624; a109: 1132; a111: 1132 | 1132 | 303.6481 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.5 | 73.5417 | 51.7899 | 71.75 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 100765 | 100.765 | 100.765 | a42: 5.1917; a43: 5.1917; a106: 0; a109: 27660; a111: 27660 | 27660 | 274.5001 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | REY PROVIDENCIA / J. LLAGUNO
| 2pm - 10pm | P. LABIAN / D. E. CAPIÑA
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (22%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
XCV4 - CLOSED @ 4:26 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 79PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 81 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 72PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 68PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI

## 9
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-09
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7714333 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1943624 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-09 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7718038 |  |  |  | 3705 | 3.705 | 88.92 | a41: 88.92; a42: 4.6; a43: 4.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1944749; a109: 1125; a111: 1125 | 1125 | 303.6437 |  |  | Manual Operation | MO
2018-10-09 | 49:00 | 2:00 | 4 | 2.8169 | 4 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7721933 |  |  |  | 3895 | 3.895 | 93.48 | a41: 93.48; a42: 6.1; a43: 6.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1945850; a109: 1101; a111: 1101 | 1101 | 282.6701 | 1.03 |  | Scheduled Shutdown | SS
2018-10-09 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7726007 |  |  |  | 4074 | 4.074 | 97.776 | a41: 97.776; a42: 7.8; a43: 7.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1946969; a109: 1119; a111: 1119 | 1119 | 274.6686 |  |  | Start Up Error | SU
2018-10-09 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7730220 |  |  |  | 4213 | 4.213 | 101.112 | a41: 101.112; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1948089; a109: 1120; a111: 1120 | 1120 | 265.8438 |  |  | Shutdown Error | SE
2018-10-09 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7734498 |  |  |  | 4278 | 4.278 | 102.672 | a41: 102.672; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1949128; a109: 1039; a111: 1039 | 1039 | 242.8705 |  |  | Error - General | E
2018-10-09 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7739703 |  |  |  | 5205 | 5.205 | 124.92 | a41: 124.92; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1950272; a109: 1144; a111: 1144 | 1144 | 219.7887 | 1.09 |  | Power Interruption | PI
2018-10-09 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7745057 |  |  |  | 5354 | 5.354 | 128.496 | a41: 128.496; a42: 8.9; a43: 8.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 1951466; a109: 1194; a111: 1194 | 1194 | 223.0108 |  |  | Water Interruption | WI
2018-10-09 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7749782 |  |  |  | 4725 | 4.725 | 113.4 | a41: 113.4; a42: 8.3; a43: 8.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 1952648; a109: 1182; a111: 1182 | 1182 | 250.1587 |  |  | Equipment Maintenance | EM
2018-10-09 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7754240 |  |  |  | 4458 | 4.458 | 106.992 | a41: 106.992; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 1953848; a109: 1200; a111: 1200 | 1200 | 269.179
2018-10-09 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7758669 |  |  |  | 4429 | 4.429 | 106.296 | a41: 106.296; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 1955051; a109: 1203; a111: 1203 | 1203 | 271.6189 | 0.98
2018-10-09 | 58:00 | 11:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7763139 |  |  |  | 4470 | 4.47 | 107.28 | a41: 107.28; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 1956242; a109: 1191; a111: 1191 | 1191 | 266.443 |  |  | UNITS
2018-10-09 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7767367 |  |  |  | 4228 | 4.228 | 101.472 | a41: 101.472; a42: 5.9; a43: 5.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 1957433; a109: 1191; a111: 1191 | 1191 | 281.6935 |  |  | PRESSURE | Atmospheric Pressure
2018-10-09 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7771695 |  |  |  | 4328 | 4.328 | 103.872 | a41: 103.872; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 1958622; a109: 1189; a111: 1189 | 1189 | 274.7227 |  |  | m of H2O | 14.7
2018-10-09 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7776081 |  |  |  | 4386 | 4.386 | 105.264 | a41: 105.264; a42: 4.9; a43: 4.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 1959821; a109: 1199; a111: 1199 | 1199 | 273.3698 | 1.07 |  | psi | 10.36
2018-10-09 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7780247 |  |  |  | 4166 | 4.166 | 99.984 | a41: 99.984; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 1960957; a109: 1136; a111: 1136 | 1136 | 272.6836 |  |  | bar | 1.0132
2018-10-09 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7784389 |  |  |  | 4142 | 4.142 | 99.408 | a41: 99.408; a42: 4.1; a43: 4.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1004; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.37%; a89: 0%; a96: 0%; a107: 1962100; a109: 1143; a111: 1143 | 1143 | 275.9536 |  |  | atm | 1
2018-10-09 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7788741 |  |  |  | 4352 | 4.352 | 104.448 | a41: 104.448; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 1963264; a109: 1164; a111: 1164 | 1164 | 267.4632 |  |  | kPA | 101.325
2018-10-09 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7793178 |  |  |  | 4437 | 4.437 | 106.488 | a41: 106.488; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 1964432; a109: 1168; a111: 1168 | 1168 | 263.2409 | 1.01
2018-10-09 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7797546 |  |  |  | 4368 | 4.368 | 104.832 | a41: 104.832; a42: 2.9; a43: 2.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 1965589; a109: 1157; a111: 1157 | 1157 | 264.881 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-09 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 71 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7801974 |  |  |  | 4428 | 4.428 | 106.272 | a41: 106.272; a42: 2.6; a43: 2.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 1966769; a109: 1180; a111: 1180 | 1180 | 266.486 |  |  | m of H2O | psi
2018-10-09 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 72 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7806286 |  |  |  | 4312 | 4.312 | 103.488 | a41: 103.488; a42: 2.2; a43: 2.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 1967916; a109: 1147; a111: 1147 | 1147 | 266.0019 |  |  | 1 | 1.4189
2018-10-09 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7810730 |  |  |  | 4444 | 4.444 | 106.656 | a41: 106.656; a42: 2; a43: 2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 1969052; a109: 1136; a111: 1136 | 1136 | 255.6256 | 1
2018-10-09 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7814977 |  |  |  | 4247 | 4.247 | 101.928 | a41: 101.928; a42: 2.5; a43: 2.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1970177; a109: 1125; a111: 1125 | 1125 | 264.8929 |  |  | FLOW | MLD
2018-10-09 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 63 | 44.3662 | 60 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7818285 |  |  |  | 3308 | 3.308 | 79.392 | a41: 79.392; a42: 4.1; a43: 4.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1971276; a109: 1099; a111: 1099 | 1099 | 332.2249 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.75 | 73.2083 | 51.5552 | 71.4167 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 103952 | 103.952 | 103.952 | a42: 5.5542; a43: 5.5542; a106: 0; a109: 27652; a111: 27652 | 27652 | 266.0074 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | REY PROVIDENCIA / A.RAYALA II
| 2pm - 10pm | P. LABIAN / D. E. CAPIÑA
| 10pm - 6am | GEORGE HERNANNDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 69 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
XCV4 - CLOSED @ 3:55 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 72PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (11%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 64 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 63 PSI

## 10
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-10
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7818285 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1971276 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-10 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 69 | 48.5915 | 65 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7822051 |  |  |  | 3766 | 3.766 | 90.384 | a41: 90.384; a42: 5.8; a43: 5.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1972448; a109: 1172; a111: 1172 | 1172 | 311.2055 |  |  | Manual Operation | MO
2018-10-10 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7825861 |  |  |  | 3810 | 3.81 | 91.44 | a41: 91.44; a42: 7.1; a43: 7.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1973540; a109: 1092; a111: 1092 | 1092 | 286.6142 | 0.87 |  | Scheduled Shutdown | SS
2018-10-10 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7829925 |  |  |  | 4064 | 4.064 | 97.536 | a41: 97.536; a42: 8.3; a43: 8.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1974640; a109: 1100; a111: 1100 | 1100 | 270.6693 |  |  | Start Up Error | SU
2018-10-10 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7834051 |  |  |  | 4126 | 4.126 | 99.024 | a41: 99.024; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1975752; a109: 1112; a111: 1112 | 1112 | 269.5104 |  |  | Shutdown Error | SE
2018-10-10 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7838272 |  |  |  | 4221 | 4.221 | 101.304 | a41: 101.304; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1976872; a109: 1120; a111: 1120 | 1120 | 265.34 |  |  | Error - General | E
2018-10-10 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7843211 |  |  |  | 4939 | 4.939 | 118.536 | a41: 118.536; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1977931; a109: 1059; a111: 1059 | 1059 | 214.4159 | 0.9 |  | Power Interruption | PI
2018-10-10 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7848204 |  |  |  | 4993 | 4.993 | 119.832 | a41: 119.832; a42: 9; a43: 9; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 1979103; a109: 1172; a111: 1172 | 1172 | 234.7286 |  |  | Water Interruption | WI
2018-10-10 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7853139 |  |  |  | 4935 | 4.935 | 118.44 | a41: 118.44; a42: 8.4; a43: 8.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 1980304; a109: 1201; a111: 1201 | 1201 | 243.3637 |  |  | Equipment Maintenance | EM
2018-10-10 | 56:00 | 9:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7857624 |  |  |  | 4485 | 4.485 | 107.64 | a41: 107.64; a42: 7.6; a43: 7.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 1981499; a109: 1195; a111: 1195 | 1195 | 266.4437
2018-10-10 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7862150 |  |  |  | 4526 | 4.526 | 108.624 | a41: 108.624; a42: 7.1; a43: 7.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: 0%; a107: 1982719; a109: 1220; a111: 1220 | 1220 | 269.5537 | 0.92
2018-10-10 | 58:00 | 11:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7866605 |  |  |  | 4455 | 4.455 | 106.92 | a41: 106.92; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 1983920; a109: 1201; a111: 1201 | 1201 | 269.5847 |  |  | UNITS
2018-10-10 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7871020 |  |  |  | 4415 | 4.415 | 105.96 | a41: 105.96; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 1985107; a109: 1187; a111: 1187 | 1187 | 268.8562 |  |  | PRESSURE | Atmospheric Pressure
2018-10-10 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7875276 |  |  |  | 4256 | 4.256 | 102.144 | a41: 102.144; a42: 5.1; a43: 5.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 1986271; a109: 1164; a111: 1164 | 1164 | 273.4962 |  |  | m of H2O | 14.7
2018-10-10 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7879703 |  |  |  | 4427 | 4.427 | 106.248 | a41: 106.248; a42: 4.7; a43: 4.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 1987481; a109: 1210; a111: 1210 | 1210 | 273.3228 | 1.08 |  | psi | 10.36
2018-10-10 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7884008 |  |  |  | 4305 | 4.305 | 103.32 | a41: 103.32; a42: 4.3; a43: 4.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1988656; a109: 1175; a111: 1175 | 1175 | 272.9384 |  |  | bar | 1.0132
2018-10-10 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7888314 |  |  |  | 4306 | 4.306 | 103.344 | a41: 103.344; a42: 3.8; a43: 3.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 1989781; a109: 1125; a111: 1125 | 1125 | 261.2634 |  |  | atm | 1
2018-10-10 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7892984 |  |  |  | 4670 | 4.67 | 112.08 | a41: 112.08; a42: 3.5; a43: 3.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1990944; a109: 1163; a111: 1163 | 1163 | 249.0364 |  |  | kPA | 101.325
2018-10-10 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7897618 |  |  |  | 4634 | 4.634 | 111.216 | a41: 111.216; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1992110; a109: 1166; a111: 1166 | 1166 | 251.6185 | 1.01
2018-10-10 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7902280 |  |  |  | 4662 | 4.662 | 111.888 | a41: 111.888; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1993297; a109: 1187; a111: 1187 | 1187 | 254.6118 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-10 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 71 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7906736 |  |  |  | 4456 | 4.456 | 106.944 | a41: 106.944; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 1994486; a109: 1189; a111: 1189 | 1189 | 266.8312 |  |  | m of H2O | psi
2018-10-10 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 72 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7911025 |  |  |  | 4289 | 4.289 | 102.936 | a41: 102.936; a42: 2; a43: 2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 1995600; a109: 1114; a111: 1114 | 1114 | 259.7342 |  |  | 1 | 1.4189
2018-10-10 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7915877 |  |  |  | 4852 | 4.852 | 116.448 | a41: 116.448; a42: 1.8; a43: 1.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 1996779; a109: 1179; a111: 1179 | 1179 | 242.9926 | 0.81
2018-10-10 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7920060 |  |  |  | 4183 | 4.183 | 100.392 | a41: 100.392; a42: 2.3; a43: 2.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1997851; a109: 1072; a111: 1072 | 1072 | 256.2754 |  |  | FLOW | MLD
2018-10-10 | 71:00 | 24:00 | 4 | 2.8169 | -2 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7924218 |  |  |  | 4158 | 4.158 | 99.792 | a41: 99.792; a42: 3.4; a43: 3.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 1998963; a109: 1112; a111: 1112 | 1112 | 267.4363 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.5833 | 73.4167 | 51.7019 | 71.5833 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 105933 | 105.933 | 105.933 | a42: 5.5417; a43: 5.5417; a106: 0; a109: 27687; a111: 27687 | 27687 | 261.3633 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA / D. E. CAPIÑA
| 10pm - 6am | GEORGE HERNANNDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (18%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 69 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 71 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
XCV4 - CLOSED @ 3:50 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.8 ELEVATION LEVEL.
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (12%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 69 PSI

## 11
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-11
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 7924218 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 1998963 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-11 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 67 | 47.1831 | 65 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7927988 |  |  |  | 3770 | 3.77 | 90.48 | a41: 90.48; a42: 5.3; a43: 5.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2000071; a109: 1108; a111: 1108 | 1108 | 293.8992 |  |  | Manual Operation | MO
2018-10-11 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7931966 |  |  |  | 3978 | 3.978 | 95.472 | a41: 95.472; a42: 6.7; a43: 6.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2001171; a109: 1100; a111: 1100 | 1100 | 276.5209 | 1.02 |  | Scheduled Shutdown | SS
2018-10-11 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7936260 |  |  |  | 4294 | 4.294 | 103.056 | a41: 103.056; a42: 8.5; a43: 8.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2002290; a109: 1119; a111: 1119 | 1119 | 260.5962 |  |  | Start Up Error | SU
2018-10-11 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 82 | 57.7465 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7940466 |  |  |  | 4206 | 4.206 | 100.944 | a41: 100.944; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2003393; a109: 1103; a111: 1103 | 1103 | 262.2444 |  |  | Shutdown Error | SE
2018-10-11 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7944864 |  |  |  | 4398 | 4.398 | 105.552 | a41: 105.552; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2004482; a109: 1089; a111: 1089 | 1089 | 247.6126 |  |  | Error - General | E
2018-10-11 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 73 | 51.4085 | 71 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7949786 |  |  |  | 4922 | 4.922 | 118.128 | a41: 118.128; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2005563; a109: 1081; a111: 1081 | 1081 | 219.6262 | 1.05 |  | Power Interruption | PI
2018-10-11 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7954887 |  |  |  | 5101 | 5.101 | 122.424 | a41: 122.424; a42: 9.1; a43: 9.1; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 1047; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.98%; a89: 0%; a96: 0%; a107: 2006759; a109: 1196; a111: 1196 | 1196 | 234.4638 |  |  | Water Interruption | WI
2018-10-11 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7960172 |  |  |  | 5285 | 5.285 | 126.84 | a41: 126.84; a42: 8.4; a43: 8.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1048; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 88.07%; a89: 0%; a96: 0%; a107: 2007947; a109: 1188; a111: 1188 | 1188 | 224.7871 |  |  | Equipment Maintenance | EM
2018-10-11 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7965267 |  |  |  | 5095 | 5.095 | 122.28 | a41: 122.28; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1028; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.39%; a89: 0%; a96: 0%; a107: 2009159; a109: 1212; a111: 1212 | 1212 | 237.8803
2018-10-11 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7970050 |  |  |  | 4783 | 4.783 | 114.792 | a41: 114.792; a42: 7; a43: 7; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2010356; a109: 1197; a111: 1197 | 1197 | 250.2613 | 0.98
2018-10-11 | 58:00 | 11:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7974485 |  |  |  | 4435 | 4.435 | 106.44 | a41: 106.44; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2011544; a109: 1188; a111: 1188 | 1188 | 267.8692 |  |  | UNITS
2018-10-11 | 59:00 | 12:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7978975 |  |  |  | 4490 | 4.49 | 107.76 | a41: 107.76; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2012737; a109: 1193; a111: 1193 | 1193 | 265.7016 |  |  | PRESSURE | Atmospheric Pressure
2018-10-11 | 60:00 | 13:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7983440 |  |  |  | 4465 | 4.465 | 107.16 | a41: 107.16; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2013924; a109: 1187; a111: 1187 | 1187 | 265.8455 |  |  | m of H2O | 14.7
2018-10-11 | 61:00 | 14:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7987979 |  |  |  | 4539 | 4.539 | 108.936 | a41: 108.936; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2015106; a109: 1182; a111: 1182 | 1182 | 260.4098 | 1.07 |  | psi | 10.36
2018-10-11 | 62:00 | 15:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7992430 |  |  |  | 4451 | 4.451 | 106.824 | a41: 106.824; a42: 4.4; a43: 4.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2016266; a109: 1160; a111: 1160 | 1160 | 260.6156 |  |  | bar | 1.0132
2018-10-11 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 7996974 |  |  |  | 4544 | 4.544 | 109.056 | a41: 109.056; a42: 3.9; a43: 3.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2017420; a109: 1154; a111: 1154 | 1154 | 253.9613 |  |  | atm | 1
2018-10-11 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8001587 |  |  |  | 4613 | 4.613 | 110.712 | a41: 110.712; a42: 3.5; a43: 3.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1011; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.96%; a89: 0%; a96: 0%; a107: 2018577; a109: 1157; a111: 1157 | 1157 | 250.8129 |  |  | kPA | 101.325
2018-10-11 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8006057 |  |  |  | 4470 | 4.47 | 107.28 | a41: 107.28; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1011; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.96%; a89: 0%; a96: 0%; a107: 2019742; a109: 1165; a111: 1165 | 1165 | 260.6264 | 1.01
2018-10-11 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8010370 |  |  |  | 4313 | 4.313 | 103.512 | a41: 103.512; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2020902; a109: 1160; a111: 1160 | 1160 | 268.9543 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-11 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 71 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8014715 |  |  |  | 4345 | 4.345 | 104.28 | a41: 104.28; a42: 2.2; a43: 2.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1047; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.98%; a89: 0%; a96: 0%; a107: 2022068; a109: 1166; a111: 1166 | 1166 | 268.3544 |  |  | m of H2O | psi
2018-10-11 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8019312 |  |  |  | 4597 | 4.597 | 110.328 | a41: 110.328; a42: 1.7; a43: 1.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 2023237; a109: 1169; a111: 1169 | 1169 | 254.2963 |  |  | 1 | 1.4189
2018-10-11 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8024112 |  |  |  | 4800 | 4.8 | 115.2 | a41: 115.2; a42: 1.5; a43: 1.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1014; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.21%; a89: 0%; a96: 0%; a107: 2024384; a109: 1147; a111: 1147 | 1147 | 238.9583 | 0.87
2018-10-11 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8028360 |  |  |  | 4248 | 4.248 | 101.952 | a41: 101.952; a42: 2.1; a43: 2.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2025483; a109: 1099; a111: 1099 | 1099 | 258.71 |  |  | FLOW | MLD
2018-10-11 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8032525 |  |  |  | 4165 | 4.165 | 99.96 | a41: 99.96; a42: 3.1; a43: 3.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2026594; a109: 1111; a111: 1111 | 1111 | 266.7467 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.625 | 73.9167 | 52.054 | 71.7917 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 108307 | 108.307 | 108.307 | a42: 5.4875; a43: 5.4875; a106: 0; a109: 27631; a111: 27631 | 27631 | 255.1174 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA / P. LABIAN
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 67 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI
XCV4 - CLOSED @ 3:40 AM WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 82 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.5 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
XCV4 -OPENED @ 10:01 PM (12%)
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (12%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 72 PSI

## 12
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-12
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8032525 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2026594 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-12 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 68 | 47.8873 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8035980 |  |  |  | 3455 | 3.455 | 82.92 | a41: 82.92; a42: 4.8; a43: 4.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2027702; a109: 1108; a111: 1108 | 1108 | 320.6946 |  |  | Manual Operation | MO
2018-10-12 | 49:00 | 2:00 | 4 | 2.8169 | 2 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8039875 |  |  |  | 3895 | 3.895 | 93.48 | a41: 93.48; a42: 6.4; a43: 6.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2028817; a109: 1115; a111: 1115 | 1115 | 286.2644 | 0.88 |  | Scheduled Shutdown | SS
2018-10-12 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8043875 |  |  |  | 4000 | 4 | 96 | a41: 96; a42: 8; a43: 8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2029925; a109: 1108; a111: 1108 | 1108 | 277 |  |  | Start Up Error | SU
2018-10-12 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8048165 |  |  |  | 4290 | 4.29 | 102.96 | a41: 102.96; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2031022; a109: 1097; a111: 1097 | 1097 | 255.711 |  |  | Shutdown Error | SE
2018-10-12 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8052464 |  |  |  | 4299 | 4.299 | 103.176 | a41: 103.176; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2032123; a109: 1101; a111: 1101 | 1101 | 256.1061 |  |  | Error - General | E
2018-10-12 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8057316 |  |  |  | 4852 | 4.852 | 116.448 | a41: 116.448; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2033291; a109: 1168; a111: 1168 | 1168 | 240.7255 | 0.9 |  | Power Interruption | PI
2018-10-12 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8062565 |  |  |  | 5249 | 5.249 | 125.976 | a41: 125.976; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: 0%; a107: 2034401; a109: 1110; a111: 1110 | 1110 | 211.4689 |  |  | Water Interruption | WI
2018-10-12 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8067970 |  |  |  | 5405 | 5.405 | 129.72 | a41: 129.72; a42: 8.3; a43: 8.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1046; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.9%; a96: 0%; a107: 2035625; a109: 1224; a111: 1224 | 1224 | 226.457 |  |  | Equipment Maintenance | EM
2018-10-12 | 56:00 | 9:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8072779 |  |  |  | 4809 | 4.809 | 115.416 | a41: 115.416; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1047; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.98%; a96: 0%; a107: 2036792; a109: 1167; a111: 1167 | 1167 | 242.67
2018-10-12 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8077618 |  |  |  | 4839 | 4.839 | 116.136 | a41: 116.136; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1047; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.98%; a96: 0%; a107: 2038045; a109: 1253; a111: 1253 | 1253 | 258.9378 | 1.05
2018-10-12 | 58:00 | 11:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8082168 |  |  |  | 4550 | 4.55 | 109.2 | a41: 109.2; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2039197; a109: 1152; a111: 1152 | 1152 | 253.1868 |  |  | UNITS
2018-10-12 | 59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8086695 |  |  |  | 4527 | 4.527 | 108.648 | a41: 108.648; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2040383; a109: 1186; a111: 1186 | 1186 | 261.9837 |  |  | PRESSURE | Atmospheric Pressure
2018-10-12 | 60:00 | 13:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8091250 |  |  |  | 4555 | 4.555 | 109.32 | a41: 109.32; a42: 5.2; a43: 5.2; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2041575; a109: 1192; a111: 1192 | 1192 | 261.6905 |  |  | m of H2O | 14.7
2018-10-12 | 61:00 | 14:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8095894 |  |  |  | 4644 | 4.644 | 111.456 | a41: 111.456; a42: 4.6; a43: 4.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2042792; a109: 1217; a111: 1217 | 1217 | 262.0586 | 0.98 |  | psi | 10.36
2018-10-12 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8100489 |  |  |  | 4595 | 4.595 | 110.28 | a41: 110.28; a42: 4.2; a43: 4.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2043951; a109: 1159; a111: 1159 | 1159 | 252.2307 |  |  | bar | 1.0132
2018-10-12 | 63:00 | 16:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8105004 |  |  |  | 4515 | 4.515 | 108.36 | a41: 108.36; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2045093; a109: 1142; a111: 1142 | 1142 | 252.9347 |  |  | atm | 1
2018-10-12 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8109638 |  |  |  | 4634 | 4.634 | 111.216 | a41: 111.216; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2046245; a109: 1152; a111: 1152 | 1152 | 248.5973 |  |  | kPA | 101.325
2018-10-12 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8114195 |  |  |  | 4557 | 4.557 | 109.368 | a41: 109.368; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2047412; a109: 1167; a111: 1167 | 1167 | 256.0895 | 1.07
2018-10-12 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8118444 |  |  |  | 4249 | 4.249 | 101.976 | a41: 101.976; a42: 2.6; a43: 2.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2048556; a109: 1144; a111: 1144 | 1144 | 269.2398 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-12 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 71 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8122797 |  |  |  | 4353 | 4.353 | 104.472 | a41: 104.472; a42: 2.2; a43: 2.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2049723; a109: 1167; a111: 1167 | 1167 | 268.091 |  |  | m of H2O | psi
2018-10-12 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8127058 |  |  |  | 4261 | 4.261 | 102.264 | a41: 102.264; a42: 1.9; a43: 1.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2050861; a109: 1138; a111: 1138 | 1138 | 267.0735 |  |  | 1 | 1.4189
2018-10-12 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8131538 |  |  |  | 4480 | 4.48 | 107.52 | a41: 107.52; a42: 1.6; a43: 1.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2052035; a109: 1174; a111: 1174 | 1174 | 262.0536 | 1.03
2018-10-12 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8135615 |  |  |  | 4077 | 4.077 | 97.848 | a41: 97.848; a42: 2.1; a43: 2.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2053095; a109: 1060; a111: 1060 | 1060 | 259.9951 |  |  | FLOW | MLD
2018-10-12 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 68 | 47.8873 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8139400 |  |  |  | 3785 | 3.785 | 90.84 | a41: 90.84; a42: 3.1; a43: 3.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2054219; a109: 1124; a111: 1124 | 1124 | 296.9617 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.3333 | 73.0417 | 51.4378 | 71.25 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 106875 | 106.875 | 106.875 | a42: 5.4042; a43: 5.4042; a106: 0; a109: 27625; a111: 27625 | 27625 | 258.4795 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | P. LABIAN / D. E. CAPIÑA
| 10pm - 6am | GEORGE HERNANDEZ / REY PROVIDENCIA
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 68 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 71 PSI
XCV4 - CLOSED @ 3:55 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 78 PSI
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
XCV4 -OPENED @ 10:01 PM (12%)
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (12%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 68 PSI

## 13
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-13
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8139400 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2054219 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-13 | 48:00 | 1:00 | 4 | 2.8169 | 0 | 63 | 44.3662 | 61 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8142831 |  |  |  | 3431 | 3.431 | 82.344 | a41: 82.344; a42: 4.8; a43: 4.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2055270; a109: 1051; a111: 1051 | 1051 | 306.3247 |  |  | Manual Operation | MO
2018-10-13 | 49:00 | 2:00 | 4 | 2.8169 | 2 | 68 | 47.8873 | 65 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8146830 |  |  |  | 3999 | 3.999 | 95.976 | a41: 95.976; a42: 6; a43: 6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2056363; a109: 1093; a111: 1093 | 1093 | 273.3183 | 1.02 |  | Scheduled Shutdown | SS
2018-10-13 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 63 | 44.3662 | 61 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8150630 |  |  |  | 3800 | 3.8 | 91.2 | a41: 91.2; a42: 7.5; a43: 7.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2057448; a109: 1085; a111: 1085 | 1085 | 285.5263 |  |  | Start Up Error | SU
2018-10-13 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 74 | 52.1127 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8154666 |  |  |  | 4036 | 4.036 | 96.864 | a41: 96.864; a42: 8.8; a43: 8.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2058565; a109: 1117; a111: 1117 | 1117 | 276.7592 |  |  | Shutdown Error | SE
2018-10-13 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8158732 |  |  |  | 4066 | 4.066 | 97.584 | a41: 97.584; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2059636; a109: 1071; a111: 1071 | 1071 | 263.4038 |  |  | Error - General | E
2018-10-13 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8163275 |  |  |  | 4543 | 4.543 | 109.032 | a41: 109.032; a42: 9.5; a43: 9.5; a47: 3B; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2060735; a109: 1099; a111: 1099 | 1099 | 241.9106 | 1.05 |  | Power Interruption | PI
2018-10-13 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8168591 |  |  |  | 5316 | 5.316 | 127.584 | a41: 127.584; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2061887; a109: 1152; a111: 1152 | 1152 | 216.7043 |  |  | Water Interruption | WI
2018-10-13 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8173689 |  |  |  | 5098 | 5.098 | 122.352 | a41: 122.352; a42: 8.5; a43: 8.5; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1046; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.9%; a89: 0%; a96: 0%; a107: 2063110; a109: 1223; a111: 1223 | 1223 | 239.898 |  |  | Equipment Maintenance | EM
2018-10-13 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8178206 |  |  |  | 4517 | 4.517 | 108.408 | a41: 108.408; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1046; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.9%; a89: 0%; a96: 0%; a107: 2064309; a109: 1199; a111: 1199 | 1199 | 265.4417
2018-10-13 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8182976 |  |  |  | 4770 | 4.77 | 114.48 | a41: 114.48; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1047; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.98%; a89: 0%; a96: 0%; a107: 2065604; a109: 1295; a111: 1295 | 1295 | 271.4885 | 0.95
2018-10-13 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 71 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8186992 |  |  |  | 4016 | 4.016 | 96.384 | a41: 96.384; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1047; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.98%; a89: 0%; a96: 0%; a107: 2066688; a109: 1084; a111: 1084 | 1084 | 269.9203 |  |  | UNITS
2018-10-13 | 59:00 | 12:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 70 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8191193 |  |  |  | 4201 | 4.201 | 100.824 | a41: 100.824; a42: 5.4; a43: 5.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1047; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.98%; a89: 0%; a96: 0%; a107: 2067879; a109: 1191; a111: 1191 | 1191 | 283.5039 |  |  | PRESSURE | Atmospheric Pressure
2018-10-13 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 70 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8195487 |  |  |  | 4294 | 4.294 | 103.056 | a41: 103.056; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1047; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.98%; a89: 0%; a96: 0%; a107: 2069110; a109: 1231; a111: 1231 | 1231 | 286.6791 |  |  | m of H2O | 14.7
2018-10-13 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 70 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8199800 |  |  |  | 4313 | 4.313 | 103.512 | a41: 103.512; a42: 4.1; a43: 4.1; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2070315; a109: 1205; a111: 1205 | 1205 | 279.3879 | 1.01 |  | psi | 10.36
2018-10-13 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 72 | 50.7042 | 70 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8203858 |  |  |  | 4058 | 4.058 | 97.392 | a41: 97.392; a42: 3.5; a43: 3.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2071431; a109: 1116; a111: 1116 | 1116 | 275.0123 |  |  | bar | 1.0132
2018-10-13 | 63:00 | 16:00 | 4 | 2.8169 | 1 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8208002 |  |  |  | 4144 | 4.144 | 99.456 | a41: 99.456; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2072594; a109: 1163; a111: 1163 | 1163 | 280.6467 |  |  | atm | 1
2018-10-13 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8212085 |  |  |  | 4083 | 4.083 | 97.992 | a41: 97.992; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2073745; a109: 1151; a111: 1151 | 1151 | 281.9006 |  |  | kPA | 101.325
2018-10-13 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 71 | 50 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8216416 |  |  |  | 4331 | 4.331 | 103.944 | a41: 103.944; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2074943; a109: 1198; a111: 1198 | 1198 | 276.6105 | 0.97
2018-10-13 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8220434 |  |  |  | 4018 | 4.018 | 96.432 | a41: 96.432; a42: 2; a43: 2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2076073; a109: 1130; a111: 1130 | 1130 | 281.2344 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-13 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 72 | 50.7042 | 70 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8224550 |  |  |  | 4116 | 4.116 | 98.784 | a41: 98.784; a42: 1.7; a43: 1.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2077225; a109: 1152; a111: 1152 | 1152 | 279.8834 |  |  | m of H2O | psi
2018-10-13 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8228710 |  |  |  | 4160 | 4.16 | 99.84 | a41: 99.84; a42: 1.4; a43: 1.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2078388; a109: 1163; a111: 1163 | 1163 | 279.5673 |  |  | 1 | 1.4189
2018-10-13 | 69:00 | 22:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8233095 |  |  |  | 4385 | 4.385 | 105.24 | a41: 105.24; a42: 1.4; a43: 1.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2079474; a109: 1086; a111: 1086 | 1086 | 247.6625 | 1.11
2018-10-13 | 70:00 | 23:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8236953 |  |  |  | 3858 | 3.858 | 92.592 | a41: 92.592; a42: 1.9; a43: 1.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2080551; a109: 1077; a111: 1077 | 1077 | 279.1602 |  |  | FLOW | MLD
2018-10-13 | 71:00 | 24:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8241255 |  |  |  | 4302 | 4.302 | 103.248 | a41: 103.248; a42: 2.4; a43: 2.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2081649; a109: 1098; a111: 1098 | 1098 | 255.2301 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.8333 | 72.2083 | 50.8509 | 70.25 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 101855 | 101.855 | 101.855 | a42: 5.0625; a43: 5.0625; a106: 0; a109: 27430; a111: 27430 | 27430 | 269.3044 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | D.E. CAPIÑA / A. RAYALA II
| 10pm - 6am | REY PROVIDENCIA/ FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4 - INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 63 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 68 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 63 PSI
XCV4 - DECREASE OPENING FROM 20% TO 15% SETTING @ 3:01 AM DUE TO LOW DISCHARGE PRESSURE AS PER CONROL CENTER ADVICE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
XCV4 - CLOSED @ 4:30 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 76 PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 71 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 72 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
SP1 - STOPPED @ 9:15 PM DUE TO PARAMETER CAPACITY OF 1.3 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
XCV4 -OPENED @ 10:01 PM (10%)
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI

## 14
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-14
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8241255 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2081649 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-14 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8244808 |  |  |  | 3553 | 3.553 | 85.272 | a41: 85.272; a42: 3.4; a43: 3.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2082746; a109: 1097; a111: 1097 | 1097 | 308.7532 |  |  | Manual Operation | MO
2018-10-14 | 49:00 | 2:00 | 4 | 2.8169 | 3 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8248752 |  |  |  | 3944 | 3.944 | 94.656 | a41: 94.656; a42: 4.8; a43: 4.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2083849; a109: 1103; a111: 1103 | 1103 | 279.6653 | 0.98 |  | Scheduled Shutdown | SS
2018-10-14 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8252536 |  |  |  | 3784 | 3.784 | 90.816 | a41: 90.816; a42: 6.3; a43: 6.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2084951; a109: 1102; a111: 1102 | 1102 | 291.2262 |  |  | Start Up Error | SU
2018-10-14 | 51:00 | 4:00 | 4 | 2.8169 | 6 | 67 | 47.1831 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8256520 |  |  |  | 3984 | 3.984 | 95.616 | a41: 95.616; a42: 8.3; a43: 8.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2086084; a109: 1133; a111: 1133 | 1133 | 284.3876 |  |  | Shutdown Error | SE
2018-10-14 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8260562 |  |  |  | 4042 | 4.042 | 97.008 | a41: 97.008; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2087183; a109: 1099; a111: 1099 | 1099 | 271.8951 |  |  | Error - General | E
2018-10-14 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 81 | 57.0423 | 79 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8265139 |  |  |  | 4577 | 4.577 | 109.848 | a41: 109.848; a42: 9.5; a43: 9.5; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2088290; a109: 1107; a111: 1107 | 1107 | 241.8615 | 0.95 |  | Power Interruption | PI
2018-10-14 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 79 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8270002 |  |  |  | 4863 | 4.863 | 116.712 | a41: 116.712; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2089382; a109: 1092; a111: 1092 | 1092 | 224.5527 |  |  | Water Interruption | WI
2018-10-14 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8275267 |  |  |  | 5265 | 5.265 | 126.36 | a41: 126.36; a42: 9.5; a43: 9.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: DEF; a107: 2090485; a109: 1103; a111: 1103 | 1103 | 209.4967 |  |  | Equipment Maintenance | EM
2018-10-14 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8280334 |  |  |  | 5067 | 5.067 | 121.608 | a41: 121.608; a42: 8.8; a43: 8.8; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 2091748; a109: 1263; a111: 1263 | 1263 | 249.2599
2018-10-14 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8284902 |  |  |  | 4568 | 4.568 | 109.632 | a41: 109.632; a42: 8.1; a43: 8.1; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: DEF; a107: 2092935; a109: 1187; a111: 1187 | 1187 | 259.8511 | 0.94
2018-10-14 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8289314 |  |  |  | 4412 | 4.412 | 105.888 | a41: 105.888; a42: 7.5; a43: 7.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 2094085; a109: 1150; a111: 1150 | 1150 | 260.6528 |  |  | UNITS
2018-10-14 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8294073 |  |  |  | 4759 | 4.759 | 114.216 | a41: 114.216; a42: 6.8; a43: 6.8; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 2095330; a109: 1245; a111: 1245 | 1245 | 261.6096 |  |  | PRESSURE | Atmospheric Pressure
2018-10-14 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8298306 |  |  |  | 4233 | 4.233 | 101.592 | a41: 101.592; a42: 6.2; a43: 6.2; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: DEF; a107: 2096484; a109: 1154; a111: 1154 | 1154 | 272.6199 |  |  | m of H2O | 14.7
2018-10-14 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8302843 |  |  |  | 4537 | 4.537 | 108.888 | a41: 108.888; a42: 5.6; a43: 5.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: DEF; a107: 2097688; a109: 1204; a111: 1204 | 1204 | 265.3736 | 0.99 |  | psi | 10.36
2018-10-14 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8308002 |  |  |  | 5159 | 5.159 | 123.816 | a41: 123.816; a42: 5.1; a43: 5.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1015; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.29%; a96: DEF; a107: 2098834; a109: 1146; a111: 1146 | 1146 | 222.1361 |  |  | bar | 1.0132
2018-10-14 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8313130 |  |  |  | 5128 | 5.128 | 123.072 | a41: 123.072; a42: 4.7; a43: 4.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1015; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.29%; a96: DEF; a107: 2099984; a109: 1150; a111: 1150 | 1150 | 224.259 |  |  | atm | 1
2018-10-14 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8318285 |  |  |  | 5155 | 5.155 | 123.72 | a41: 123.72; a42: 4.2; a43: 4.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1015; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.29%; a96: DEF; a107: 2101141; a109: 1157; a111: 1157 | 1157 | 224.4423 |  |  | kPA | 101.325
2018-10-14 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8323398 |  |  |  | 5113 | 5.113 | 122.712 | a41: 122.712; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: DEF; a107: 2102312; a109: 1171; a111: 1171 | 1171 | 229.0241 | 0.91
2018-10-14 | 66:00 | 19:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8328203 |  |  |  | 4805 | 4.805 | 115.32 | a41: 115.32; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: DEF; a107: 2103491; a109: 1179; a111: 1179 | 1179 | 245.3694 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-14 | 67:00 | 20:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8333062 |  |  |  | 4859 | 4.859 | 116.616 | a41: 116.616; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: DEF; a107: 2104638; a109: 1147; a111: 1147 | 1147 | 236.0568 |  |  | m of H2O | psi
2018-10-14 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8338761 |  |  |  | 5699 | 5.699 | 136.776 | a41: 136.776; a42: 2.6; a43: 2.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: DEF; a107: 2105781; a109: 1143; a111: 1143 | 1143 | 200.5615 |  |  | 1 | 1.4189
2018-10-14 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 74 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8343985 |  |  |  | 5224 | 5.224 | 125.376 | a41: 125.376; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: DEF; a107: 2106951; a109: 1170; a111: 1170 | 1170 | 223.9663 | 0.87
2018-10-14 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8348312 |  |  |  | 4327 | 4.327 | 103.848 | a41: 103.848; a42: 3.5; a43: 3.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2108015; a109: 1064; a111: 1064 | 1064 | 245.8979 |  |  | FLOW | MLD
2018-10-14 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8352405 |  |  |  | 4093 | 4.093 | 98.232 | a41: 98.232; a42: 5.2; a43: 5.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: DEF; a107: 2109121; a109: 1106; a111: 1106 | 1106 | 270.2174 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.875 | 74.25 | 52.2887 | 73.1667 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 111150 | 111.15 | 111.15 | a42: 5.9; a43: 5.9; a106: 0; a109: 27472; a111: 27472 | 27472 | 247.1615 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | D.E. CAPIÑA / J. LLAGUNO
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4 - INCREASE OPENING @ 12:01 AM (18%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 71 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 67 PSI
XCV4 - CLOSED @ 4:24 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 81 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 81 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
SP2 - STARTED @ 7:45 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
MR. NOEL NERPIO AND TEAM OF SOUTH MAINTENANCE ARRIVE @ 2:40 PM TO CONDUCT WARM UP GENSET 1&2 FOR 5 MINS.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.5 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
XCV4 -OPENED @ 10:01 PM (15%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 70 PSI

## 15
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-15
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8352405 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2109121 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-15 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8356515 |  |  |  | 4110 | 4.11 | 98.64 | a41: 98.64; a42: 6.7; a43: 6.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2110234; a109: 1113; a111: 1113 | 1113 | 270.8029 |  |  | Manual Operation | MO
2018-10-15 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8360888 |  |  |  | 4373 | 4.373 | 104.952 | a41: 104.952; a42: 8.3; a43: 8.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2111328; a109: 1094; a111: 1094 | 1094 | 250.1715 | 0.79 |  | Scheduled Shutdown | SS
2018-10-15 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8365330 |  |  |  | 4442 | 4.442 | 106.608 | a41: 106.608; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2112435; a109: 1107; a111: 1107 | 1107 | 249.2121 |  |  | Start Up Error | SU
2018-10-15 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8369290 |  |  |  | 3960 | 3.96 | 95.04 | a41: 95.04; a42: 9.5; a43: 9.5; a47: 3B; a48: 1095; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 92.02%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2113436; a109: 1001; a111: 1001 | 1001 | 252.7778 |  |  | Shutdown Error | SE
2018-10-15 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8373414 |  |  |  | 4124 | 4.124 | 98.976 | a41: 98.976; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2114444; a109: 1008; a111: 1008 | 1008 | 244.4229 |  |  | Error - General | E
2018-10-15 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8378270 |  |  |  | 4856 | 4.856 | 116.544 | a41: 116.544; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2115549; a109: 1105; a111: 1105 | 1105 | 227.5535 | 0.82 |  | Power Interruption | PI
2018-10-15 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8383992 |  |  |  | 5722 | 5.722 | 137.328 | a41: 137.328; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1017; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.46%; a89: 0%; a96: 0%; a107: 2116739; a109: 1190; a111: 1190 | 1190 | 207.9692 |  |  | Water Interruption | WI
2018-10-15 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8389574 |  |  |  | 5582 | 5.582 | 133.968 | a41: 133.968; a42: 8.5; a43: 8.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2117893; a109: 1154; a111: 1154 | 1154 | 206.7359 |  |  | Equipment Maintenance | EM
2018-10-15 | 56:00 | 9:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8394167 |  |  |  | 4593 | 4.593 | 110.232 | a41: 110.232; a42: 8; a43: 8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2119105; a109: 1212; a111: 1212 | 1212 | 263.8798
2018-10-15 | 57:00 | 10:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8398919 |  |  |  | 4752 | 4.752 | 114.048 | a41: 114.048; a42: 7.2; a43: 7.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2120350; a109: 1245; a111: 1245 | 1245 | 261.9949 | 1.02
2018-10-15 | 58:00 | 11:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8403163 |  |  |  | 4244 | 4.244 | 101.856 | a41: 101.856; a42: 6.7; a43: 6.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 2121480; a109: 1130; a111: 1130 | 1130 | 266.2582 |  |  | UNITS
2018-10-15 | 59:00 | 12:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8407759 |  |  |  | 4596 | 4.596 | 110.304 | a41: 110.304; a42: 6.1; a43: 6.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 2122688; a109: 1208; a111: 1208 | 1208 | 262.8372 |  |  | PRESSURE | Atmospheric Pressure
2018-10-15 | 60:00 | 13:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8412348 |  |  |  | 4589 | 4.589 | 110.136 | a41: 110.136; a42: 5.4; a43: 5.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 2123902; a109: 1214; a111: 1214 | 1214 | 264.5457 |  |  | m of H2O | 14.7
2018-10-15 | 61:00 | 14:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8416598 |  |  |  | 4250 | 4.25 | 102 | a41: 102; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2125059; a109: 1157; a111: 1157 | 1157 | 272.2353 | 1.11 |  | psi | 10.36
2018-10-15 | 62:00 | 15:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8420780 |  |  |  | 4182 | 4.182 | 100.368 | a41: 100.368; a42: 4.3; a43: 4.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2126196; a109: 1137; a111: 1137 | 1137 | 271.8795 |  |  | bar | 1.0132
2018-10-15 | 63:00 | 16:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8425253 |  |  |  | 4473 | 4.473 | 107.352 | a41: 107.352; a42: 3.8; a43: 3.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2127325; a109: 1129; a111: 1129 | 1129 | 252.4033 |  |  | atm | 1
2018-10-15 | 64:00 | 17:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8429909 |  |  |  | 4656 | 4.656 | 111.744 | a41: 111.744; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2128486; a109: 1161; a111: 1161 | 1161 | 249.3557 |  |  | kPA | 101.325
2018-10-15 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8434545 |  |  |  | 4636 | 4.636 | 111.264 | a41: 111.264; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2129652; a109: 1166; a111: 1166 | 1166 | 251.5099 | 1.05
2018-10-15 | 66:00 | 19:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8438980 |  |  |  | 4435 | 4.435 | 106.44 | a41: 106.44; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2130798; a109: 1146; a111: 1146 | 1146 | 258.3991 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-15 | 67:00 | 20:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 71 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8443212 |  |  |  | 4232 | 4.232 | 101.568 | a41: 101.568; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2131913; a109: 1115; a111: 1115 | 1115 | 263.4688 |  |  | m of H2O | psi
2018-10-15 | 68:00 | 21:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8447894 |  |  |  | 4682 | 4.682 | 112.368 | a41: 112.368; a42: 2.2; a43: 2.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2133068; a109: 1155; a111: 1155 | 1155 | 246.6894 |  |  | 1 | 1.4189
2018-10-15 | 69:00 | 22:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 72 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8452795 |  |  |  | 4901 | 4.901 | 117.624 | a41: 117.624; a42: 2; a43: 2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2134205; a109: 1137; a111: 1137 | 1137 | 231.9935 | 0.99
2018-10-15 | 70:00 | 23:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8456762 |  |  |  | 3967 | 3.967 | 95.208 | a41: 95.208; a42: 2.8; a43: 2.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2135306; a109: 1101; a111: 1101 | 1101 | 277.5397 |  |  | FLOW | MLD
2018-10-15 | 71:00 | 24:00 | 4 | 2.8169 | 4 | 69 | 48.5915 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8460344 |  |  |  | 3582 | 3.582 | 85.968 | a41: 85.968; a42: 4.1; a43: 4.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2136450; a109: 1144; a111: 1144 | 1144 | 319.3747 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.0417 | 74.125 | 52.2007 | 72.25 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 107939 | 107.939 | 107.939 | a42: 5.8292; a43: 5.8292; a106: 0; a109: 27329; a111: 27329 | 27329 | 253.1893 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA / D. E. CAPIÑA
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4 - INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 72 PSI
XCV4 - CLOSED @ 2:42 AM WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 80 PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
XCV4 -OPENED @ 10:01 PM (15%)
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 69 PSI

## 16
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-16
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8460344 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2136450 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-16 | 48:00 | 1:00 | 4 | 2.8169 | 5 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8464633 |  |  |  | 4289 | 4.289 | 102.936 | a41: 102.936; a42: 5.6; a43: 5.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2137530; a109: 1080; a111: 1080 | 1080 | 251.8069 |  |  | Manual Operation | MO
2018-10-16 | 49:00 | 2:00 | 4 | 2.8169 | 6 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8468799 |  |  |  | 4166 | 4.166 | 99.984 | a41: 99.984; a42: 7.1; a43: 7.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2138640; a109: 1110; a111: 1110 | 1110 | 266.4426 | 0.88 |  | Scheduled Shutdown | SS
2018-10-16 | 50:00 | 3:00 | 4 | 2.8169 | 7 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8472972 |  |  |  | 4173 | 4.173 | 100.152 | a41: 100.152; a42: 8.8; a43: 8.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2139727; a109: 1087; a111: 1087 | 1087 | 260.4841 |  |  | Start Up Error | SU
2018-10-16 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 80 | 56.338 | 78 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8477240 |  |  |  | 4268 | 4.268 | 102.432 | a41: 102.432; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2140835; a109: 1108; a111: 1108 | 1108 | 259.6064 |  |  | Shutdown Error | SE
2018-10-16 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 79 | 55.6338 | 77 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8481350 |  |  |  | 4110 | 4.11 | 98.64 | a41: 98.64; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2141825; a109: 990; a111: 990 | 990 | 240.8759 |  |  | Error - General | E
2018-10-16 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8486540 |  |  |  | 5190 | 5.19 | 124.56 | a41: 124.56; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2142977; a109: 1152; a111: 1152 | 1152 | 221.9653 | 1.12 |  | Power Interruption | PI
2018-10-16 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8492553 |  |  |  | 6013 | 6.013 | 144.312 | a41: 144.312; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2144214; a109: 1237; a111: 1237 | 1237 | 205.7209 |  |  | Water Interruption | WI
2018-10-16 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8497723 |  |  |  | 5170 | 5.17 | 124.08 | a41: 124.08; a42: 8.6; a43: 8.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2145335; a109: 1121; a111: 1121 | 1121 | 216.8279 |  |  | Equipment Maintenance | EM
2018-10-16 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8502142 |  |  |  | 4419 | 4.419 | 106.056 | a41: 106.056; a42: 8; a43: 8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2146464; a109: 1129; a111: 1129 | 1129 | 255.4877
2018-10-16 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8506705 |  |  |  | 4563 | 4.563 | 109.512 | a41: 109.512; a42: 7.3; a43: 7.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2147683; a109: 1219; a111: 1219 | 1219 | 267.1488 | 1.03
2018-10-16 | 58:00 | 11:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8511094 |  |  |  | 4389 | 4.389 | 105.336 | a41: 105.336; a42: 6.7; a43: 6.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2148815; a109: 1132; a111: 1132 | 1132 | 257.9175 |  |  | UNITS
2018-10-16 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8515602 |  |  |  | 4508 | 4.508 | 108.192 | a41: 108.192; a42: 6; a43: 6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2150060; a109: 1245; a111: 1245 | 1245 | 276.1757 |  |  | PRESSURE | Atmospheric Pressure
2018-10-16 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 75 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8519758 |  |  |  | 4156 | 4.156 | 99.744 | a41: 99.744; a42: 5.5; a43: 5.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2151169; a109: 1109; a111: 1109 | 1109 | 266.8431 |  |  | m of H2O | 14.7
2018-10-16 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8524404 |  |  |  | 4646 | 4.646 | 111.504 | a41: 111.504; a42: 5; a43: 5; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2152374; a109: 1205; a111: 1205 | 1205 | 259.3629 | 1.18 |  | psi | 10.36
2018-10-16 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8529096 |  |  |  | 4692 | 4.692 | 112.608 | a41: 112.608; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2153562; a109: 1188; a111: 1188 | 1188 | 253.1969 |  |  | bar | 1.0132
2018-10-16 | 63:00 | 16:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8533942 |  |  |  | 4846 | 4.846 | 116.304 | a41: 116.304; a42: 4.1; a43: 4.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2154744; a109: 1182; a111: 1182 | 1182 | 243.9125 |  |  | atm | 1
2018-10-16 | 64:00 | 17:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8538558 |  |  |  | 4616 | 4.616 | 110.784 | a41: 110.784; a42: 3.6; a43: 3.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2155868; a109: 1124; a111: 1124 | 1124 | 243.5009 |  |  | kPA | 101.325
2018-10-16 | 65:00 | 18:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8543270 |  |  |  | 4712 | 4.712 | 113.088 | a41: 113.088; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2157000; a109: 1132; a111: 1132 | 1132 | 240.2377 | 1.22
2018-10-16 | 66:00 | 19:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 68 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8547842 |  |  |  | 4572 | 4.572 | 109.728 | a41: 109.728; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2158138; a109: 1138; a111: 1138 | 1138 | 248.9064 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-16 | 67:00 | 20:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 68 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8552556 |  |  |  | 4714 | 4.714 | 113.136 | a41: 113.136; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2159336; a109: 1198; a111: 1198 | 1198 | 254.1366 |  |  | m of H2O | psi
2018-10-16 | 68:00 | 21:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8557118 |  |  |  | 4562 | 4.562 | 109.488 | a41: 109.488; a42: 1.9; a43: 1.9; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2160464; a109: 1128; a111: 1128 | 1128 | 247.26 |  |  | 1 | 1.4189
2018-10-16 | 69:00 | 22:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8561884 |  |  |  | 4766 | 4.766 | 114.384 | a41: 114.384; a42: 1.6; a43: 1.6; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1025; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.13%; a96: 0%; a107: 2161626; a109: 1162; a111: 1162 | 1162 | 243.8103 | 1.14
2018-10-16 | 70:00 | 23:00 | 4 | 2.8169 | 2 | 71 | 50 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8565786 |  |  |  | 3902 | 3.902 | 93.648 | a41: 93.648; a42: 2.4; a43: 2.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2162734; a109: 1108; a111: 1108 | 1108 | 283.9569 |  |  | FLOW | MLD
2018-10-16 | 71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8569994 |  |  |  | 4208 | 4.208 | 100.992 | a41: 100.992; a42: 3.3; a43: 3.3; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2163826; a109: 1092; a111: 1092 | 1092 | 259.5057 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 4.375 | 74.625 | 52.5528 | 71.375 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 109650 | 109.65 | 109.65 | a42: 5.6583; a43: 5.6583; a106: 0; a109: 27376; a111: 27376 | 27376 | 249.6671 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | M.A. ESTOCHE / D.E. CAPIÑA / R. PROVIDENCIA
| 2pm - 10pm | FIDEL RAMOS / DYAN ELVIN CAPIÑA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4 - INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 69 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 69 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI
XCV4 - CLOSED @ 3:20 AM WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 79 PSI
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
MR. VALDEZ AND TEAM MIESCOR LOGISTIC ARRIVED @ 10:42 AM FOR REPAIR/REPLACE BRPKEN GLASS WINDOW AT SECURITY OFFICE.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE / ACTUAL READING 78PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
MR.CHARLES FLORES OF RJEN INNOVATIVE FOR SITE INSPECTION OF STRUCTURED CABLING
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.6 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 77PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI

## 17
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-17
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8569994 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2163826 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-17 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8573828 |  |  |  | 3834 | 3.834 | 92.016 | a41: 92.016; a42: 4.8; a43: 4.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2164956; a109: 1130; a111: 1130 | 1130 | 294.7314 |  |  | Manual Operation | MO
2018-10-17 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8578006 |  |  |  | 4178 | 4.178 | 100.272 | a41: 100.272; a42: 6.2; a43: 6.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2166040; a109: 1084; a111: 1084 | 1084 | 259.4543 | 1.14 |  | Scheduled Shutdown | SS
2018-10-17 | 50:00 | 3:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8582314 |  |  |  | 4308 | 4.308 | 103.392 | a41: 103.392; a42: 7.6; a43: 7.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2167210; a109: 1170; a111: 1170 | 1170 | 271.5877 |  |  | Start Up Error | SU
2018-10-17 | 51:00 | 4:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8586646 |  |  |  | 4332 | 4.332 | 103.968 | a41: 103.968; a42: 9; a43: 9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2168292; a109: 1082; a111: 1082 | 1082 | 249.7692 |  |  | Shutdown Error | SE
2018-10-17 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8591156 |  |  |  | 4510 | 4.51 | 108.24 | a41: 108.24; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2169326; a109: 1034; a111: 1034 | 1034 | 229.2683 |  |  | Error - General | E
2018-10-17 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8595666 |  |  |  | 4510 | 4.51 | 108.24 | a41: 108.24; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2170386; a109: 1060; a111: 1060 | 1060 | 235.0333 | 1.18 |  | Power Interruption | PI
2018-10-17 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8600888 |  |  |  | 5222 | 5.222 | 125.328 | a41: 125.328; a42: 9; a43: 9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2171610; a109: 1224; a111: 1224 | 1224 | 234.393 |  |  | Water Interruption | WI
2018-10-17 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8606263 |  |  |  | 5375 | 5.375 | 129 | a41: 129; a42: 8.3; a43: 8.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2172846; a109: 1236; a111: 1236 | 1236 | 229.9535 |  |  | Equipment Maintenance | EM
2018-10-17 | 56:00 | 9:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8610909 |  |  |  | 4646 | 4.646 | 111.504 | a41: 111.504; a42: 7.6; a43: 7.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2174046; a109: 1200; a111: 1200 | 1200 | 258.2867
2018-10-17 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8615562 |  |  |  | 4653 | 4.653 | 111.672 | a41: 111.672; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2175251; a109: 1205; a111: 1205 | 1205 | 258.9727 | 1.2
2018-10-17 | 58:00 | 11:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8620251 |  |  |  | 4689 | 4.689 | 112.536 | a41: 112.536; a42: 6.8; a43: 6.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2176455; a109: 1204; a111: 1204 | 1204 | 256.7712 |  |  | UNITS
2018-10-17 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8624948 |  |  |  | 4697 | 4.697 | 112.728 | a41: 112.728; a42: 5.9; a43: 5.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2177678; a109: 1223; a111: 1223 | 1223 | 260.379 |  |  | PRESSURE | Atmospheric Pressure
2018-10-17 | 60:00 | 13:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8629030 |  |  |  | 4082 | 4.082 | 97.968 | a41: 97.968; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2178727; a109: 1049; a111: 1049 | 1049 | 256.9819 |  |  | m of H2O | 14.7
2018-10-17 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8633678 |  |  |  | 4648 | 4.648 | 111.552 | a41: 111.552; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1025; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.13%; a89: 0%; a96: 0%; a107: 2179954; a109: 1227; a111: 1227 | 1227 | 263.9845 | 0.98 |  | psi | 10.36
2018-10-17 | 62:00 | 15:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8638292 |  |  |  | 4614 | 4.614 | 110.736 | a41: 110.736; a42: 4.4; a43: 4.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2181108; a109: 1154; a111: 1154 | 1154 | 250.1084 |  |  | bar | 1.0132
2018-10-17 | 63:00 | 16:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8642913 |  |  |  | 4621 | 4.621 | 110.904 | a41: 110.904; a42: 3.9; a43: 3.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2182267; a109: 1159; a111: 1159 | 1159 | 250.8115 |  |  | atm | 1
2018-10-17 | 64:00 | 17:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8647477 |  |  |  | 4564 | 4.564 | 109.536 | a41: 109.536; a42: 3.6; a43: 3.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2183415; a109: 1148; a111: 1148 | 1148 | 251.5337 |  |  | kPA | 101.325
2018-10-17 | 65:00 | 18:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8652001 |  |  |  | 4524 | 4.524 | 108.576 | a41: 108.576; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2184577; a109: 1162; a111: 1162 | 1162 | 256.8523 | 1.09
2018-10-17 | 66:00 | 19:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8656425 |  |  |  | 4424 | 4.424 | 106.176 | a41: 106.176; a42: 2.9; a43: 2.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2185720; a109: 1143; a111: 1143 | 1143 | 258.3635 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-17 | 67:00 | 20:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 70 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8660643 |  |  |  | 4218 | 4.218 | 101.232 | a41: 101.232; a42: 2.6; a43: 2.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2186870; a109: 1150; a111: 1150 | 1150 | 272.6411 |  |  | m of H2O | psi
2018-10-17 | 68:00 | 21:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8665180 |  |  |  | 4537 | 4.537 | 108.888 | a41: 108.888; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2188024; a109: 1154; a111: 1154 | 1154 | 254.3531 |  |  | 1 | 1.4189
2018-10-17 | 69:00 | 22:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8669734 |  |  |  | 4554 | 4.554 | 109.296 | a41: 109.296; a42: 2.1; a43: 2.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2189166; a109: 1142; a111: 1142 | 1142 | 250.7686 | 1.14
2018-10-17 | 70:00 | 23:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8673326 |  |  |  | 3592 | 3.592 | 86.208 | a41: 86.208; a42: 2.9; a43: 2.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2190252; a109: 1086; a111: 1086 | 1086 | 302.3385 |  |  | FLOW | MLD
2018-10-17 | 71:00 | 24:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8677258 |  |  |  | 3932 | 3.932 | 94.368 | a41: 94.368; a42: 3.9; a43: 3.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2191344; a109: 1092; a111: 1092 | 1092 | 277.7213 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 4.7083 | 74.125 | 52.2007 | 71.5417 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 107264 | 107.264 | 107.264 | a42: 5.55; a43: 5.55; a106: 0; a109: 27518; a111: 27518 | 27518 | 256.5446 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | M.A. ESTOCHE / J. LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA / D. E. CAPIÑA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 72PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
XCV4 - CLOSED @ 4:10 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 77PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
SAFETY LEAD BY EMAN REYES ARRIVE @ 11:00AM FOR INSPECTION.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
MR. VALDEZ AND TEAM MIESCOR LOGISTIC ARRIVED @ 4:27 PM FOR INSTALLATION OF BROPKEN GLASS WINDOW AT SECURITY OFFICE.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 74PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.1 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE/ ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 74PSI

## 18
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-18
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8677258 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2191344 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-18 | 48:00 | 1:00 | 4 | 2.8169 | 4 | 71 | 50 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8680986 |  |  |  | 3728 | 3.728 | 89.472 | a41: 89.472; a42: 5.4; a43: 5.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2192452; a109: 1108; a111: 1108 | 1108 | 297.2103 |  |  | Manual Operation | MO
2018-10-18 | 49:00 | 2:00 | 4 | 2.8169 | 6 | 73 | 51.4085 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8685264 |  |  |  | 4278 | 4.278 | 102.672 | a41: 102.672; a42: 6.8; a43: 6.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2193644; a109: 1192; a111: 1192 | 1192 | 278.6349 | 1.16 |  | Scheduled Shutdown | SS
2018-10-18 | 50:00 | 3:00 | 4 | 2.8169 | 7 | 73 | 51.4085 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8688956 |  |  |  | 3692 | 3.692 | 88.608 | a41: 88.608; a42: 8.3; a43: 8.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2194662; a109: 1018; a111: 1018 | 1018 | 275.7313 |  |  | Start Up Error | SU
2018-10-18 | 51:00 | 4:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 78 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8693164 |  |  |  | 4208 | 4.208 | 100.992 | a41: 100.992; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2195774; a109: 1112; a111: 1112 | 1112 | 264.2586 |  |  | Shutdown Error | SE
2018-10-18 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8697834 |  |  |  | 4670 | 4.67 | 112.08 | a41: 112.08; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2196930; a109: 1156; a111: 1156 | 1156 | 247.5375 |  |  | Error - General | E
2018-10-18 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 75 | 52.8169 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8702407 |  |  |  | 4573 | 4.573 | 109.752 | a41: 109.752; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2198004; a109: 1074; a111: 1074 | 1074 | 234.8568 | 1.19 |  | Power Interruption | PI
2018-10-18 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8707184 |  |  |  | 4777 | 4.777 | 114.648 | a41: 114.648; a42: 8.9; a43: 8.9; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2199148; a109: 1144; a111: 1144 | 1144 | 239.4808 |  |  | Water Interruption | WI
2018-10-18 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8712459 |  |  |  | 5275 | 5.275 | 126.6 | a41: 126.6; a42: 8.2; a43: 8.2; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2200387; a109: 1239; a111: 1239 | 1239 | 234.8815 |  |  | Equipment Maintenance | EM
2018-10-18 | 56:00 | 9:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8716947 |  |  |  | 4488 | 4.488 | 107.712 | a41: 107.712; a42: 7.6; a43: 7.6; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2201530; a109: 1143; a111: 1143 | 1143 | 254.6791
2018-10-18 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8721851 |  |  |  | 4904 | 4.904 | 117.696 | a41: 117.696; a42: 6.8; a43: 6.8; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2202814; a109: 1284; a111: 1284 | 1284 | 261.8271 | 1.2
2018-10-18 | 58:00 | 11:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8726136 |  |  |  | 4285 | 4.285 | 102.84 | a41: 102.84; a42: 6.3; a43: 6.3; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2203958; a109: 1144; a111: 1144 | 1144 | 266.9778 |  |  | UNITS
2018-10-18 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8730592 |  |  |  | 4456 | 4.456 | 106.944 | a41: 106.944; a42: 5.7; a43: 5.7; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2205115; a109: 1157; a111: 1157 | 1157 | 259.6499 |  |  | PRESSURE | Atmospheric Pressure
2018-10-18 | 60:00 | 13:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8735002 |  |  |  | 4410 | 4.41 | 105.84 | a41: 105.84; a42: 5.1; a43: 5.1; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2206331; a109: 1216; a111: 1216 | 1216 | 275.737 |  |  | m of H2O | 14.7
2018-10-18 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8739585 |  |  |  | 4583 | 4.583 | 109.992 | a41: 109.992; a42: 4.6; a43: 4.6; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2207519; a109: 1188; a111: 1188 | 1188 | 259.2189 | 1.22 |  | psi | 10.36
2018-10-18 | 62:00 | 15:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8744228 |  |  |  | 4643 | 4.643 | 111.432 | a41: 111.432; a42: 4.2; a43: 4.2; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1015; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.29%; a96: 0%; a107: 2208690; a109: 1171; a111: 1171 | 1171 | 252.2076 |  |  | bar | 1.0132
2018-10-18 | 63:00 | 16:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8748691 |  |  |  | 4463 | 4.463 | 107.112 | a41: 107.112; a42: 3.8; a43: 3.8; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1015; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.29%; a96: 0%; a107: 2209839; a109: 1149; a111: 1149 | 1149 | 257.4501 |  |  | atm | 1
2018-10-18 | 64:00 | 17:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8753427 |  |  |  | 4736 | 4.736 | 113.664 | a41: 113.664; a42: 3.5; a43: 3.5; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1015; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.29%; a96: 0%; a107: 2211007; a109: 1168; a111: 1168 | 1168 | 246.6216 |  |  | kPA | 101.325
2018-10-18 | 65:00 | 18:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8758267 |  |  |  | 4840 | 4.84 | 116.16 | a41: 116.16; a42: 3.1; a43: 3.1; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1014; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.21%; a96: 0%; a107: 2212157; a109: 1150; a111: 1150 | 1150 | 237.6033 | 1.18
2018-10-18 | 66:00 | 19:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 69 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8763051 |  |  |  | 4784 | 4.784 | 114.816 | a41: 114.816; a42: 2.7; a43: 2.7; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1014; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.21%; a96: 0%; a107: 2213262; a109: 1105; a111: 1105 | 1105 | 230.9783 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-18 | 67:00 | 20:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 68 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8767261 |  |  |  | 4210 | 4.21 | 101.04 | a41: 101.04; a42: 2.3; a43: 2.3; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1014; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.21%; a96: 0%; a107: 2214480; a109: 1218; a111: 1218 | 1218 | 289.3112 |  |  | m of H2O | psi
2018-10-18 | 68:00 | 21:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8771791 |  |  |  | 4530 | 4.53 | 108.72 | a41: 108.72; a42: 2; a43: 2; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1014; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.21%; a96: 0%; a107: 2215608; a109: 1128; a111: 1128 | 1128 | 249.0066 |  |  | 1 | 1.4189
2018-10-18 | 69:00 | 22:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8776354 |  |  |  | 4563 | 4.563 | 109.512 | a41: 109.512; a42: 1.7; a43: 1.7; a47: 3B+IS; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: 0%; a107: 2216748; a109: 1140; a111: 1140 | 1140 | 249.8356 | 1.16
2018-10-18 | 70:00 | 23:00 | 4 | 2.8169 | 2 | 73 | 51.4085 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8780172 |  |  |  | 3818 | 3.818 | 91.632 | a41: 91.632; a42: 2.6; a43: 2.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2217850; a109: 1102; a111: 1102 | 1102 | 288.6328 |  |  | FLOW | MLD
2018-10-18 | 71:00 | 24:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8784304 |  |  |  | 4132 | 4.132 | 99.168 | a41: 99.168; a42: 3.5; a43: 3.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2218936; a109: 1086; a111: 1086 | 1086 | 262.8267 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 4.7083 | 75 | 52.8169 | 71.875 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 107046 | 107.046 | 107.046 | a42: 5.4833; a43: 5.4833; a106: 0; a109: 27592; a111: 27592 | 27592 | 257.7583 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | M.A. ESTOCHE / D. CAPIÑA
| 2pm - 10pm | REY PROVIDENCIA / A.RAYALA II
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE/ ACTUAL READING 73PSI
XCV4 - CLOSED @ 3:42 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE/ ACTUAL READING 83PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 78PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 73PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.7 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 74PSI

## 19
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-19
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8784304 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2218936 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-19 | 48:00 | 1:00 | 4 | 2.8169 | 4 | 71 | 50 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8788096 |  |  |  | 3792 | 3.792 | 91.008 | a41: 91.008; a42: 5.1; a43: 5.1; a47: 3B; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2220056; a109: 1120; a111: 1120 | 1120 | 295.3586 |  |  | Manual Operation | MO
2018-10-19 | 49:00 | 2:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8792028 |  |  |  | 3932 | 3.932 | 94.368 | a41: 94.368; a42: 6.6; a43: 6.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2221178; a109: 1122; a111: 1122 | 1122 | 285.351 | 1.1 |  | Scheduled Shutdown | SS
2018-10-19 | 50:00 | 3:00 | 4 | 2.8169 | 7 | 74 | 52.1127 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8795856 |  |  |  | 3828 | 3.828 | 91.872 | a41: 91.872; a42: 8.1; a43: 8.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2222298; a109: 1120; a111: 1120 | 1120 | 292.581 |  |  | Start Up Error | SU
2018-10-19 | 51:00 | 4:00 | 4 | 2.8169 | 9 | 82 | 57.7465 | 78 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8799952 |  |  |  | 4096 | 4.096 | 98.304 | a41: 98.304; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2223398; a109: 1100; a111: 1100 | 1100 | 268.5547 |  |  | Shutdown Error | SE
2018-10-19 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 79 | 55.6338 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8804116 |  |  |  | 4164 | 4.164 | 99.936 | a41: 99.936; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2224482; a109: 1084; a111: 1084 | 1084 | 260.3266 |  |  | Error - General | E
2018-10-19 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 75 | 52.8169 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8808772 |  |  |  | 4656 | 4.656 | 111.744 | a41: 111.744; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2225594; a109: 1112; a111: 1112 | 1112 | 238.8316 | 1.18 |  | Power Interruption | PI
2018-10-19 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8813501 |  |  |  | 4729 | 4.729 | 113.496 | a41: 113.496; a42: 9.1; a43: 9.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2226752; a109: 1158; a111: 1158 | 1158 | 244.8721 |  |  | Water Interruption | WI
2018-10-19 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8818599 |  |  |  | 5098 | 5.098 | 122.352 | a41: 122.352; a42: 8.4; a43: 8.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2227960; a109: 1208; a111: 1208 | 1208 | 236.9557 |  |  | Equipment Maintenance | EM
2018-10-19 | 56:00 | 9:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8823265 |  |  |  | 4666 | 4.666 | 111.984 | a41: 111.984; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2229177; a109: 1217; a111: 1217 | 1217 | 260.823
2018-10-19 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8827798 |  |  |  | 4533 | 4.533 | 108.792 | a41: 108.792; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2230386; a109: 1209; a111: 1209 | 1209 | 266.7108 | 1.13
2018-10-19 | 58:00 | 11:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8832212 |  |  |  | 4414 | 4.414 | 105.936 | a41: 105.936; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2231495; a109: 1109; a111: 1109 | 1109 | 251.246 |  |  | UNITS
2018-10-19 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8836702 |  |  |  | 4490 | 4.49 | 107.76 | a41: 107.76; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2232772; a109: 1277; a111: 1277 | 1277 | 284.4098 |  |  | PRESSURE | Atmospheric Pressure
2018-10-19 | 60:00 | 13:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 75 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8840994 |  |  |  | 4292 | 4.292 | 103.008 | a41: 103.008; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2233935; a109: 1163; a111: 1163 | 1163 | 270.9692 |  |  | m of H2O | 14.7
2018-10-19 | 61:00 | 14:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8845444 |  |  |  | 4450 | 4.45 | 106.8 | a41: 106.8; a42: 4.9; a43: 4.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2235087; a109: 1152; a111: 1152 | 1152 | 258.8764 | 1.02 |  | psi | 10.36
2018-10-19 | 62:00 | 15:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8849865 |  |  |  | 4421 | 4.421 | 106.104 | a41: 106.104; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2236240; a109: 1153; a111: 1153 | 1153 | 260.8007 |  |  | bar | 1.0132
2018-10-19 | 63:00 | 16:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8854478 |  |  |  | 4613 | 4.613 | 110.712 | a41: 110.712; a42: 4.2; a43: 4.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2237398; a109: 1158; a111: 1158 | 1158 | 251.0297 |  |  | atm | 1
2018-10-19 | 64:00 | 17:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8858875 |  |  |  | 4397 | 4.397 | 105.528 | a41: 105.528; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2238555; a109: 1157; a111: 1157 | 1157 | 263.134 |  |  | kPA | 101.325
2018-10-19 | 65:00 | 18:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8863465 |  |  |  | 4590 | 4.59 | 110.16 | a41: 110.16; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2239740; a109: 1185; a111: 1185 | 1185 | 258.1699 | 0.87
2018-10-19 | 66:00 | 19:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8868060 |  |  |  | 4595 | 4.595 | 110.28 | a41: 110.28; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2240905; a109: 1165; a111: 1165 | 1165 | 253.5365 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-19 | 67:00 | 20:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 71 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8872348 |  |  |  | 4288 | 4.288 | 102.912 | a41: 102.912; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2242062; a109: 1157; a111: 1157 | 1157 | 269.8228 |  |  | m of H2O | psi
2018-10-19 | 68:00 | 21:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8876726 |  |  |  | 4378 | 4.378 | 105.072 | a41: 105.072; a42: 2.4; a43: 2.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2243191; a109: 1129; a111: 1129 | 1129 | 257.8803 |  |  | 1 | 1.4189
2018-10-19 | 69:00 | 22:00 | 4 | 2.8169 | -4 | 76 | 53.5211 | 74 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8881416 |  |  |  | 4690 | 4.69 | 112.56 | a41: 112.56; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2244326; a109: 1135; a111: 1135 | 1135 | 242.0043 | 1.03
2018-10-19 | 70:00 | 23:00 | 4 | 2.8169 | -2 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8885581 |  |  |  | 4165 | 4.165 | 99.96 | a41: 99.96; a42: 2.7; a43: 2.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2245427; a109: 1101; a111: 1101 | 1101 | 264.3457 |  |  | FLOW | MLD
2018-10-19 | 71:00 | 24:00 | 4 | 2.8169 | 1 | 70 | 49.2958 | 73 | [7 empty] | 68 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 8889971 |  |  |  | 4390 | 4.39 | 105.36 | a41: 105.36; a42: 3.6; a43: 3.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2246523; a109: 1096; a111: 1096 | 1096 | 249.6583 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.2083 | 75 | 52.8169 | 74.8333 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 105667 | 105.667 | 105.667 | a42: 5.65; a43: 5.65; a106: 0; a109: 27587; a111: 27587 | 27587 | 261.0749 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | A.RAYALA II / J. LLAGUNO
| 2pm - 10pm | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 10pm - 6am | REY PROVIDENCIA / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 74PSI
XCV4 - CLOSED @ 3:50 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 82PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 79PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
SP1 - STARTED @ 6:17 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
MIESCOR LEAD BY ENGR, AUGUSTUS VALDEZ ARRIVE @ 9:12 AM FOR DELIVERY OF 10 PCS ROAD LIGHT AND 3 PCS ELECTRICAL TAPE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 75PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.3 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 70PSI

## 20
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-20
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8889971 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2246523 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-20 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8893513 |  |  |  | 3542 | 3.542 | 85.008 | a41: 85.008; a42: 5.1; a43: 5.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2247635; a109: 1112; a111: 1112 | 1112 | 313.9469 |  |  | Manual Operation | MO
2018-10-20 | 49:00 | 2:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8897541 |  |  |  | 4028 | 4.028 | 96.672 | a41: 96.672; a42: 6.7; a43: 6.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2248736; a109: 1101; a111: 1101 | 1101 | 273.3366 | 0.98 |  | Scheduled Shutdown | SS
2018-10-20 | 50:00 | 3:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8901645 |  |  |  | 4104 | 4.104 | 98.496 | a41: 98.496; a42: 8.1; a43: 8.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2249850; a109: 1114; a111: 1114 | 1114 | 271.4425 |  |  | Start Up Error | SU
2018-10-20 | 51:00 | 4:00 | 4 | 2.8169 | 7 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8905629 |  |  |  | 3984 | 3.984 | 95.616 | a41: 95.616; a42: 9.5; a43: 9.5; a47: 3B; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2250944; a109: 1094; a111: 1094 | 1094 | 274.5984 |  |  | Shutdown Error | SE
2018-10-20 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 82 | 57.7465 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8909742 |  |  |  | 4113 | 4.113 | 98.712 | a41: 98.712; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2251992; a109: 1048; a111: 1048 | 1048 | 254.8018 |  |  | Error - General | E
2018-10-20 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8914448 |  |  |  | 4706 | 4.706 | 112.944 | a41: 112.944; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2253112; a109: 1120; a111: 1120 | 1120 | 237.9941 | 1.05 |  | Power Interruption | PI
2018-10-20 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8919202 |  |  |  | 4754 | 4.754 | 114.096 | a41: 114.096; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2254170; a109: 1058; a111: 1058 | 1058 | 222.5494 |  |  | Water Interruption | WI
2018-10-20 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8924321 |  |  |  | 5119 | 5.119 | 122.856 | a41: 122.856; a42: 9.6; a43: 9.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2255401; a109: 1231; a111: 1231 | 1231 | 240.4767 |  |  | Equipment Maintenance | EM
2018-10-20 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8928952 |  |  |  | 4631 | 4.631 | 111.144 | a41: 111.144; a42: 8.4; a43: 8.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2256580; a109: 1179; a111: 1179 | 1179 | 254.5886
2018-10-20 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8933550 |  |  |  | 4598 | 4.598 | 110.352 | a41: 110.352; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2257801; a109: 1221; a111: 1221 | 1221 | 265.5502 | 1.1
2018-10-20 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8938120 |  |  |  | 4570 | 4.57 | 109.68 | a41: 109.68; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2259032; a109: 1231; a111: 1231 | 1231 | 269.3654 |  |  | UNITS
2018-10-20 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 71 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8942305 |  |  |  | 4185 | 4.185 | 100.44 | a41: 100.44; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2260184; a109: 1152; a111: 1152 | 1152 | 275.2688 |  |  | PRESSURE | Atmospheric Pressure
2018-10-20 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8946434 |  |  |  | 4129 | 4.129 | 99.096 | a41: 99.096; a42: 5.6; a43: 5.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2261377; a109: 1193; a111: 1193 | 1193 | 288.9319 |  |  | m of H2O | 14.7
2018-10-20 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8951314 |  |  |  | 4880 | 4.88 | 117.12 | a41: 117.12; a42: 5.2; a43: 5.2; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2262650; a109: 1273; a111: 1273 | 1273 | 260.8607 | 1.05 |  | psi | 10.36
2018-10-20 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8955360 |  |  |  | 4046 | 4.046 | 97.104 | a41: 97.104; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: 0%; a107: 2263741; a109: 1091; a111: 1091 | 1091 | 269.649 |  |  | bar | 1.0132
2018-10-20 | 63:00 | 16:00 | 4 | 2.8169 | 1 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8959560 |  |  |  | 4200 | 4.2 | 100.8 | a41: 100.8; a42: 3.9; a43: 3.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: 0%; a107: 2264888; a109: 1147; a111: 1147 | 1147 | 273.0952 |  |  | atm | 1
2018-10-20 | 64:00 | 17:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8963883 |  |  |  | 4323 | 4.323 | 103.752 | a41: 103.752; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2266035; a109: 1147; a111: 1147 | 1147 | 265.325 |  |  | kPA | 101.325
2018-10-20 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 73 | 51.4085 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8968305 |  |  |  | 4422 | 4.422 | 106.128 | a41: 106.128; a42: 3; a43: 3; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2267233; a109: 1198; a111: 1198 | 1198 | 270.9181 | 0.99
2018-10-20 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8972558 |  |  |  | 4253 | 4.253 | 102.072 | a41: 102.072; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2268366; a109: 1133; a111: 1133 | 1133 | 266.4002 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-20 | 67:00 | 20:00 | 4 | 2.8169 | -2 | 74 | 52.1127 | 72 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8976835 |  |  |  | 4277 | 4.277 | 102.648 | a41: 102.648; a42: 2.4; a43: 2.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2269508; a109: 1142; a111: 1142 | 1142 | 267.0096 |  |  | m of H2O | psi
2018-10-20 | 68:00 | 21:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8981293 |  |  |  | 4458 | 4.458 | 106.992 | a41: 106.992; a42: 2.2; a43: 2.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2270651; a109: 1143; a111: 1143 | 1143 | 256.393 |  |  | 1 | 1.4189
2018-10-20 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 68 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8986044 |  |  |  | 4751 | 4.751 | 114.024 | a41: 114.024; a42: 2; a43: 2; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1004; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.37%; a96: 0%; a107: 2271812; a109: 1161; a111: 1161 | 1161 | 244.3696 | 1.14
2018-10-20 | 70:00 | 23:00 | 4 | 2.8169 | 1 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8989976 |  |  |  | 3932 | 3.932 | 94.368 | a41: 94.368; a42: 2.8; a43: 2.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2272930; a109: 1118; a111: 1118 | 1118 | 284.3337 |  |  | FLOW | MLD
2018-10-20 | 71:00 | 24:00 | 4 | 2.8169 | 3 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8994204 |  |  |  | 4228 | 4.228 | 101.472 | a41: 101.472; a42: 3.8; a43: 3.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2274010; a109: 1080; a111: 1080 | 1080 | 255.4399 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.3333 | 74.5417 | 52.4941 | 72.3333 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 104233 | 104.233 | 104.233 | a42: 5.7667; a43: 5.7667; a106: 0; a109: 27487; a111: 27487 | 27487 | 263.7073 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | M.A. ESTOCHE / A. RAYALA II
| 2pm - 10pm | J.LLAGUNO / D. CAPIÑA
| 10pm - 6am | REY PROVIDENCIA/ FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 72PSI
XCV4 - CLOSED @ 3:57 AM WATER ELEVATION (9.5 M)
MEET THE TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE.
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 82PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 79 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
SP2 - STARTED @ 7:20 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 74 PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.0 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI

## 21
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-21
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 8994204 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2274010 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-21 | 48:00 | 1:00 | 4 | 2.8169 | 4 | 70 | 49.2958 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 8998022 |  |  |  | 3818 | 3.818 | 91.632 | a41: 91.632; a42: 5.3; a43: 5.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2275164; a109: 1154; a111: 1154 | 1154 | 302.2525 |  |  | Manual Operation | MO
2018-10-21 | 49:00 | 2:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9002106 |  |  |  | 4084 | 4.084 | 98.016 | a41: 98.016; a42: 6.9; a43: 6.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2276268; a109: 1104; a111: 1104 | 1104 | 270.3232 | 1.16 |  | Scheduled Shutdown | SS
2018-10-21 | 50:00 | 3:00 | 4 | 2.8169 | 7 | 73 | 51.4085 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9006444 |  |  |  | 4338 | 4.338 | 104.112 | a41: 104.112; a42: 8.3; a43: 8.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2277368; a109: 1100; a111: 1100 | 1100 | 253.5731 |  |  | Start Up Error | SU
2018-10-21 | 51:00 | 4:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 78 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9010102 |  |  |  | 3658 | 3.658 | 87.792 | a41: 87.792; a42: 9.5; a43: 9.5; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2278448; a109: 1080; a111: 1080 | 1080 | 295.2433 |  |  | Shutdown Error | SE
2018-10-21 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 78 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9014194 |  |  |  | 4092 | 4.092 | 98.208 | a41: 98.208; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2279496; a109: 1048; a111: 1048 | 1048 | 256.1095 |  |  | Error - General | E
2018-10-21 | 53:00 | 6:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9018723 |  |  |  | 4529 | 4.529 | 108.696 | a41: 108.696; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2280547; a109: 1051; a111: 1051 | 1051 | 232.0601 | 1.19 |  | Power Interruption | PI
2018-10-21 | 54:00 | 7:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 80 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9022951 |  |  |  | 4228 | 4.228 | 101.472 | a41: 101.472; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2281632; a109: 1085; a111: 1085 | 1085 | 256.6225 |  |  | Water Interruption | WI
2018-10-21 | 55:00 | 8:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9028056 |  |  |  | 5105 | 5.105 | 122.52 | a41: 122.52; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2282692; a109: 1060; a111: 1060 | 1060 | 207.6396 |  |  | Equipment Maintenance | EM
2018-10-21 | 56:00 | 9:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9032854 |  |  |  | 4798 | 4.798 | 115.152 | a41: 115.152; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2283859; a109: 1167; a111: 1167 | 1167 | 243.2263
2018-10-21 | 57:00 | 10:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9037991 |  |  |  | 5137 | 5.137 | 123.288 | a41: 123.288; a42: 8.6; a43: 8.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2285035; a109: 1176; a111: 1176 | 1176 | 228.9274 | 1.15
2018-10-21 | 58:00 | 11:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9043259 |  |  |  | 5268 | 5.268 | 126.432 | a41: 126.432; a42: 7.9; a43: 7.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2286256; a109: 1221; a111: 1221 | 1221 | 231.7768 |  |  | UNITS
2018-10-21 | 59:00 | 12:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9048436 |  |  |  | 5177 | 5.177 | 124.248 | a41: 124.248; a42: 7.3; a43: 7.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2287504; a109: 1248; a111: 1248 | 1248 | 241.0663 |  |  | PRESSURE | Atmospheric Pressure
2018-10-21 | 60:00 | 13:00 | 4 | 2.8169 | 6 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9052865 |  |  |  | 4429 | 4.429 | 106.296 | a41: 106.296; a42: 6.6; a43: 6.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2288639; a109: 1135; a111: 1135 | 1135 | 256.2655 |  |  | m of H2O | 14.7
2018-10-21 | 61:00 | 14:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9057647 |  |  |  | 4782 | 4.782 | 114.768 | a41: 114.768; a42: 6; a43: 6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 2289887; a109: 1248; a111: 1248 | 1248 | 260.9787 | 1.1 |  | psi | 10.36
2018-10-21 | 62:00 | 15:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 71 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9061982 |  |  |  | 4335 | 4.335 | 104.04 | a41: 104.04; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 2291007; a109: 1120; a111: 1120 | 1120 | 258.3622 |  |  | bar | 1.0132
2018-10-21 | 63:00 | 16:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9066670 |  |  |  | 4688 | 4.688 | 112.512 | a41: 112.512; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 2292253; a109: 1246; a111: 1246 | 1246 | 265.785 |  |  | atm | 1
2018-10-21 | 64:00 | 17:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9071236 |  |  |  | 4566 | 4.566 | 109.584 | a41: 109.584; a42: 4.3; a43: 4.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2293411; a109: 1158; a111: 1158 | 1158 | 253.6137 |  |  | kPA | 101.325
2018-10-21 | 65:00 | 18:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9076032 |  |  |  | 4796 | 4.796 | 115.104 | a41: 115.104; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2294596; a109: 1185; a111: 1185 | 1185 | 247.0809 | 1.12
2018-10-21 | 66:00 | 19:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9080308 |  |  |  | 4276 | 4.276 | 102.624 | a41: 102.624; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1025; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.13%; a89: 0%; a96: 0%; a107: 2295648; a109: 1052; a111: 1052 | 1052 | 246.0243 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-21 | 67:00 | 20:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9084788 |  |  |  | 4480 | 4.48 | 107.52 | a41: 107.52; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2296818; a109: 1170; a111: 1170 | 1170 | 261.1607 |  |  | m of H2O | psi
2018-10-21 | 68:00 | 21:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 70 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9089764 |  |  |  | 4976 | 4.976 | 119.424 | a41: 119.424; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2298036; a109: 1218; a111: 1218 | 1218 | 244.7749 |  |  | 1 | 1.4189
2018-10-21 | 69:00 | 22:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 70 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9094322 |  |  |  | 4558 | 4.558 | 109.392 | a41: 109.392; a42: 2.2; a43: 2.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1025; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.13%; a89: 0%; a96: 0%; a107: 2299168; a109: 1132; a111: 1132 | 1132 | 248.3545 | 1.18
2018-10-21 | 70:00 | 23:00 | 4 | 2.8169 | 3 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9098204 |  |  |  | 3882 | 3.882 | 93.168 | a41: 93.168; a42: 3; a43: 3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2300276; a109: 1108; a111: 1108 | 1108 | 285.4199 |  |  | FLOW | MLD
2018-10-21 | 71:00 | 24:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9102482 |  |  |  | 4278 | 4.278 | 102.672 | a41: 102.672; a42: 4; a43: 4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2301344; a109: 1068; a111: 1068 | 1068 | 249.6494 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 5.5 | 75.9167 | 53.4624 | 72.9167 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 108278 | 108.278 | 108.278 | a42: 6.2292; a43: 6.2292; a106: 0; a109: 27334; a111: 27334 | 27334 | 252.4428 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | M.A. ESTOCHE / A. RAYALA II
| 2pm - 10pm | A.RAYALA II/ D. CAPIÑA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI
XCV4 - CLOSED @ 3:40 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 83PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 83PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 83 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 83 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 78 PSI
SP1 - STARTED @ 8:12 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
MR. NOEL NERPIO AND SOUTH MAINTENANCE TEAM ARRIVE @ 2:37 PM TO CONDUCT WARM UP EXSERCISE OF GENSET 1&2 FOR 5 MINUTES.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 75 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.2 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 78PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 74PSI

## 22
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-22
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9102482 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2301344 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-22 | 48:00 | 1:00 | 4 | 2.8169 | 4 | 71 | 50 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9106568 |  |  |  | 4086 | 4.086 | 98.064 | a41: 98.064; a42: 5.9; a43: 5.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2302542; a109: 1198; a111: 1198 | 1198 | 293.1963 |  |  | Manual Operation | MO
2018-10-22 | 49:00 | 2:00 | 4 | 2.8169 | 6 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9110266 |  |  |  | 3698 | 3.698 | 88.752 | a41: 88.752; a42: 6.9; a43: 6.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2303570; a109: 1028; a111: 1028 | 1028 | 277.9881 | 1.16 |  | Scheduled Shutdown | SS
2018-10-22 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 74 | 52.1127 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9114148 |  |  |  | 3882 | 3.882 | 93.168 | a41: 93.168; a42: 8.4; a43: 8.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2304700; a109: 1130; a111: 1130 | 1130 | 291.0871 |  |  | Start Up Error | SU
2018-10-22 | 51:00 | 4:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9117944 |  |  |  | 3796 | 3.796 | 91.104 | a41: 91.104; a42: 9.5; a43: 9.5; a47: 3B; a48: 1156; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 97.14%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2305760; a109: 1060; a111: 1060 | 1060 | 279.2413 |  |  | Shutdown Error | SE
2018-10-22 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 78 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9123042 |  |  |  | 5098 | 5.098 | 122.352 | a41: 122.352; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2306955; a109: 1195; a111: 1195 | 1195 | 234.4056 |  |  | Error - General | E
2018-10-22 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9127051 |  |  |  | 4009 | 4.009 | 96.216 | a41: 96.216; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2307978; a109: 1023; a111: 1023 | 1023 | 255.1759 | 1.05 |  | Power Interruption | PI
2018-10-22 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 78 | 54.9296 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9131390 |  |  |  | 4339 | 4.339 | 104.136 | a41: 104.136; a42: 9.5; a43: 9.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: 0%; a107: 2309008; a109: 1030; a111: 1030 | 1030 | 237.3819 |  |  | Water Interruption | WI
2018-10-22 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9136391 |  |  |  | 5001 | 5.001 | 120.024 | a41: 120.024; a42: 9; a43: 9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2310211; a109: 1203; a111: 1203 | 1203 | 240.5519 |  |  | Equipment Maintenance | EM
2018-10-22 | 56:00 | 9:00 | 4 | 2.8169 | 7 | 75 | 52.8169 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9141210 |  |  |  | 4819 | 4.819 | 115.656 | a41: 115.656; a42: 8.3; a43: 8.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2311419; a109: 1208; a111: 1208 | 1208 | 250.6744
2018-10-22 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9145985 |  |  |  | 4775 | 4.775 | 114.6 | a41: 114.6; a42: 7.6; a43: 7.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1037; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.14%; a96: 0%; a107: 2312620; a109: 1201; a111: 1201 | 1201 | 251.5183 | 0.96
2018-10-22 | 58:00 | 11:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9150561 |  |  |  | 4576 | 4.576 | 109.824 | a41: 109.824; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1036; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 87.06%; a96: 0%; a107: 2313819; a109: 1199; a111: 1199 | 1199 | 262.0192 |  |  | UNITS
2018-10-22 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9155017 |  |  |  | 4456 | 4.456 | 106.944 | a41: 106.944; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: 0%; a107: 2315008; a109: 1189; a111: 1189 | 1189 | 266.8312 |  |  | PRESSURE | Atmospheric Pressure
2018-10-22 | 60:00 | 13:00 | 4 | 2.8169 | 5 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9159280 |  |  |  | 4263 | 4.263 | 102.312 | a41: 102.312; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: 0%; a107: 2316197; a109: 1189; a111: 1189 | 1189 | 278.9116 |  |  | m of H2O | 14.7
2018-10-22 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9163640 |  |  |  | 4360 | 4.36 | 104.64 | a41: 104.64; a42: 5; a43: 5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2317367; a109: 1170; a111: 1170 | 1170 | 268.3486 | 0.91 |  | psi | 10.36
2018-10-22 | 62:00 | 15:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9167980 |  |  |  | 4340 | 4.34 | 104.16 | a41: 104.16; a42: 4.9; a43: 4.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1006; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.54%; a96: 0%; a107: 2318539; a109: 1172; a111: 1172 | 1172 | 270.0461 |  |  | bar | 1.0132
2018-10-22 | 63:00 | 16:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9172300 |  |  |  | 4320 | 4.32 | 103.68 | a41: 103.68; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1005; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.45%; a96: 0%; a107: 2319696; a109: 1157; a111: 1157 | 1157 | 267.8241 |  |  | atm | 1
2018-10-22 | 64:00 | 17:00 | 4 | 2.8169 | -2 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9176540 |  |  |  | 4240 | 4.24 | 101.76 | a41: 101.76; a42: 4; a43: 4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2320831; a109: 1135; a111: 1135 | 1135 | 267.6887 |  |  | kPA | 101.325
2018-10-22 | 65:00 | 18:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9180885 |  |  |  | 4345 | 4.345 | 104.28 | a41: 104.28; a42: 3.6; a43: 3.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2322002; a109: 1171; a111: 1171 | 1171 | 269.5052 | 1.04
2018-10-22 | 66:00 | 19:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 70 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9185310 |  |  |  | 4425 | 4.425 | 106.2 | a41: 106.2; a42: 3.2; a43: 3.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2323177; a109: 1175; a111: 1175 | 1175 | 265.5367 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-22 | 67:00 | 20:00 | 4 | 2.8169 | -5 | 73 | 51.4085 | 70 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9189588 |  |  |  | 4278 | 4.278 | 102.672 | a41: 102.672; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2324342; a109: 1165; a111: 1165 | 1165 | 272.3235 |  |  | m of H2O | psi
2018-10-22 | 68:00 | 21:00 | 4 | 2.8169 | -5 | 74 | 52.1127 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9193918 |  |  |  | 4330 | 4.33 | 103.92 | a41: 103.92; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2325465; a109: 1123; a111: 1123 | 1123 | 259.3533 |  |  | 1 | 1.4189
2018-10-22 | 69:00 | 22:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 71 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9198678 |  |  |  | 4760 | 4.76 | 114.24 | a41: 114.24; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2326644; a109: 1179; a111: 1179 | 1179 | 247.6891 | 1.14
2018-10-22 | 70:00 | 23:00 | 4 | 2.8169 | 2 | 72 | 50.7042 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9202372 |  |  |  | 3694 | 3.694 | 88.656 | a41: 88.656; a42: 3.2; a43: 3.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2327708; a109: 1064; a111: 1064 | 1064 | 288.0347 |  |  | FLOW | MLD
2018-10-22 | 71:00 | 24:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9206364 |  |  |  | 3992 | 3.992 | 95.808 | a41: 95.808; a42: 4.3; a43: 4.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2328798; a109: 1090; a111: 1090 | 1090 | 273.0461 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.0833 | 75.4167 | 53.1103 | 72.9167 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 103882 | 103.882 | 103.882 | a42: 5.9792; a43: 5.9792; a106: 0; a109: 27454; a111: 27454 | 27454 | 264.2806 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | REY PROVIDENCIA / J. LLAGUNO
| 2pm - 10pm | GEORGE HERNANDEZ / DYAN ELVIN CAPIÑA
| 10pm - 6am | FIDEL RAMOS / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 74PSI
XCV4 - CLOSED @ 3:42 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 83PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 83PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
SP2 - STARTED @ 6:48 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 73PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 74 PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.3 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 77PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 75PSI

## 23
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-23
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9206364 | [10 empty] | 1.3m-10m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2328798 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-23 | 48:00 | 1:00 | 4 | 2.8169 | 4 | 72 | 50.7042 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9210228 |  |  |  | 3864 | 3.864 | 92.736 | a41: 92.736; a42: 5.8; a43: 5.8; a47: 3B; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2329934; a109: 1136; a111: 1136 | 1136 | 293.9959 |  |  | Manual Operation | MO
2018-10-23 | 49:00 | 2:00 | 4 | 2.8169 | 6 | 73 | 51.4085 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9214012 |  |  |  | 3784 | 3.784 | 90.816 | a41: 90.816; a42: 7.3; a43: 7.3; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2331080; a109: 1146; a111: 1146 | 1146 | 302.8541 | 1.16 |  | Scheduled Shutdown | SS
2018-10-23 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 73 | 51.4085 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9217798 |  |  |  | 3786 | 3.786 | 90.864 | a41: 90.864; a42: 8.8; a43: 8.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2332230; a109: 1150; a111: 1150 | 1150 | 303.7507 |  |  | Start Up Error | SU
2018-10-23 | 51:00 | 4:00 | 4 | 2.8169 | 9 | 83 | 58.4507 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9222038 |  |  |  | 4240 | 4.24 | 101.76 | a41: 101.76; a42: 9.5; a43: 9.5; a47: 3B; a48: 1166; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 97.98%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2333288; a109: 1058; a111: 1058 | 1058 | 249.5283 |  |  | Shutdown Error | SE
2018-10-23 | 52:00 | 5:00 | 4 | 2.8169 | 9 | 80 | 56.338 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9226206 |  |  |  | 4168 | 4.168 | 100.032 | a41: 100.032; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2334306; a109: 1018; a111: 1018 | 1018 | 244.2418 |  |  | Error - General | E
2018-10-23 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 79 | 55.6338 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9230938 |  |  |  | 4732 | 4.732 | 113.568 | a41: 113.568; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2335388; a109: 1082; a111: 1082 | 1082 | 228.656 | 1.09 |  | Power Interruption | PI
2018-10-23 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9235767 |  |  |  | 4829 | 4.829 | 115.896 | a41: 115.896; a42: 9; a43: 9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2336559; a109: 1171; a111: 1171 | 1171 | 242.4933 |  |  | Water Interruption | WI
2018-10-23 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9240930 |  |  |  | 5163 | 5.163 | 123.912 | a41: 123.912; a42: 8.3; a43: 8.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 2337765; a109: 1206; a111: 1206 | 1206 | 233.5851 |  |  | Equipment Maintenance | EM
2018-10-23 | 56:00 | 9:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9245415 |  |  |  | 4485 | 4.485 | 107.64 | a41: 107.64; a42: 7.7; a43: 7.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 2338921; a109: 1156; a111: 1156 | 1156 | 257.748
2018-10-23 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9250094 |  |  |  | 4679 | 4.679 | 112.296 | a41: 112.296; a42: 7; a43: 7; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 2340144; a109: 1223; a111: 1223 | 1223 | 261.3806 | 0.95
2018-10-23 | 58:00 | 11:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9254661 |  |  |  | 4567 | 4.567 | 109.608 | a41: 109.608; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 2341349; a109: 1205; a111: 1205 | 1205 | 263.8494 |  |  | UNITS
2018-10-23 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9259169 |  |  |  | 4508 | 4.508 | 108.192 | a41: 108.192; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 2342556; a109: 1207; a111: 1207 | 1207 | 267.7462 |  |  | PRESSURE | Atmospheric Pressure
2018-10-23 | 60:00 | 13:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9263438 |  |  |  | 4269 | 4.269 | 102.456 | a41: 102.456; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1017; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.46%; a89: 0%; a96: 0%; a107: 2343710; a109: 1154; a111: 1154 | 1154 | 270.3209 |  |  | m of H2O | 14.7
2018-10-23 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9267851 |  |  |  | 4413 | 4.413 | 105.912 | a41: 105.912; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2344905; a109: 1195; a111: 1195 | 1195 | 270.7908 | 0.9 |  | psi | 10.36
2018-10-23 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9272106 |  |  |  | 4255 | 4.255 | 102.12 | a41: 102.12; a42: 4.4; a43: 4.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2346035; a109: 1130; a111: 1130 | 1130 | 265.5699 |  |  | bar | 1.0132
2018-10-23 | 63:00 | 16:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9276619 |  |  |  | 4513 | 4.513 | 108.312 | a41: 108.312; a42: 4; a43: 4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2347207; a109: 1172; a111: 1172 | 1172 | 259.6942 |  |  | atm | 1
2018-10-23 | 64:00 | 17:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9280972 |  |  |  | 4353 | 4.353 | 104.472 | a41: 104.472; a42: 3.6; a43: 3.6; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2348355; a109: 1148; a111: 1148 | 1148 | 263.7262 |  |  | kPA | 101.325
2018-10-23 | 65:00 | 18:00 | 4 | 2.8169 | -1 | 73 | 51.4085 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9285361 |  |  |  | 4389 | 4.389 | 105.336 | a41: 105.336; a42: 3.2; a43: 3.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2349519; a109: 1164; a111: 1164 | 1164 | 265.2085 | 0.93
2018-10-23 | 66:00 | 19:00 | 4 | 2.8169 | -2 | 73 | 51.4085 | 71 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9289763 |  |  |  | 4402 | 4.402 | 105.648 | a41: 105.648; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1014; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.21%; a89: 0%; a96: 0%; a107: 2350699; a109: 1180; a111: 1180 | 1180 | 268.06 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-23 | 67:00 | 20:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 72 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9293887 |  |  |  | 4124 | 4.124 | 98.976 | a41: 98.976; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2351840; a109: 1141; a111: 1141 | 1141 | 276.6731 |  |  | m of H2O | psi
2018-10-23 | 68:00 | 21:00 | 4 | 2.8169 | -3 | 74 | 52.1127 | 72 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9298240 |  |  |  | 4353 | 4.353 | 104.472 | a41: 104.472; a42: 2.1; a43: 2.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2352999; a109: 1159; a111: 1159 | 1159 | 266.2532 |  |  | 1 | 1.4189
2018-10-23 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 77 | 54.2254 | 75 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9303310 |  |  |  | 5070 | 5.07 | 121.68 | a41: 121.68; a42: 1.9; a43: 1.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2354244; a109: 1245; a111: 1245 | 1245 | 245.5621 | 0.87
2018-10-23 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9306675 |  |  |  | 3365 | 3.365 | 80.76 | a41: 80.76; a42: 2.8; a43: 2.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2355284; a109: 1040; a111: 1040 | 1040 | 309.0639 |  |  | FLOW | MLD
2018-10-23 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9310565 |  |  |  | 3890 | 3.89 | 93.36 | a41: 93.36; a42: 4; a43: 4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2356384; a109: 1100; a111: 1100 | 1100 | 282.7763 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.1667 | 75.1667 | 52.9343 | 73.4167 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 104201 | 104.201 | 104.201 | a42: 5.6667; a43: 5.6667; a106: 0; a109: 27586; a111: 27586 | 27586 | 264.7383 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | R. PROVIDENCIA /M.A. ESTOCHE / A. RAYALA II
| 2pm - 10pm | A.RAYALA II / J. LLAGUNO
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI
XCV4 - CLOSED @ 3:18 AM WATER ELEVATION (9.5 M)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 83PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 80PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 79 PSI
SP1 - STARTED @ 6:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 73 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 74 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 1.9 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 77PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (16%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI

## 24
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-24
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9310565 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2356384 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-24 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9314190 |  |  |  | 3625 | 3.625 | 87 | a41: 87; a42: 5.7; a43: 5.7; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2357489; a109: 1105; a111: 1105 | 1105 | 304.8276 |  |  | Manual Operation | MO
2018-10-24 | 49:00 | 2:00 | 4 | 2.8169 | 3 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9318120 |  |  |  | 3930 | 3.93 | 94.32 | a41: 94.32; a42: 7.2; a43: 7.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2358616; a109: 1127; a111: 1127 | 1127 | 286.7684 | 0.86 |  | Scheduled Shutdown | SS
2018-10-24 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9322011 |  |  |  | 3891 | 3.891 | 93.384 | a41: 93.384; a42: 9; a43: 9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2359725; a109: 1109; a111: 1109 | 1109 | 285.0167 |  |  | Start Up Error | SU
2018-10-24 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9325750 |  |  |  | 3739 | 3.739 | 89.736 | a41: 89.736; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2360787; a109: 1062; a111: 1062 | 1062 | 284.0332 |  |  | Shutdown Error | SE
2018-10-24 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9329747 |  |  |  | 3997 | 3.997 | 95.928 | a41: 95.928; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2361812; a109: 1025; a111: 1025 | 1025 | 256.4423 |  |  | Error - General | E
2018-10-24 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9334410 |  |  |  | 4663 | 4.663 | 111.912 | a41: 111.912; a42: 9.5; a43: 9.5; a47: 3B; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2362931; a109: 1119; a111: 1119 | 1119 | 239.9743 | 0.9 |  | Power Interruption | PI
2018-10-24 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9339336 |  |  |  | 4926 | 4.926 | 118.224 | a41: 118.224; a42: 9.5; a43: 9.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2364067; a109: 1136; a111: 1136 | 1136 | 230.6131 |  |  | Water Interruption | WI
2018-10-24 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9344426 |  |  |  | 5090 | 5.09 | 122.16 | a41: 122.16; a42: 8.8; a43: 8.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2365267; a109: 1200; a111: 1200 | 1200 | 235.7564 |  |  | Equipment Maintenance | EM
2018-10-24 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9349061 |  |  |  | 4635 | 4.635 | 111.24 | a41: 111.24; a42: 8.2; a43: 8.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2366446; a109: 1179; a111: 1179 | 1179 | 254.3689
2018-10-24 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9353784 |  |  |  | 4723 | 4.723 | 113.352 | a41: 113.352; a42: 7.5; a43: 7.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2367656; a109: 1210; a111: 1210 | 1210 | 256.1931 | 1.12
2018-10-24 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9358420 |  |  |  | 4636 | 4.636 | 111.264 | a41: 111.264; a42: 6.9; a43: 6.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2368832; a109: 1176; a111: 1176 | 1176 | 253.667 |  |  | UNITS
2018-10-24 | 59:00 | 12:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9362894 |  |  |  | 4474 | 4.474 | 107.376 | a41: 107.376; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2370025; a109: 1193; a111: 1193 | 1193 | 266.6518 |  |  | PRESSURE | Atmospheric Pressure
2018-10-24 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9367199 |  |  |  | 4305 | 4.305 | 103.32 | a41: 103.32; a42: 5.7; a43: 5.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2371219; a109: 1194; a111: 1194 | 1194 | 277.3519 |  |  | m of H2O | 14.7
2018-10-24 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9371760 |  |  |  | 4561 | 4.561 | 109.464 | a41: 109.464; a42: 5.2; a43: 5.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1016; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.38%; a96: 0%; a107: 2372418; a109: 1199; a111: 1199 | 1199 | 262.8809 | 1.03 |  | psi | 10.36
2018-10-24 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9376024 |  |  |  | 4264 | 4.264 | 102.336 | a41: 102.336; a42: 4.7; a43: 4.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1017; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.46%; a96: 0%; a107: 2373562; a109: 1144; a111: 1144 | 1144 | 268.2927 |  |  | bar | 1.0132
2018-10-24 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9380448 |  |  |  | 4424 | 4.424 | 106.176 | a41: 106.176; a42: 4.3; a43: 4.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2374738; a109: 1176; a111: 1176 | 1176 | 265.8228 |  |  | atm | 1
2018-10-24 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9384855 |  |  |  | 4407 | 4.407 | 105.768 | a41: 105.768; a42: 3.8; a43: 3.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2375891; a109: 1153; a111: 1153 | 1153 | 261.6292 |  |  | kPA | 101.325
2018-10-24 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9389562 |  |  |  | 4707 | 4.707 | 112.968 | a41: 112.968; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2377053; a109: 1162; a111: 1162 | 1162 | 246.8664 | 1.09
2018-10-24 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9394272 |  |  |  | 4710 | 4.71 | 113.04 | a41: 113.04; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2378228; a109: 1175; a111: 1175 | 1175 | 249.4692 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-24 | 67:00 | 20:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9398819 |  |  |  | 4547 | 4.547 | 109.128 | a41: 109.128; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2379364; a109: 1136; a111: 1136 | 1136 | 249.8351 |  |  | m of H2O | psi
2018-10-24 | 68:00 | 21:00 | 4 | 0 | -1 | 76 | 53.5211 | 74 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9403647 |  |  |  | 4828 | 4.828 | 115.872 | a41: 115.872; a42: 2.4; a43: 2.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2380511; a109: 1147; a111: 1147 | 1147 | 237.5725 |  |  | 1 | 1.4189
2018-10-24 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 77 | 54.2254 | 75 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9408450 |  |  |  | 4803 | 4.803 | 115.272 | a41: 115.272; a42: 2.3; a43: 2.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2381673; a109: 1162; a111: 1162 | 1162 | 241.9321 | 0.81
2018-10-24 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9412000 |  |  |  | 3550 | 3.55 | 85.2 | a41: 85.2; a42: 3.4; a43: 3.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2382726; a109: 1053; a111: 1053 | 1053 | 296.6197 |  |  | FLOW | MLD
2018-10-24 | 71:00 | 24:00 | 4 | 2.8169 | -2 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9416480 |  |  |  | 4480 | 4.48 | 107.52 | a41: 107.52; a42: 5; a43: 5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2383875; a109: 1149; a111: 1149 | 1149 | 256.4732 |  |  | MLD | 1
|  |  | 4 | 2.6995 | 3.0417 | 75.0833 | 52.8756 | 73 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 105915 | 105.915 | 105.915 | a42: 5.9792; a43: 5.9792; a106: 0; a109: 27491; a111: 27491 | 27491 | 259.5572 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA / D. E. CAPIÑA
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 73 PSI
XCV4 - CLOSED @ 3:20 AM RESERVOIR WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE/ ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
SP1 - STARTED @ 6:30 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @11:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @12:01 PM AS PER SCHEDULE/ ACTUAL READING 7 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 76 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.3 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 77PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI

## 25
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-25
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9416480 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2383875 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-25 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9420170 |  |  |  | 3690 | 3.69 | 88.56 | a41: 88.56; a42: 6.5; a43: 6.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2384975; a109: 1100; a111: 1100 | 1100 | 298.103 |  |  | Manual Operation | MO
2018-10-25 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9424100 |  |  |  | 3930 | 3.93 | 94.32 | a41: 94.32; a42: 8.5; a43: 8.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2386085; a109: 1110; a111: 1110 | 1110 | 282.4427 | 1.01 |  | Scheduled Shutdown | SS
2018-10-25 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9427911 |  |  |  | 3811 | 3.811 | 91.464 | a41: 91.464; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2387172; a109: 1087; a111: 1087 | 1087 | 285.227 |  |  | Start Up Error | SU
2018-10-25 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9431800 |  |  |  | 3889 | 3.889 | 93.336 | a41: 93.336; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2388175; a109: 1003; a111: 1003 | 1003 | 257.9069 |  |  | Shutdown Error | SE
2018-10-25 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9435930 |  |  |  | 4130 | 4.13 | 99.12 | a41: 99.12; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2389195; a109: 1020; a111: 1020 | 1020 | 246.9734 |  |  | Error - General | E
2018-10-25 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 78 | 54.9296 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9440625 |  |  |  | 4695 | 4.695 | 112.68 | a41: 112.68; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2390306; a109: 1111; a111: 1111 | 1111 | 236.6347 | 1.1 |  | Power Interruption | PI
2018-10-25 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9445179 |  |  |  | 4554 | 4.554 | 109.296 | a41: 109.296; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2391387; a109: 1081; a111: 1081 | 1081 | 237.3737 |  |  | Water Interruption | WI
2018-10-25 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9449971 |  |  |  | 4792 | 4.792 | 115.008 | a41: 115.008; a42: 9.3; a43: 9.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1028; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.39%; a89: 0%; a96: 0%; a107: 2392550; a109: 1163; a111: 1163 | 1163 | 242.6962 |  |  | Equipment Maintenance | EM
2018-10-25 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9454485 |  |  |  | 4514 | 4.514 | 108.336 | a41: 108.336; a42: 8.6; a43: 8.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2393712; a109: 1162; a111: 1162 | 1162 | 257.4214
2018-10-25 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9459504 |  |  |  | 5019 | 5.019 | 120.456 | a41: 120.456; a42: 8; a43: 8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2394939; a109: 1227; a111: 1227 | 1227 | 244.471 | 1.15
2018-10-25 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9464103 |  |  |  | 4599 | 4.599 | 110.376 | a41: 110.376; a42: 7.4; a43: 7.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2396145; a109: 1206; a111: 1206 | 1206 | 262.2309 |  |  | UNITS
2018-10-25 | 59:00 | 12:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9468689 |  |  |  | 4586 | 4.586 | 110.064 | a41: 110.064; a42: 6.8; a43: 6.8; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2397363; a109: 1218; a111: 1218 | 1218 | 265.5909 |  |  | PRESSURE | Atmospheric Pressure
2018-10-25 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9473239 |  |  |  | 4550 | 4.55 | 109.2 | a41: 109.2; a42: 6.3; a43: 6.3; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2398506; a109: 1143; a111: 1143 | 1143 | 251.2088 |  |  | m of H2O | 14.7
2018-10-25 | 61:00 | 14:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9477661 |  |  |  | 4422 | 4.422 | 106.128 | a41: 106.128; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2399708; a109: 1202; a111: 1202 | 1202 | 271.8227 | 0.98 |  | psi | 10.36
2018-10-25 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9481893 |  |  |  | 4232 | 4.232 | 101.568 | a41: 101.568; a42: 5.4; a43: 5.4; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2400855; a109: 1147; a111: 1147 | 1147 | 271.0302 |  |  | bar | 1.0132
2018-10-25 | 63:00 | 16:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9486152 |  |  |  | 4259 | 4.259 | 102.216 | a41: 102.216; a42: 5; a43: 5; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2402010; a109: 1155; a111: 1155 | 1155 | 271.1904 |  |  | atm | 1
2018-10-25 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9490438 |  |  |  | 4286 | 4.286 | 102.864 | a41: 102.864; a42: 4.7; a43: 4.7; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2403166; a109: 1156; a111: 1156 | 1156 | 269.7154 |  |  | kPA | 101.325
2018-10-25 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9494715 |  |  |  | 4277 | 4.277 | 102.648 | a41: 102.648; a42: 4.3; a43: 4.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2404330; a109: 1164; a111: 1164 | 1164 | 272.1534 | 1.09
2018-10-25 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9499100 |  |  |  | 4385 | 4.385 | 105.24 | a41: 105.24; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2405496; a109: 1166; a111: 1166 | 1166 | 265.9065 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-25 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 74 | 52.1127 | 72 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9503234 |  |  |  | 4134 | 4.134 | 99.216 | a41: 99.216; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2406653; a109: 1157; a111: 1157 | 1157 | 279.8742 |  |  | m of H2O | psi
2018-10-25 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9507395 |  |  |  | 4161 | 4.161 | 99.864 | a41: 99.864; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2407804; a109: 1151; a111: 1151 | 1151 | 276.6162 |  |  | 1 | 1.4189
2018-10-25 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 74 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9511785 |  |  |  | 4390 | 4.39 | 105.36 | a41: 105.36; a42: 2.9; a43: 2.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2408956; a109: 1152; a111: 1152 | 1152 | 262.4146 | 0.78
2018-10-25 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9515230 |  |  |  | 3445 | 3.445 | 82.68 | a41: 82.68; a42: 4.1; a43: 4.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2410059; a109: 1103; a111: 1103 | 1103 | 320.1742 |  |  | FLOW | MLD
2018-10-25 | 71:00 | 24:00 | 4 | 2.8169 | -5 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9518800 |  |  |  | 3570 | 3.57 | 85.68 | a41: 85.68; a42: 5.4; a43: 5.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2411173; a109: 1114; a111: 1114 | 1114 | 312.0448 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.6667 | 75.5833 | 53.2277 | 73.4583 | [20 empty] | -409882 |  |  |  |  | 102320 | 102.32 | 102.32 | a42: 6.5292; a43: 6.5292; a106: 0; a109: 27298; a111: 27298 | 27298 | 266.7905 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA/ FIDEL RAMOS
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 69 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 72 PSI
XCV4 - CLOSED @ 2:45 AM RESERVOIR WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @12:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 74PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
PEST CONTROL LEAD BY JAYSON NIDUA ARRIVE @ 7:26 PM PM FOR SPRAYING/MISTING/SPOT TREAT MENT FOR TERMITE (IF POSITIVE)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 75 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.9 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 77PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 69 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI

## 26
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-26
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9518800 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2411173 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-26 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9522078 |  |  |  | 3278 | 3.278 | 78.672 | a41: 78.672; a42: 6.9; a43: 6.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2412304; a109: 1131; a111: 1131 | 1131 | 345.0275 |  |  | Manual Operation | MO
2018-10-26 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9525480 |  |  |  | 3402 | 3.402 | 81.648 | a41: 81.648; a42: 8.4; a43: 8.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2413393; a109: 1089; a111: 1089 | 1089 | 320.1058 | 0.89 |  | Scheduled Shutdown | SS
2018-10-26 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9529160 |  |  |  | 3680 | 3.68 | 88.32 | a41: 88.32; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2414478; a109: 1085; a111: 1085 | 1085 | 294.837 |  |  | Start Up Error | SU
2018-10-26 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9532790 |  |  |  | 3630 | 3.63 | 87.12 | a41: 87.12; a42: 9.5; a43: 9.5; a47: 3B; a48: 1146; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.3%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2415523; a109: 1045; a111: 1045 | 1045 | 287.8788 |  |  | Shutdown Error | SE
2018-10-26 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9536570 |  |  |  | 3780 | 3.78 | 90.72 | a41: 90.72; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2416542; a109: 1019; a111: 1019 | 1019 | 269.5767 |  |  | Error - General | E
2018-10-26 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9540839 |  |  |  | 4269 | 4.269 | 102.456 | a41: 102.456; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2417683; a109: 1141; a111: 1141 | 1141 | 267.2757 | 0.91 |  | Power Interruption | PI
2018-10-26 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9545573 |  |  |  | 4734 | 4.734 | 113.616 | a41: 113.616; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2418785; a109: 1102; a111: 1102 | 1102 | 232.7841 |  |  | Water Interruption | WI
2018-10-26 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9550399 |  |  |  | 4826 | 4.826 | 115.824 | a41: 115.824; a42: 9.1; a43: 9.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2419973; a109: 1188; a111: 1188 | 1188 | 246.1666 |  |  | Equipment Maintenance | EM
2018-10-26 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9554922 |  |  |  | 4523 | 4.523 | 108.552 | a41: 108.552; a42: 8.4; a43: 8.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2421135; a109: 1162; a111: 1162 | 1162 | 256.9091
2018-10-26 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9559657 |  |  |  | 4735 | 4.735 | 113.64 | a41: 113.64; a42: 7.8; a43: 7.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2422364; a109: 1229; a111: 1229 | 1229 | 259.5565 | 1.01
2018-10-26 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9564241 |  |  |  | 4584 | 4.584 | 110.016 | a41: 110.016; a42: 7.2; a43: 7.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: 0%; a107: 2423563; a109: 1199; a111: 1199 | 1199 | 261.562 |  |  | UNITS
2018-10-26 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9568743 |  |  |  | 4502 | 4.502 | 108.048 | a41: 108.048; a42: 6.6; a43: 6.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2424724; a109: 1161; a111: 1161 | 1161 | 257.8854 |  |  | PRESSURE | Atmospheric Pressure
2018-10-26 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9573107 |  |  |  | 4364 | 4.364 | 104.736 | a41: 104.736; a42: 6; a43: 6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2425907; a109: 1183; a111: 1183 | 1183 | 271.0816 |  |  | m of H2O | 14.7
2018-10-26 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9577602 |  |  |  | 4495 | 4.495 | 107.88 | a41: 107.88; a42: 5.4; a43: 5.4; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1012; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 85.04%; a96: 0%; a107: 2427099; a109: 1192; a111: 1192 | 1192 | 265.1835 | 0.87 |  | psi | 10.36
2018-10-26 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9581957 |  |  |  | 4355 | 4.355 | 104.52 | a41: 104.52; a42: 5; a43: 5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2428278; a109: 1179; a111: 1179 | 1179 | 270.7233 |  |  | bar | 1.0132
2018-10-26 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9586281 |  |  |  | 4324 | 4.324 | 103.776 | a41: 103.776; a42: 4.6; a43: 4.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2429434; a109: 1156; a111: 1156 | 1156 | 267.3451 |  |  | atm | 1
2018-10-26 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 74 | 52.1127 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9590603 |  |  |  | 4322 | 4.322 | 103.728 | a41: 103.728; a42: 4.2; a43: 4.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2430585; a109: 1151; a111: 1151 | 1151 | 266.3119 |  |  | kPA | 101.325
2018-10-26 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 73 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9594925 |  |  |  | 4322 | 4.322 | 103.728 | a41: 103.728; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2431741; a109: 1156; a111: 1156 | 1156 | 267.4688 | 0.94
2018-10-26 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 74 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9599329 |  |  |  | 4404 | 4.404 | 105.696 | a41: 105.696; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2432908; a109: 1167; a111: 1167 | 1167 | 264.9864 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-26 | 67:00 | 20:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 74 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9603800 |  |  |  | 4471 | 4.471 | 107.304 | a41: 107.304; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2434104; a109: 1196; a111: 1196 | 1196 | 267.5017 |  |  | m of H2O | psi
2018-10-26 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 75 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9608180 |  |  |  | 4380 | 4.38 | 105.12 | a41: 105.12; a42: 2.6; a43: 2.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2435243; a109: 1139; a111: 1139 | 1139 | 260.0457 |  |  | 1 | 1.4189
2018-10-26 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 74 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9612562 |  |  |  | 4382 | 4.382 | 105.168 | a41: 105.168; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2436369; a109: 1126; a111: 1126 | 1126 | 256.9603 | 0.86
2018-10-26 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9618270 |  |  |  | 5708 | 5.708 | 136.992 | a41: 136.992; a42: 3.5; a43: 3.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2437478; a109: 1109; a111: 1109 | 1109 | 194.2887 |  |  | FLOW | MLD
2018-10-26 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9619950 |  |  |  | 1680 | 1.68 | 40.32 | a41: 40.32; a42: 5; a43: 5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2438589; a109: 1111; a111: 1111 | 1111 | 661.3095 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.125 | 75.7917 | 53.3744 | 74 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 101150 | 101.15 | 101.15 | a42: 6.2792; a43: 6.2792; a106: 0; a109: 27416; a111: 27416 | 27416 | 271.043 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | J.LLAGUNO / D. CAPIÑA
| 10pm - 6am | REY PROVIDENCIA / GEORGE HERNANDEZ
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 73 PSI
XCV4 - CLOSED @ 2:45 AM RESERVOIR WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
SP2 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 79 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @1:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
R. DE LEON AND TEAM OF I.T. ARRIVE @ 1:40 PM FOR PULL OUT OF CPU SCADA.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @2:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @3:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 76 PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.5 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 71 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 69 PSI

## 27
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-27
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9619950 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2438589 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-27 | 48:00 | 1:00 | 4 | 2.8169 | 2 | 68 | 47.8873 | 66 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9623270 |  |  |  | 3320 | 3.32 | 79.68 | a41: 79.68; a42: 6.8; a43: 6.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2439740; a109: 1151; a111: 1151 | 1151 | 346.6867 |  |  | Manual Operation | MO
2018-10-27 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 69 | 48.5915 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9626738 |  |  |  | 3468 | 3.468 | 83.232 | a41: 83.232; a42: 8.6; a43: 8.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2440855; a109: 1115; a111: 1115 | 1115 | 321.511 | 1.03 |  | Scheduled Shutdown | SS
2018-10-27 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9630333 |  |  |  | 3595 | 3.595 | 86.28 | a41: 86.28; a42: 9.5; a43: 9.5; a47: 3B; a48: 1148; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.47%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2441930; a109: 1075; a111: 1075 | 1075 | 299.0264 |  |  | Start Up Error | SU
2018-10-27 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9633950 |  |  |  | 3617 | 3.617 | 86.808 | a41: 86.808; a42: 9.5; a43: 9.5; a47: 3B; a48: 1095; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 92.02%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2442895; a109: 965; a111: 965 | 965 | 266.7957 |  |  | Shutdown Error | SE
2018-10-27 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9637888 |  |  |  | 3938 | 3.938 | 94.512 | a41: 94.512; a42: 9.5; a43: 9.5; a47: 3B; a48: 1096; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 92.1%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2443914; a109: 1019; a111: 1019 | 1019 | 258.7608 |  |  | Error - General | E
2018-10-27 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9642164 |  |  |  | 4276 | 4.276 | 102.624 | a41: 102.624; a42: 9.5; a43: 9.5; a47: 3B; a48: 1096; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 92.1%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2444987; a109: 1073; a111: 1073 | 1073 | 250.9355 | 1.15 |  | Power Interruption | PI
2018-10-27 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9646376 |  |  |  | 4212 | 4.212 | 101.088 | a41: 101.088; a42: 9.5; a43: 9.5; a47: 3B+1S; a48: 1096; a49: 1185; a50: 0; a51: 1185; a64: 1028; a65: 0; a80: 92.1%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.39%; a89: 0%; a96: 0%; a107: 2445994; a109: 1007; a111: 1007 | 1007 | 239.0788 |  |  | Water Interruption | WI
2018-10-27 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9651098 |  |  |  | 4722 | 4.722 | 113.328 | a41: 113.328; a42: 8.9; a43: 8.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1028; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.39%; a89: 0%; a96: 0%; a107: 2447177; a109: 1183; a111: 1183 | 1183 | 250.5294 |  |  | Equipment Maintenance | EM
2018-10-27 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9656105 |  |  |  | 5007 | 5.007 | 120.168 | a41: 120.168; a42: 8.2; a43: 8.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2448397; a109: 1220; a111: 1220 | 1220 | 243.6589
2018-10-27 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9661316 |  |  |  | 5211 | 5.211 | 125.064 | a41: 125.064; a42: 7.5; a43: 7.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2449664; a109: 1267; a111: 1267 | 1267 | 243.1395 | 1.04
2018-10-27 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9665988 |  |  |  | 4672 | 4.672 | 112.128 | a41: 112.128; a42: 7; a43: 7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2450788; a109: 1124; a111: 1124 | 1124 | 240.5822 |  |  | UNITS
2018-10-27 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9670316 |  |  |  | 4328 | 4.328 | 103.872 | a41: 103.872; a42: 6.4; a43: 6.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2451930; a109: 1142; a111: 1142 | 1142 | 263.8632 |  |  | PRESSURE | Atmospheric Pressure
2018-10-27 | 60:00 | 13:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9675048 |  |  |  | 4732 | 4.732 | 113.568 | a41: 113.568; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1025; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.13%; a89: 0%; a96: 0%; a107: 2453168; a109: 1238; a111: 1238 | 1238 | 261.623 |  |  | m of H2O | 14.7
2018-10-27 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 74 | 52.1127 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9679465 |  |  |  | 4417 | 4.417 | 106.008 | a41: 106.008; a42: 5.2; a43: 5.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2454337; a109: 1169; a111: 1169 | 1169 | 264.6593 | 0.99 |  | psi | 10.36
2018-10-27 | 62:00 | 15:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9683918 |  |  |  | 4453 | 4.453 | 106.872 | a41: 106.872; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2455522; a109: 1185; a111: 1185 | 1185 | 266.1127 |  |  | bar | 1.0132
2018-10-27 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9688200 |  |  |  | 4282 | 4.282 | 102.768 | a41: 102.768; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2456666; a109: 1144; a111: 1144 | 1144 | 267.1649 |  |  | atm | 1
2018-10-27 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 72 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9692528 |  |  |  | 4328 | 4.328 | 103.872 | a41: 103.872; a42: 4; a43: 4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2457828; a109: 1162; a111: 1162 | 1162 | 268.4843 |  |  | kPA | 101.325
2018-10-27 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 72 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9696749 |  |  |  | 4221 | 4.221 | 101.304 | a41: 101.304; a42: 3.6; a43: 3.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2458990; a109: 1162; a111: 1162 | 1162 | 275.2902 | 1.07
2018-10-27 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9701235 |  |  |  | 4486 | 4.486 | 107.664 | a41: 107.664; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1006; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.54%; a89: 0%; a96: 0%; a107: 2460141; a109: 1151; a111: 1151 | 1151 | 256.576 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-27 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9705608 |  |  |  | 4373 | 4.373 | 104.952 | a41: 104.952; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2461298; a109: 1157; a111: 1157 | 1157 | 264.5781 |  |  | m of H2O | psi
2018-10-27 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9710006 |  |  |  | 4398 | 4.398 | 105.552 | a41: 105.552; a42: 2.7; a43: 2.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2462436; a109: 1138; a111: 1138 | 1138 | 258.754 |  |  | 1 | 1.4189
2018-10-27 | 69:00 | 22:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9714681 |  |  |  | 4675 | 4.675 | 112.2 | a41: 112.2; a42: 2.5; a43: 2.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1005; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 84.45%; a89: 0%; a96: 0%; a107: 2463598; a109: 1162; a111: 1162 | 1162 | 248.5561 | 0.95
2018-10-27 | 70:00 | 23:00 | 4 | 2.8169 | 1 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9718707 |  |  |  | 4026 | 4.026 | 96.624 | a41: 96.624; a42: 3.1; a43: 3.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2464703; a109: 1105; a111: 1105 | 1105 | 274.466 |  |  | FLOW | MLD
2018-10-27 | 71:00 | 24:00 | 4 | 2.8169 | 2 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF | DEF | DEF | [5 empty] | 9722676 |  |  |  | 3969 | 3.969 | 95.256 | a41: 95.256; a42: 4; a43: 4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2465806; a109: 1103; a111: 1103 | 1103 | 277.9038 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.5 | 75.5417 | 53.1984 | 73.5 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 102726 | 102.726 | 102.726 | a42: 6.1417; a43: 6.1417; a106: 0; a109: 27217; a111: 27217 | 27217 | 264.9475 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | J.LLAGUNO / D. CAPIÑA
| 10pm - 6am | REY PROVIDENCIA/ FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 68 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 69 PSI
XCV4 - CLOSED @ 2:30 AM RESERVOIR WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
SP1 - STARTED @ 6:48 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @2:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @3:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 75 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.5 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 77PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 72PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 75 PSI

## 28
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-28
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9722676 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2465806 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-28 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9726260 |  |  |  | 3584 | 3.584 | 86.016 | a41: 86.016; a42: 5.4; a43: 5.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2466909; a109: 1103; a111: 1103 | 1103 | 307.7567 |  |  | Manual Operation | MO
2018-10-28 | 49:00 | 2:00 | 4 | 2.8169 | 4 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9729889 |  |  |  | 3629 | 3.629 | 87.096 | a41: 87.096; a42: 6.9; a43: 6.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2468010; a109: 1101; a111: 1101 | 1101 | 303.3894 | 1.03 |  | Scheduled Shutdown | SS
2018-10-28 | 50:00 | 3:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9733599 |  |  |  | 3710 | 3.71 | 89.04 | a41: 89.04; a42: 8.4; a43: 8.4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2469122; a109: 1112; a111: 1112 | 1112 | 299.7305 |  |  | Start Up Error | SU
2018-10-28 | 51:00 | 4:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 79 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9737223 |  |  |  | 3624 | 3.624 | 86.976 | a41: 86.976; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2470136; a109: 1014; a111: 1014 | 1014 | 279.8013 |  |  | Shutdown Error | SE
2018-10-28 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9741047 |  |  |  | 3824 | 3.824 | 91.776 | a41: 91.776; a42: 9.5; a43: 9.5; a47: 3B; a48: 1154; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.97%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2471184; a109: 1048; a111: 1048 | 1048 | 274.0586 |  |  | Error - General | E
2018-10-28 | 53:00 | 6:00 | 4 | 2.8169 | 8 | 81 | 57.0423 | 79 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9745029 |  |  |  | 3982 | 3.982 | 95.568 | a41: 95.568; a42: 9.5; a43: 9.5; a47: 3B; a48: 1154; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.97%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2472188; a109: 1004; a111: 1004 | 1004 | 252.1346 | 1.11 |  | Power Interruption | PI
2018-10-28 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9749679 |  |  |  | 4650 | 4.65 | 111.6 | a41: 111.6; a42: 9.5; a43: 9.5; a47: 3B; a48: 1147; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.39%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2473287; a109: 1099; a111: 1099 | 1099 | 236.3441 |  |  | Water Interruption | WI
2018-10-28 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9754281 |  |  |  | 4602 | 4.602 | 110.448 | a41: 110.448; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2474377; a109: 1090; a111: 1090 | 1090 | 236.8535 |  |  | Equipment Maintenance | EM
2018-10-28 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9758954 |  |  |  | 4673 | 4.673 | 112.152 | a41: 112.152; a42: 9; a43: 9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1029; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.47%; a96: 0%; a107: 2475537; a109: 1160; a111: 1160 | 1160 | 248.2345
2018-10-28 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9763719 |  |  |  | 4765 | 4.765 | 114.36 | a41: 114.36; a42: 8.4; a43: 8.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: 0%; a107: 2476744; a109: 1207; a111: 1207 | 1207 | 253.3054 | 1.05
2018-10-28 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9768628 |  |  |  | 4909 | 4.909 | 117.816 | a41: 117.816; a42: 7.8; a43: 7.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1028; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.39%; a96: 0%; a107: 2477936; a109: 1192; a111: 1192 | 1192 | 242.8193 |  |  | UNITS
2018-10-28 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9773025 |  |  |  | 4397 | 4.397 | 105.528 | a41: 105.528; a42: 7.2; a43: 7.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2479123; a109: 1187; a111: 1187 | 1187 | 269.9568 |  |  | PRESSURE | Atmospheric Pressure
2018-10-28 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 74 | 52.1127 | 72 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9777593 |  |  |  | 4568 | 4.568 | 109.632 | a41: 109.632; a42: 6.6; a43: 6.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2480325; a109: 1202; a111: 1202 | 1202 | 263.1349 |  |  | m of H2O | 14.7
2018-10-28 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9782129 |  |  |  | 4536 | 4.536 | 108.864 | a41: 108.864; a42: 6; a43: 6; a47: 3B+1S; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2481522; a109: 1197; a111: 1197 | 1197 | 263.8889 | 0.97 |  | psi | 10.36
2018-10-28 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9786510 |  |  |  | 4381 | 4.381 | 105.144 | a41: 105.144; a42: 5.5; a43: 5.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2482702; a109: 1180; a111: 1180 | 1180 | 269.3449 |  |  | bar | 1.0132
2018-10-28 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 76 | 53.5211 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9790907 |  |  |  | 4397 | 4.397 | 105.528 | a41: 105.528; a42: 5.1; a43: 5.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2483854; a109: 1152; a111: 1152 | 1152 | 261.9968 |  |  | atm | 1
2018-10-28 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9795213 |  |  |  | 4306 | 4.306 | 103.344 | a41: 103.344; a42: 4.7; a43: 4.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2485018; a109: 1164; a111: 1164 | 1164 | 270.3205 |  |  | kPA | 101.325
2018-10-28 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 74 | 52.1127 | 73 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9799676 |  |  |  | 4463 | 4.463 | 107.112 | a41: 107.112; a42: 4.2; a43: 4.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1011; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.96%; a96: 0%; a107: 2486191; a109: 1173; a111: 1173 | 1173 | 262.8277 | 0.99
2018-10-28 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 76 | 53.5211 | 74 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9804074 |  |  |  | 4398 | 4.398 | 105.552 | a41: 105.552; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2487333; a109: 1142; a111: 1142 | 1142 | 259.6635 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-28 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 76 | 53.5211 | 74 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9808597 |  |  |  | 4523 | 4.523 | 108.552 | a41: 108.552; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2488508; a109: 1175; a111: 1175 | 1175 | 259.7833 |  |  | m of H2O | psi
2018-10-28 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 75 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9813158 |  |  |  | 4561 | 4.561 | 109.464 | a41: 109.464; a42: 3.1; a43: 3.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2489649; a109: 1141; a111: 1141 | 1141 | 250.1644 |  |  | 1 | 1.4189
2018-10-28 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 78 | 54.9296 | 76 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9818008 |  |  |  | 4850 | 4.85 | 116.4 | a41: 116.4; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1010; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 84.87%; a96: 0%; a107: 2490808; a109: 1159; a111: 1159 | 1159 | 238.9691 | 1.02
2018-10-28 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9822190 |  |  |  | 4182 | 4.182 | 100.368 | a41: 100.368; a42: 4; a43: 4; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2491957; a109: 1149; a111: 1149 | 1149 | 274.7489 |  |  | FLOW | MLD
2018-10-28 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9825853 |  |  |  | 3663 | 3.663 | 87.912 | a41: 87.912; a42: 5.8; a43: 5.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2493058; a109: 1101; a111: 1101 | 1101 | 300.5733 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3 | 75.6667 | 53.2864 | 73.625 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 103177 | 103.177 | 103.177 | a42: 6.4875; a43: 6.4875; a106: 0; a109: 27252; a111: 27252 | 27252 | 264.1286 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | A. RAYALA II/ D. E. CAPIÑA
| 10pm - 6am | G. HERNANDEZ / D. E. CAPIÑA
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 73PSI
XCV4 - CLOSED @ 3:31 AM WATER ELEVATION (9.5 M)
MEET TARGET DISCHARGE PRESSURE 75 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
MEET TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 83PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 81 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 80 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
SP1 - STARTED @ 8:11 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 AM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 AM AS PER SCHEDULE/ ACTUAL READING 75 PSI
MR. NOEL NERPIO AND SOUTH MAINTENANCE TEAM ARRIVE @ 2:37 PM TO CONDUCT WARM UP EXERCISE OF GENSET 1&2 FOR 5 MINUTES.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @3:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 76 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 77 PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.5 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 78PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 69 PSI

## 29
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-29
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9825853 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2493058 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-29 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9829550 |  |  |  | 3697 | 3.697 | 88.728 | a41: 88.728; a42: 7.5; a43: 7.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2494135; a109: 1077; a111: 1077 | 1077 | 291.3173 |  |  | Manual Operation | MO
2018-10-29 | 49:00 | 2:00 | 4 | 2.8169 | 6 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9833390 |  |  |  | 3840 | 3.84 | 92.16 | a41: 92.16; a42: 9.2; a43: 9.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2495232; a109: 1097; a111: 1097 | 1097 | 285.6771 | 0.84 |  | Scheduled Shutdown | SS
2018-10-29 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9837290 |  |  |  | 3900 | 3.9 | 93.6 | a41: 93.6; a42: 9.5; a43: 9.5; a47: 3B; a48: 1046; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 87.9%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2496307; a109: 1075; a111: 1075 | 1075 | 275.641 |  |  | Start Up Error | SU
2018-10-29 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9840840 |  |  |  | 3550 | 3.55 | 85.2 | a41: 85.2; a42: 9.5; a43: 9.5; a47: 3B; a48: 1045; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 87.82%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2497275; a109: 968; a111: 968 | 968 | 272.6761 |  |  | Shutdown Error | SE
2018-10-29 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9844430 |  |  |  | 3590 | 3.59 | 86.16 | a41: 86.16; a42: 9.5; a43: 9.5; a47: 3B; a48: 1147; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.39%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2498244; a109: 969; a111: 969 | 969 | 269.9164 |  |  | Error - General | E
2018-10-29 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9848649 |  |  |  | 4219 | 4.219 | 101.256 | a41: 101.256; a42: 9.5; a43: 9.5; a47: 3B; a48: 1186; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.66%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2499334; a109: 1090; a111: 1090 | 1090 | 258.3551 | 1.7 |  | Power Interruption | PI
2018-10-29 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9853252 |  |  |  | 4603 | 4.603 | 110.472 | a41: 110.472; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2500433; a109: 1099; a111: 1099 | 1099 | 238.7573 |  |  | Water Interruption | WI
2018-10-29 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9857920 |  |  |  | 4668 | 4.668 | 112.032 | a41: 112.032; a42: 9.3; a43: 9.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2501638; a109: 1205; a111: 1205 | 1205 | 258.1405 |  |  | Equipment Maintenance | EM
2018-10-29 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9862579 |  |  |  | 4659 | 4.659 | 111.816 | a41: 111.816; a42: 8.7; a43: 8.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2502825; a109: 1187; a111: 1187 | 1187 | 254.7757
2018-10-29 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9867450 |  |  |  | 4871 | 4.871 | 116.904 | a41: 116.904; a42: 8.1; a43: 8.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2504041; a109: 1216; a111: 1216 | 1216 | 249.6407 | 0.93
2018-10-29 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9872302 |  |  |  | 4852 | 4.852 | 116.448 | a41: 116.448; a42: 7.5; a43: 7.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2505223; a109: 1182; a111: 1182 | 1182 | 243.6109 |  |  | UNITS
2018-10-29 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9877017 |  |  |  | 4715 | 4.715 | 113.16 | a41: 113.16; a42: 6.8; a43: 6.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1037; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.14%; a89: 0%; a96: 0%; a107: 2506423; a109: 1200; a111: 1200 | 1200 | 254.5069 |  |  | PRESSURE | Atmospheric Pressure
2018-10-29 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9881622 |  |  |  | 4605 | 4.605 | 110.52 | a41: 110.52; a42: 6.2; a43: 6.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1036; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 87.06%; a89: 0%; a96: 0%; a107: 2507625; a109: 1202; a111: 1202 | 1202 | 261.0206 |  |  | m of H2O | 14.7
2018-10-29 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 74 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9886083 |  |  |  | 4461 | 4.461 | 107.064 | a41: 107.064; a42: 5.8; a43: 5.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2508785; a109: 1160; a111: 1160 | 1160 | 260.0314 | 0.97 |  | psi | 10.36
2018-10-29 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 77 | 54.2254 | 75 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9890693 |  |  |  | 4610 | 4.61 | 110.64 | a41: 110.64; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2509956; a109: 1171; a111: 1171 | 1171 | 254.013 |  |  | bar | 1.0132
2018-10-29 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9895454 |  |  |  | 4761 | 4.761 | 114.264 | a41: 114.264; a42: 5; a43: 5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2511139; a109: 1183; a111: 1183 | 1183 | 248.4772 |  |  | atm | 1
2018-10-29 | 64:00 | 17:00 | 4 | 2.8169 | 1 | 76 | 53.5211 | 74 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9900002 |  |  |  | 4548 | 4.548 | 109.152 | a41: 109.152; a42: 4.6; a43: 4.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2512294; a109: 1155; a111: 1155 | 1155 | 253.9578 |  |  | kPA | 101.325
2018-10-29 | 65:00 | 18:00 | 4 | 2.8169 | 0 | 74 | 52.1127 | 73 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9904516 |  |  |  | 4514 | 4.514 | 108.336 | a41: 108.336; a42: 4.1; a43: 4.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2513448; a109: 1154; a111: 1154 | 1154 | 255.6491 | 0.94
2018-10-29 | 66:00 | 19:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9909219 |  |  |  | 4703 | 4.703 | 112.872 | a41: 112.872; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2514630; a109: 1182; a111: 1182 | 1182 | 251.3289 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-29 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 75 | 52.8169 | 73 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9913988 |  |  |  | 4769 | 4.769 | 114.456 | a41: 114.456; a42: 3.3; a43: 3.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2515794; a109: 1164; a111: 1164 | 1164 | 244.0763 |  |  | m of H2O | psi
2018-10-29 | 68:00 | 21:00 | 4 | 2.8169 | -2 | 76 | 53.5211 | 74 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9918645 |  |  |  | 4657 | 4.657 | 111.768 | a41: 111.768; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1015; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.29%; a89: 0%; a96: 0%; a107: 2516944; a109: 1150; a111: 1150 | 1150 | 246.9401 |  |  | 1 | 1.4189
2018-10-29 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 76 | 53.5211 | 74 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9923344 |  |  |  | 4699 | 4.699 | 112.776 | a41: 112.776; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1016; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.38%; a89: 0%; a96: 0%; a107: 2518068; a109: 1124; a111: 1124 | 1124 | 239.1998 | 1.01
2018-10-29 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9927640 |  |  |  | 4296 | 4.296 | 103.104 | a41: 103.104; a42: 3.6; a43: 3.6; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2519186; a109: 1118; a111: 1118 | 1118 | 260.2421 |  |  | FLOW | MLD
2018-10-29 | 71:00 | 24:00 | 4 | 2.8169 | -2 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9931577 |  |  |  | 3937 | 3.937 | 94.488 | a41: 94.488; a42: 4.8; a43: 4.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2520272; a109: 1086; a111: 1086 | 1086 | 275.8446 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 2.9583 | 76.1667 | 53.6385 | 74.0833 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 105724 | 105.724 | 105.724 | a42: 6.5333; a43: 6.5333; a106: 0; a109: 27214; a111: 27214 | 27214 | 257.4061 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./JONEL LLAGUNO
| 2pm - 10pm | REY PROVIDENCIA / D. E. CAPIÑA
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 72PSI
XCV4 - CLOSED @ 2:15 AM RESERVOIR WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE / ACTUAL READING 79 PSI
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE / ACTUAL READING 76 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE / ACTUAL READING 78 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE / ACTUAL READING 77 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE / ACTUAL READING 77 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE / ACTUAL READING 76 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 76 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 74 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 75 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 76 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 2.8 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 76PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 70PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI

## 30
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-30
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 9931577 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2520272 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-30 | 48:00 | 1:00 | 4 | 2.8169 | 0 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9935509 |  |  |  | 3932 | 3.932 | 94.368 | a41: 94.368; a42: 6.5; a43: 6.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2521410; a109: 1138; a111: 1138 | 1138 | 289.4201 |  |  | Manual Operation | MO
2018-10-30 | 49:00 | 2:00 | 4 | 2.8169 | 3 | 72 | 50.7042 | 70 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9939380 |  |  |  | 3871 | 3.871 | 92.904 | a41: 92.904; a42: 8.2; a43: 8.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2522520; a109: 1110; a111: 1110 | 1110 | 286.7476 | 0.86 |  | Scheduled Shutdown | SS
2018-10-30 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9943240 |  |  |  | 3860 | 3.86 | 92.64 | a41: 92.64; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2523630; a109: 1110; a111: 1110 | 1110 | 287.5648 |  |  | Start Up Error | SU
2018-10-30 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9946899 |  |  |  | 3659 | 3.659 | 87.816 | a41: 87.816; a42: 9.5; a43: 9.5; a47: 3B; a48: 1096; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 92.1%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2524616; a109: 986; a111: 986 | 986 | 269.4725 |  |  | Shutdown Error | SE
2018-10-30 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9950740 |  |  |  | 3841 | 3.841 | 92.184 | a41: 92.184; a42: 9.5; a43: 9.5; a47: 3B; a48: 1147; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.39%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2525590; a109: 974; a111: 974 | 974 | 253.5798 |  |  | Error - General | E
2018-10-30 | 53:00 | 6:00 | 4 | 2.8169 | 7 | 80 | 56.338 | 78 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9955116 |  |  |  | 4376 | 4.376 | 105.024 | a41: 105.024; a42: 9.5; a43: 9.5; a47: 3B; a48: 1147; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 96.39%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2526681; a109: 1091; a111: 1091 | 1091 | 249.3144 | 0.93 |  | Power Interruption | PI
2018-10-30 | 54:00 | 7:00 | 4 | 2.8169 | 7 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9959836 |  |  |  | 4720 | 4.72 | 113.28 | a41: 113.28; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2527780; a109: 1099; a111: 1099 | 1099 | 232.839 |  |  | Water Interruption | WI
2018-10-30 | 55:00 | 8:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9964395 |  |  |  | 4559 | 4.559 | 109.416 | a41: 109.416; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2528906; a109: 1126; a111: 1126 | 1126 | 246.984 |  |  | Equipment Maintenance | EM
2018-10-30 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 78 | 54.9296 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9969169 |  |  |  | 4774 | 4.774 | 114.576 | a41: 114.576; a42: 9; a43: 9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2530097; a109: 1191; a111: 1191 | 1191 | 249.4763
2018-10-30 | 57:00 | 10:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9973861 |  |  |  | 4692 | 4.692 | 112.608 | a41: 112.608; a42: 8.4; a43: 8.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2531280; a109: 1183; a111: 1183 | 1183 | 252.1313 | 1.04
2018-10-30 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9978566 |  |  |  | 4705 | 4.705 | 112.92 | a41: 112.92; a42: 7.8; a43: 7.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2532478; a109: 1198; a111: 1198 | 1198 | 254.6227 |  |  | UNITS
2018-10-30 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9983301 |  |  |  | 4735 | 4.735 | 113.64 | a41: 113.64; a42: 7.2; a43: 7.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2533690; a109: 1212; a111: 1212 | 1212 | 255.9662 |  |  | PRESSURE | Atmospheric Pressure
2018-10-30 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 77 | 54.2254 | 75 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9988466 |  |  |  | 5165 | 5.165 | 123.96 | a41: 123.96; a42: 6.7; a43: 6.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1027; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.3%; a96: 0%; a107: 2534881; a109: 1191; a111: 1191 | 1191 | 230.5905 |  |  | m of H2O | 14.7
2018-10-30 | 61:00 | 14:00 | 4 | 2.8169 | 4 | 78 | 54.9296 | 76 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9993793 |  |  |  | 5327 | 5.327 | 127.848 | a41: 127.848; a42: 6.1; a43: 6.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2536077; a109: 1196; a111: 1196 | 1196 | 224.5166 | 0.95 |  | psi | 10.36
2018-10-30 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 76 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 9998415 |  |  |  | 4622 | 4.622 | 110.928 | a41: 110.928; a42: 5.7; a43: 5.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2537220; a109: 1143; a111: 1143 | 1143 | 247.2955 |  |  | bar | 1.0132
2018-10-30 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 80 | 56.338 | 78 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10003096 |  |  |  | 4681 | 4.681 | 112.344 | a41: 112.344; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1025; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.13%; a96: 0%; a107: 2538397; a109: 1177; a111: 1177 | 1177 | 251.442 |  |  | atm | 1
2018-10-30 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 77 | 54.2254 | 75 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10007994 |  |  |  | 4898 | 4.898 | 117.552 | a41: 117.552; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2539568; a109: 1171; a111: 1171 | 1171 | 239.0772 |  |  | kPA | 101.325
2018-10-30 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10013336 |  |  |  | 5342 | 5.342 | 128.208 | a41: 128.208; a42: 4.4; a43: 4.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2540752; a109: 1184; a111: 1184 | 1184 | 221.6398 | 0.89
2018-10-30 | 66:00 | 19:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 75 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10018414 |  |  |  | 5078 | 5.078 | 121.872 | a41: 121.872; a42: 4; a43: 4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2541886; a109: 1134; a111: 1134 | 1134 | 223.3163 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-30 | 67:00 | 20:00 | 4 | 2.8169 | -1 | 77 | 54.2254 | 75 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10023673 |  |  |  | 5259 | 5.259 | 126.216 | a41: 126.216; a42: 3.5; a43: 3.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1026; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.22%; a96: 0%; a107: 2543059; a109: 1173; a111: 1173 | 1173 | 223.0462 |  |  | m of H2O | psi
2018-10-30 | 68:00 | 21:00 | 4 | 2.8169 | -1 | 78 | 54.9296 | 76 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10028828 |  |  |  | 5155 | 5.155 | 123.72 | a41: 123.72; a42: 3.2; a43: 3.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1024; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.05%; a96: 0%; a107: 2544203; a109: 1144; a111: 1144 | 1144 | 221.9205 |  |  | 1 | 1.4189
2018-10-30 | 69:00 | 22:00 | 4 | 2.8169 | -5 | 80 | 56.338 | 78 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10033430 |  |  |  | 4602 | 4.602 | 110.448 | a41: 110.448; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 1024; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 86.05%; a96: 0%; a107: 2545344; a109: 1141; a111: 1141 | 1141 | 247.9357 | 0.93
2018-10-30 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 75 | 52.8169 | 73 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10037830 |  |  |  | 4400 | 4.4 | 105.6 | a41: 105.6; a42: 3.8; a43: 3.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2546472; a109: 1128; a111: 1128 | 1128 | 256.3636 |  |  | FLOW | MLD
2018-10-30 | 71:00 | 24:00 | 4 | 2.8169 | 2 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10041690 |  |  |  | 3860 | 3.86 | 92.64 | a41: 92.64; a42: 5.1; a43: 5.1; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2547585; a109: 1113; a111: 1113 | 1113 | 288.342 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.0417 | 77.5833 | 54.6362 | 75.4583 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 110113 | 110.113 | 110.113 | a42: 6.6542; a43: 6.6542; a106: 0; a109: 27313; a111: 27313 | 27313 | 248.0452 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | ESTOCHE M.A./PROVIDENCIA R.
| 2pm - 10pm | D.E. CAPIÑA / F. RAMOS
| 10pm - 6am | GEORGE HERNANDEZ / FIDEL RAMOS
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 72 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 72 PSI
XCV4 - CLOSED @ 2:50 AM RESERVOIR WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE / ACTUAL READING 77 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE / ACTUAL READING 78 PSI
SP2 - STARTED @ 7:54 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE / ACTUAL READING 78 PSI
ENGR. JOSSELLE REAMICO AND SOUTH MAINTENANCE TEAM TOGETHER WITH MS. MARITES PANGILINAN OF APSI AND TEAM ARRIVE @ 9:05 AM TO CONDUCT INSPECTION IN SUBSTATION PANEL/GENSET.
ENGR. THOMAS AMPARO ARRIVE @ 9:08 AM TO CONDUCT GENSET INSPECTION AND PERFORM NO LOAD TESTING FOR 5 MINUTES AND EXTRACT OIL SAMPLE FOR LABORATORY ANALYSIS.
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE / ACTUAL READING 77 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE / ACTUAL READING 77 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 PM AS PER SCHEDULE / ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 76 PSI @ 8:01 PM AS PER SCHEDULE / ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 8:01 PM TO 10:01 AM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 PM AS PER SCHEDULE / ACTUAL READING 78 PSI
SP2 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL.
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 PM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 75PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 71 PSI

## 31
BDOM DAILY OPERATION REPORT
WATER NETWORK
| LOCATION: | VILLAMOR PUMP STATION AND RESERVOIR
| DATE | 2018-10-31
| Time |  | Suction |  |  | Discharge |  |  | Discharge |  |  | Pressure Requirement |  |  |  | Pressure Requirement |  |  |  | Plant Status | Suction Flow |  | Discharge Flow |  | Discharge Flow |  | refilling 900mm | refilling via 800mm | Totalizer |  | Totalizer 700mm1 | Totalizer 700mm2 | Totalizer 1400mm | Hourly Production |  | Hourly Production | Hourly Production 700mm2 | Hourly Production 700mm2 | Hourly Production 1400mm | Total Hourly Production | Reservoir Level |  |  |  |  | No of units in operation | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | Motor Speed (RPM) | [7 empty] | Motor Speed (%) | [7 empty] | VALVE SETTING | [24 empty] | MULTIPLIER (700) | Totalizer KWHR | Totalizer KWHR | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Totalizer KWHR | Max KwHr | Max KwHr | Max KwHr | Max KwHr/ML | Chlorine Residual (mg/l) | Hourly Remarks | Details | Code | CENTRAL B BOOSTER OPERATION OPERATORS
| From | To | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | psi | (m) | Gauge Reading (psi) | Min | Target | Actual | Max | Min | Target | Actual | Max | [9 empty] | ML | m3 | MLD | MLD | MLD | m3 | ML | MLD | MLD | MLD | MLD | MLD | Chamber 1 | Chamber 2 | Old Reservoir (m) | Cell #3 (m) | Cell #4 (m) |  | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | BP1 | BP2 | BP3 | BP4 | BP5 | BP6 | BP7 | BP8 | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP | SP1 | SP2 | SP3 | SP4 | SP5 | SP6 | SP7 | SP8 | MOV1 BP1 | MOV2 BP2 | MOV3 BP3 | MOV4 BP4 | MOV5 BP5 | MOV6 BP6 | MOV7 BP7 | MOV8 BP8 | MOV1 SP1 | MOV2 SP2 | MOV3 SP3 | MOV4 SP4 | MOV5 SP5 | MOV6 SP6 | MOV7 SP7 | MOV8 SP8 | Reservoir Inlet XCVI | MOV OLD RSV. | MOV CELL #1 | MOV CELL #2 | RIV A | RIV B | Surface Water MOV | Deepwell MOV | Discharge MOV | Power Consumption Meralco rdg | Power Consumption MTS rdg (KWHr) | Power Consumption ATS rdg (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Power Consumption MCC1 rdg (KWHr) | Hourly Energy Consumption (KWHr) | Power Consumption MCC2 Reading | Hourly Energy Consumption (KWHr) | Hourly Power Consumption | Total Hourly Energry Consumption (KWHr) | Hourly KWHr per Production KWHr/ML |  |  | Automatic - i2O | AI
[12 empty] | (psi) | (psi) | (psi) | (psi) | (m) | (m) | (m) | (m) |  | m3/hr | MLD | m3/hr | MLD | Discharge 700mm Line 2 (MLD) | Discharge 1400mm Line (MLD) |  |  | 409882 | 10041690 | [10 empty] | 2.0m-13.8m | [5 empty] | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0 | 0 | >0 to <1185 | >0 to <1185 | >0 to <1185 | N/A | N/A | N/A | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% | 0%-100% |  |  | 2547585 | [11 empty] | 0.3-1.5 |  | Automatic - Pressure Setting | AP
date | from | to | a4 | a5 | a6 | a7 | a8 | a9 | a10 | a11 | a12 | a13 | a14 | a15 | a16 | a17 | a18 | a19 | a20 | a21 | a22 | a23 | a24 | a25 | a26 | a27 | a28 | a29 | a30 | a31 | a32 | a33 | a34 | a35 | a36 | total_pro_hour | a38 | a39 | a40 | a41 | a42 | a43 | a44 | a45 | a46 | a47 | a48 | a49 | a50 | a51 | a52 | a53 | a54 | a55 | a56 | a57 | a58 | a59 | a60 | a61 | a62 | a63 | a64 | a65 | a66 | a67 | a68 | a69 | a70 | a71 | a72 | a73 | a74 | a75 | a76 | a77 | a78 | a79 | a80 | a81 | a82 | a83 | a84 | a85 | a86 | a87 | a88 | a89 | a90 | a91 | a92 | a93 | a94 | a95 | a96 | a97 | a98 | a99 | a100 | a101 | a102 | a103 | a104 | a105 | a106 | a107 | a108 | a109 | a110 | a111 | a112 | a113 | a114 | a115 | a116 | total_power_hour | ratio | a119 | a120
2018-10-31 | 48:00 | 1:00 | 4 | 2.8169 | 3 | 70 | 49.2958 | 68 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10045410 |  |  |  | 3720 | 3.72 | 89.28 | a41: 89.28; a42: 6.9; a43: 6.9; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2548691; a109: 1106; a111: 1106 | 1106 | 297.3118 |  |  | Manual Operation | MO
2018-10-31 | 49:00 | 2:00 | 4 | 2.8169 | 5 | 73 | 51.4085 | 71 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10049300 |  |  |  | 3890 | 3.89 | 93.36 | a41: 93.36; a42: 8.8; a43: 8.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2549810; a109: 1119; a111: 1119 | 1119 | 287.6607 | 1.05 |  | Scheduled Shutdown | SS
2018-10-31 | 50:00 | 3:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10052962 |  |  |  | 3662 | 3.662 | 87.888 | a41: 87.888; a42: 9.5; a43: 9.5; a47: 3B; a48: 1065; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 89.5%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2550856; a109: 1046; a111: 1046 | 1046 | 285.6363 |  |  | Start Up Error | SU
2018-10-31 | 51:00 | 4:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10056685 |  |  |  | 3723 | 3.723 | 89.352 | a41: 89.352; a42: 9.5; a43: 9.5; a47: 3B; a48: 1064; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 89.41%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2551818; a109: 962; a111: 962 | 962 | 258.3938 |  |  | Shutdown Error | SE
2018-10-31 | 52:00 | 5:00 | 4 | 2.8169 | 8 | 83 | 58.4507 | 80 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10060530 |  |  |  | 3845 | 3.845 | 92.28 | a41: 92.28; a42: 9.5; a43: 9.5; a47: 3B; a48: 1035; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 86.97%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2552800; a109: 982; a111: 982 | 982 | 255.3966 |  |  | Error - General | E
2018-10-31 | 53:00 | 6:00 | 4 | 2.8169 | 9 | 82 | 57.7465 | 80 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10064364 |  |  |  | 3834 | 3.834 | 92.016 | a41: 92.016; a42: 9.5; a43: 9.5; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2553771; a109: 971; a111: 971 | 971 | 253.2603 | 0.96 |  | Power Interruption | PI
2018-10-31 | 54:00 | 7:00 | 4 | 2.8169 | 8 | 77 | 54.2254 | 76 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10068897 |  |  |  | 4533 | 4.533 | 108.792 | a41: 108.792; a42: 9.5; a43: 9.5; a47: 3B; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2554882; a109: 1111; a111: 1111 | 1111 | 245.0916 |  |  | Water Interruption | WI
2018-10-31 | 55:00 | 8:00 | 4 | 2.8169 | 7 | 79 | 55.6338 | 77 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10073649 |  |  |  | 4752 | 4.752 | 114.048 | a41: 114.048; a42: 9.2; a43: 9.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2556078; a109: 1196; a111: 1196 | 1196 | 251.6835 |  |  | Equipment Maintenance | EM
2018-10-31 | 56:00 | 9:00 | 4 | 2.8169 | 6 | 76 | 53.5211 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10078551 |  |  |  | 4902 | 4.902 | 117.648 | a41: 117.648; a42: 8.6; a43: 8.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2557302; a109: 1224; a111: 1224 | 1224 | 249.694
2018-10-31 | 57:00 | 10:00 | 4 | 2.8169 | 6 | 77 | 54.2254 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.9 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10083343 |  |  |  | 4792 | 4.792 | 115.008 | a41: 115.008; a42: 7.9; a43: 7.9; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1027; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.3%; a89: 0%; a96: 0%; a107: 2558488; a109: 1186; a111: 1186 | 1186 | 247.4958 | 1.08
2018-10-31 | 58:00 | 11:00 | 4 | 2.8169 | 5 | 76 | 53.5211 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10088126 |  |  |  | 4783 | 4.783 | 114.792 | a41: 114.792; a42: 7.3; a43: 7.3; a47: 3B+1S; a48: 1188; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.83%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2559683; a109: 1195; a111: 1195 | 1195 | 249.8432 |  |  | UNITS
2018-10-31 | 59:00 | 12:00 | 4 | 2.8169 | 4 | 76 | 53.5211 | 75 | [7 empty] | 57.0423 | 58.4507 |  | 59.8707 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10092879 |  |  |  | 4753 | 4.753 | 114.072 | a41: 114.072; a42: 6.8; a43: 6.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2560857; a109: 1174; a111: 1174 | 1174 | 247.0019 |  |  | PRESSURE | Atmospheric Pressure
2018-10-31 | 60:00 | 13:00 | 4 | 2.8169 | 4 | 75 | 52.8169 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10097379 |  |  |  | 4500 | 4.5 | 108 | a41: 108; a42: 6.2; a43: 6.2; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2562056; a109: 1199; a111: 1199 | 1199 | 266.4444 |  |  | m of H2O | 14.7
2018-10-31 | 61:00 | 14:00 | 4 | 2.8169 | 3 | 76 | 53.5211 | 73 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10101928 |  |  |  | 4549 | 4.549 | 109.176 | a41: 109.176; a42: 5.6; a43: 5.6; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2563241; a109: 1185; a111: 1185 | 1185 | 260.4968 | 0.93 |  | psi | 10.36
2018-10-31 | 62:00 | 15:00 | 4 | 2.8169 | 3 | 78 | 54.9296 | 76 | [7 empty] | 55.6338 | 57.0423 |  | 61.2676 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10106531 |  |  |  | 4603 | 4.603 | 110.472 | a41: 110.472; a42: 5.3; a43: 5.3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2564405; a109: 1164; a111: 1164 | 1164 | 252.8786 |  |  | bar | 1.0132
2018-10-31 | 63:00 | 16:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10111091 |  |  |  | 4560 | 4.56 | 109.44 | a41: 109.44; a42: 4.8; a43: 4.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2565571; a109: 1166; a111: 1166 | 1166 | 255.7018 |  |  | atm | 1
2018-10-31 | 64:00 | 17:00 | 4 | 2.8169 | 2 | 78 | 54.9296 | 76 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10115518 |  |  |  | 4427 | 4.427 | 106.248 | a41: 106.248; a42: 4.5; a43: 4.5; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1026; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 86.22%; a89: 0%; a96: 0%; a107: 2566711; a109: 1140; a111: 1140 | 1140 | 257.5107 |  |  | kPA | 101.325
2018-10-31 | 65:00 | 18:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10120126 |  |  |  | 4608 | 4.608 | 110.592 | a41: 110.592; a42: 4.1; a43: 4.1; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1020; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.71%; a89: 0%; a96: 0%; a107: 2567876; a109: 1165; a111: 1165 | 1165 | 252.8212 | 1.08
2018-10-31 | 66:00 | 19:00 | 4 | 2.8169 | 1 | 77 | 54.2254 | 75 | [7 empty] | 51.4085 | 52.8169 |  | 57.0423 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10124872 |  |  |  | 4746 | 4.746 | 113.904 | a41: 113.904; a42: 3.7; a43: 3.7; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1020; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.71%; a89: 0%; a96: 0%; a107: 2569040; a109: 1164; a111: 1164 | 1164 | 245.2592 |  |  | Convert Pressure (Enter Unit and Value)
2018-10-31 | 67:00 | 20:00 | 4 | 2.8169 | 0 | 77 | 54.2254 | 74 | [7 empty] | 50 | 51.4085 |  | 55.6338 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10129415 |  |  |  | 4543 | 4.543 | 109.032 | a41: 109.032; a42: 3.4; a43: 3.4; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1020; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.71%; a89: 0%; a96: 0%; a107: 2570151; a109: 1111; a111: 1111 | 1111 | 244.5521 |  |  | m of H2O | psi
2018-10-31 | 68:00 | 21:00 | 4 | 2.8169 | 0 | 75 | 52.8169 | 73 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10133850 |  |  |  | 4435 | 4.435 | 106.44 | a41: 106.44; a42: 3; a43: 3; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1020; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.71%; a89: 0%; a96: 0%; a107: 2571326; a109: 1175; a111: 1175 | 1175 | 264.938 |  |  | 1 | 1.4189
2018-10-31 | 69:00 | 22:00 | 4 | 2.8169 | -2 | 77 | 54.2254 | 75 | [7 empty] | 54.9296 | 56.338 |  | 60.5634 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10138678 |  |  |  | 4828 | 4.828 | 115.872 | a41: 115.872; a42: 2.8; a43: 2.8; a47: 3B+1S; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 1020; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 85.71%; a89: 0%; a96: 0%; a107: 2572494; a109: 1168; a111: 1168 | 1168 | 241.9221 | 0.84
2018-10-31 | 70:00 | 23:00 | 4 | 2.8169 | -5 | 71 | 50 | 69 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10142350 |  |  |  | 3672 | 3.672 | 88.128 | a41: 88.128; a42: 3.8; a43: 3.8; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2573582; a109: 1088; a111: 1088 | 1088 | 296.2963 |  |  | FLOW | MLD
2018-10-31 | 71:00 | 24:00 | 4 | 2.8169 | 0 | 69 | 48.5915 | 67 | [7 empty] | 53.5211 | 54.9296 |  | 59.1549 | Manual Operation |  | DEF |  | DEF | [5 empty] | 10146400 |  |  |  | 4050 | 4.05 | 97.2 | a41: 97.2; a42: 5.2; a43: 5.2; a47: 3B; a48: 1187; a49: 1185; a50: 0; a51: 1185; a64: 0; a65: 0; a80: 99.75%; a81: 99.58%; a82: 0%; a83: 99.58%; a88: 0%; a89: 0%; a96: 0%; a107: 2574700; a109: 1118; a111: 1118 | 1118 | 276.0494 |  |  | MLD | 1
|  |  | 4 | 2.8169 | 3.5833 | 76.7917 | 54.0786 | 74.75 | [15 empty] | #DIV/0! |  |  |  |  | -409882 |  |  |  |  | 104710 | 104.71 | 104.71 | a42: 6.475; a43: 6.475; a106: 0; a109: 27115; a111: 27115 | 27115 | 258.9533 |  |  | m3/hr | 41.67
[120 empty] | Liter/sec | 11.575
ENGINEER / OPERATOR ON DUTY
| 6am - 2pm | D.E. CAPIÑA / F. RAMOS
| 2pm - 10pm | ESTOCHE M.A./PROVIDENCIA R.
| 10pm - 6am | G. HERNANDEZ / A. RAYALA II
NOTABLE REMARKS FOR THE DAY :
TARGET DISCHARGE PRESSURE SET TO 75 PSI @ 12:01 AM TO 4:01 AM AS PER SCHEDULE
XCV4- INCREASE OPENING @ 12:01 AM (20%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 1:01 AM AS PER SCHEDULE / ACTUAL READING 70 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 75 PSI @ 2:01 AM AS PER SCHEDULE / ACTUAL READING 73 PSI
XCV4 - CLOSED @ 2:25 AM RESERVOIR WATER ELEVATION (9.5 M)
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 3:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 4:01 PM TO 6:01 PM AS PER SCHEDULE
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 4:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
* NORMAL TARGET DISCHARGE PRESSURE 83 PSI @ 5:01 AM AS PER SCHEDULE / ACTUAL READING 80 PSI
TARGET DISCHARGE PRESSURE SET TO 83 PSI @ 6:01 AM TO 12:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 6:01 AM AS PER SCHEDULE/ ACTUAL READING 82 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 7:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
SP1 - STARTED @ 7:00 AM TO MEET 83 PSI TARGET DISCHARGE PRESSURE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 8:01 AM AS PER SCHEDULE/ ACTUAL READING 79 PSI
ROSENDO SANCHEZ AND TEAM OF RB SANCHEZ PME CONSULTANTS AND ASSOSCIATES INC. ARRIVE @ 8:50 AM FOR GENERAL WALKTHROUGH IN PUMP STATION IN PREPARATION FOR PUMP ASSESSMENT.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 9:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 10:01 AM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE/ ACTUAL READING 76 PSI
CHARLES FLORES AND TEAM OF RJEN ARRIVE @ 11:35 AM FOR CABLE PULLING AND TESTING. WITH ROBERT TOLENTINO AND TEAM.
TARGET DISCHARGE PRESSURE SET TO 81 PSI @ 12:01 PM TO 5:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 1:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 2:01 PM AS PER SCHEDULE/ ACTUAL READING 76 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 3:01 PM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 81 PSI @ 4:01 PM AS PER SCHEDULE/ ACTUAL READING 78 PSI
TARGET DISCHARGE PRESSURE SET TO 78 PSI @ 5:01 PM TO 7:01 PM AS PER SCHEDULE
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 5:01 PM AS PER SCHEDULE/ ACTUAL READING 78 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 6:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 7:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 76 PSI @ 7:01 PM TO 8:01 AM AS PER SCHEDULE
INDRA LEAD BY JUAN PAOLO GALANG ARRIVE @ 6:50PM FOR CHECK/CLEANING I.T CABINET
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 8:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 9:01 PM AS PER SCHEDULE/ ACTUAL READING 75 PSI
SP1 - STOPPED @ 10:00 PM DUE TO PARAMETER CAPACITY OF 3.0 ELEVATION LEVEL.
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 78 PSI @ 10:01 PM AS PER SCHEDULE/ ACTUAL READING 77 PSI
TARGET DISCHARGE PRESSURE SET TO 83PSI @ 10:01 PM TO 12:01 AM AS PER SCHEDULE
XCV4 -OPENED @ 10:01 PM (15%)
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 11:01 PM AS PER SCHEDULE / ACTUAL READING 71PSI
* UNABLE TO MEET TARGET DISCHARGE PRESSURE 83 PSI @ 12:01 AM AS PER SCHEDULE / ACTUAL READING 69 PSI